## Tracking2013 by Month (hidden)
2013 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Expected Path: Goal OP events* | 5 | 4 | 3 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 3 | 4 |  |  | 32 | 32
Amber Goal - Lowest end of range* | 7 | 5 | 4 | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 4 | 5 |  |  | 42 | 42
Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 3 | 0 |  |  | 31 | 31
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Goal - HP Distribution Mains | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 |  |  | 6 | 6
Actual - HP Distribution Mains | 4 | 1 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 9 | 9
Goal - LP Distribution | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 6 | 6
Actual - LP Distribution | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 |  |  | 3 | 3
Goal - Distribution Main Total | 2 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 2 |  |  | 12 | 12
Actual - Distribution Main Total | 4 | 1 | 0 | 2 | 2 | 0 | 0 | 1 | 1 | 0 | 1 | 0 |  |  | 12 | 12
Goal - Distribution Services Total | 2 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 2 |  |  | 12 | 12
Actual - Distribution Services Total | 4 | 1 | 0 | 2 | 2 | 0 | 0 | 1 | 1 | 0 | 1 | 0 |  |  | 12 | 12
Goal - Transmission | 3 | 3 | 2 | 1 | 1 | 2 | 0 | 1 | 2 | 1 | 2 | 2 |  |  | 20 | 20
Actual - Transmission | 4 | 2 | 2 | 2 | 0 | 2 | 0 | 3 | 1 | 1 | 2 | 0 |  |  | 19 | 19
Goal - All Large Excursions1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 11 | 11
Actual - Large Excursions - HP Distrib | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 4 | 4
Actual - Large Excursions - LP Distrib | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  |  | 1 | 1
Actual - Large Excursions - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 |  |  | 5 | 5
Actual - Total All Large Excursions | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 10 | 10
Goal - All Equipment Failure | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 13 | 13
Actual - All Equipment Failure | 4 | 1 | 0 | 2 | 1 | 2 | 0 | 3 | 0 | 1 | 1 | 0 |  |  | 15 | 15
Goal - All Operator Error | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 14 | 14
Actual - All Operator Error | 3 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | 2 | 0 | 2 | 0 |  |  | 14 | 14
Goal - At Compressor Stn or Storage | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |  |  | 4 | 4
1Q Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
1 - Large Excursions are defined as:
HP Distribution = P ≥ MOP + 10%
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MOP + 10 psi
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For November Month-To-Date: 2 transmission events, 1 HP distribution event and 0 LP distribution event (better than month-end goals for HP/LP distribution for month and transmission for month). Preliminary root cause: 2 events were human factor error-related and 1 event was equipment-related. Event details shown below.
OP Team reviewing root causes of overpressure events. Plan additional training to address human-error related OP events. Detail review of equipment-related events to formulate corrective action plan.
| Jan: Total OP Events - Jan to December; Jul: Large Excursion OP Events - Jan to December | Small Excursion OP Events - Jan to December
| 2011 Actuals | 2012 Actuals | 2013 Actuals | 2014 Actuals | 2013 Goal |  | 2011 | 2012 | 2013 | 2014 | 2013 Goal |  | 2011 | 2012 | 2013 | 2014 | 2013 Goal
T&D Total | 774 | 308 | 31 |  | 32 |  | 36 | 8 | 10 |  | 11 |  | 738 | 300 | 21 |  | 21
| 2013 Total OP - 31 Events | [5 empty] | 2013 Large Excursion OP Events - 10 Events
2013 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 66 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 774 | 774
2012 Actual - All Events | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 308 | 308
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 3 | 0 |  |  | 31 | 31
2013 Goal OP events | 5 | 4 | 3 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 3 | 4 |  |  | 32 | 32
2011 Actual - Total All Large Excursions | 6 | 5 | 3 | 2 | 6 | 4 | 2 | 1 | 4 | 1 | 2 | 0 |  |  | 36 | 36
2012 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 8 | 8
2013 Actual - Total All Large Excursions | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 10 | 10
2013 Goal - All Large Excursions1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 11 | 11
| Total OP Events |  |  |  |  | Large Excursion OP Events |  |  |  |  | Small Excursion OP Events
| 2011 Actuals | 2012 Actuals | 2013 Actuals | 2013 Goals |  | 2011 | 2012 | 2013 Actuals | 2013 Goals |  | 2011 | 2012 | 2013 Actuals | 2013 Goals
HP Dist | 38 | 7 | 9 | 6 |  | 8 | 4 | 4 | 4 |  | 30 | 3 | 5 | 2
LP Dist | 624 | 228 | 3 | 6 |  | 3 | 0 | 1 | 4 |  | 621 | 228 | 2 | 2
Dist Total | 662 | 235 | 12 | 12 |  | 11 | 4 | 5 | 8 |  | 651 | 231 | 7 | 4
Trans | 112 | 73 | 19 | 20 |  | 25 | 4 | 5 | 3 |  | 87 | 69 | 14 | 17
T&D Total | 774 | 308 | 31 | 32 |  | 36 | 8 | 10 | 11 |  | 738 | 300 | 21 | 21
Note on Q11: Singer, Kevin D: Yr-End Actual = YTD+GOAL (Remaining)
Note on R11: Singer, Kevin D: enter total monthly
Note on Q14: Singer, Kevin D: Yr-End Actual = YTD+GOAL (Remaining)
Note on R14: Singer, Kevin D: enter total monthly
Note on Q23: Singer, Kevin D: Yr-End Actual = YTD+GOAL (Remaining)
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on Q29: Singer, Kevin D: Yr-End Actual = YTD+GOAL (Remaining)
Note on A54: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on R130: Singer, Kevin D: update amber cells from 2011-2013 expanded data

## Tracking2015 by Quarter (hidden)
1Q - 2015 OP Event Performance
| Q1 | Q2 | Q3 | Q4 |  | YTD | Yr-End
Expected Path: Goal OP events | 6 | 3 | 3 | 4 |  | 16 | 16
Amber Goal - Lowest end of range | 9 | 6 | 6 | 7 |  | 28 | 28
Actual - All Events | 7 | 4 | 9 | 9 |  | 29 | 29
Asset Family OP Metrics
| Q1 | Q2 | Q3 | Q4 |  | YTD | Yr-End
Goal - HP Distribution | 2 | 0 | 0 | 2 |  | 4 | 4
Actual - HP Distribution | 2 | 4 | 3 | 4 |  | 13 | 13
Goal - LP Distribution | 2 | 1 | 0 | 0 |  | 3 | 3
Actual - LP Distribution | 1 | 0 | 1 | 1 |  | 3 | 3
Goal - Distribution Main Total | 4 | 1 | 0 | 2 |  | 7 | 7
Actual - Distribution Main Total | 3 | 4 | 4 | 5 |  | 16 | 16
Goal - Distribution Services Total | 4 | 1 | 0 | 2 |  | 7 | 7
Actual - Distribution Services Total | 3 | 4 | 4 | 5 |  | 16 | 16
Goal - Transmission | 2 | 2 | 3 | 2 |  | 9 | 9
Actual - Transmission | 4 | 0 | 5 | 4 |  | 13 | 13
Goal - All Large Excursions1 | 2 | 0 | 1 | 1 |  | 2 | 4
Actual - Large Excursions - HP Distrib | 2 | 0 | 1 | 0 |  | 2 | 3
Actual - Large Excursions - LP Distrib | 1 | 0 | 1 | 0 |  | 1 | 0
Actual - Large Excursions - Transmission | 0 | 0 | 2 | 0 |  | 0 | 3
Actual - Total All Large Excursions | 3 | 0 | 4 | 0 |  | 7 | 7
Goal - All Equipment Failure | 3 | 2 | 1 | 3 |  | 9 | 9
Actual - All Equipment Failure | 3 | 2 | 5 | 6 |  | 16 | 16
Goal - All Operator Error | 3 | 1 | 2 | 1 |  | 7 | 7
Actual - All Operator Error | 4 | 2 | 4 | 3 |  | 13 | 13
Goal - At Compressor Stn or Storage | 1 | 1 | 1 | 1 |  | 4 | 4
Actual - At Compressor Stn or Storage | 0 | 0 | 1 | 1 |  | 2 | 2
1 - Large Excursions are defined as:
HP Distribution = P ≥ MAOP + 10%
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MOP + 10 psig
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
1st Quarter
Large Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1
HP Distribution | 2 | 2 | 2 | 2 | 2
LP Distribution | 1 | 0 | 0 | 0 | 1
Transmission | 6 | 1 | 2 | 1 | 0
Grand Total | 9 | 3 | 4 | 3 | 3
Small Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1
HP Distribution | 4 | 2 | 3 | 0 | 0
LP Distribution | 172 | 179 | 0 | 1 | 0
Transmission | 35 | 45 | 6 | 2 | 4
Grand Total | 211 | 226 | 9 | 3 | 4
Total OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1
HP Distribution | 6 | 4 | 5 | 2 | 2
LP Distribution | 173 | 179 | 0 | 1 | 1
Transmission | 41 | 46 | 8 | 3 | 4
Grand Total | 220 | 229 | 13 | 6 | 7
Metric Comparison - Prior Years - 1st Quarter
OP Events by Apparent Cause - First Quarter
2015 Total OP - 0 Events as of 3/31/14 | [7 empty] | 2015 Large Excursion OP Events - 0 Events
2nd Quarter
Large Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2
HP Distribution | 5 | 0 | 1 | 0 | 0
LP Distribution | 1 | 0 | 0 | 0 | 0
Transmission | 1 | 1 | 0 | 0 | 0
Grand Total | 7 | 1 | 1 | 0 | 0
Small Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2
HP Distribution | 7 | 0 | 2 | 1 | 4
LP Distribution | 147 | 46 | 1 | 1 | 0
Transmission | 34 | 15 | 4 | 2 | 0
Grand Total | 188 | 61 | 7 | 4 | 4
Total OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2
HP Distribution | 12 | 0 | 3 | 1 | 4
LP Distribution | 148 | 46 | 1 | 1 | 0
Transmission | 35 | 16 | 4 | 2 | 0
Grand Total | 195 | 62 | 8 | 4 | 4
Metric Comparison - Prior Years - 2nd Quarter
OP Events by Apparent Cause - Second Quarter
2015 Total OP- 0 Events as of 7/1/14
3rd Quarter
Large Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3
HP Distribution | 1 | 1 | 1 | 0 | 1
LP Distribution | 0 | 0 | 1 | 0 | 1
Transmission | 1 | 0 | 1 | 2 | 2
Grand Total | 2 | 1 | 3 | 2 | 4
Small Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3
HP Distribution | 10 | 0 | 0 | 1 | 2
LP Distribution | 164 | 46 | 0 | 0 | 0
Transmission | 21 | 15 | 3 | 1 | 3
Grand Total | 195 | 61 | 3 | 2 | 5
Total OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3
HP Distribution | 11 | 1 | 1 | 1 | 3
LP Distribution | 164 | 46 | 1 | 0 | 1
Transmission | 22 | 15 | 4 | 3 | 5
Grand Total | 197 | 62 | 6 | 4 | 9
Metric Comparison - Prior Years - 3rd Quarter
OP Events by Apparent Cause - 4th Quarter
2013 Total OP- 13 Events as of 3/31/13 | [5 empty] | 2013 Large Excursion OP Events - 5 Events
4th Quarter
Large Excursion OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4
HP Distribution | 2 | 1 | 0 | 2 | 0
LP Distribution | 1 | 0 | 0 | 0 | 0
Transmission | 0 | 1 | 1 | 0 | 0
Grand Total | 3 | 2 | 1 | 2 | 0
Small Excursion OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4
HP Distribution | 8 | 1 | 0 | 0 | 4
LP Distribution | 138 | 3 | 1 | 0 | 1
Transmission | 14 | 6 | 3 | 2 | 5
Grand Total | 160 | 10 | 4 | 2 | 10
Total OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4
HP Distribution | 10 | 2 | 0 | 2 | 4
LP Distribution | 139 | 3 | 1 | 0 | 1
Transmission | 14 | 7 | 4 | 2 | 5
Grand Total | 163 | 12 | 5 | 4 | 10

## Tracking2016 by Quarter (hidden)
Q - 2016 OP Event Performance
| Q1 | Q2 | Q3 | Q4 |  | YTD | Yr-End
Expected Path: Goal OP events | 5 | 3 | 3 | 5 |  | 11 | 16
Amber Goal - Lowest end of range | 8 | 6 | 6 | 8 |  | 14 | 28
Actual - All Events | 2 | 5 | 4 | 7 |  | 18 | 23 |  |  | Q1 | Q2 | Jul | Aug | Sep | Q4 | YTD | Yr-End
[9 empty] | Expected Path: Goal OP events | 5 | 3 | 1 | 1 | 1 | 5 | 11 | 16
Asset Family OP Metrics | [8 empty] | Actual - All Events | 2 | 5 | 1 | 3 |  | 0 | 11 | 16
| Q1 | Q2 | Q3 | Q4 |  | YTD | Yr-End
Goal - HP Distribution | 2 | 0 | 0 | 2 |  | 2 | 4 |  | Goal - All Large Excursions1 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 4
Actual - HP Distribution | 0 | 2 | 2 | 4 |  | 4 | 6 |  | Actual - Total All Large Excursions | 0 | 4 | 1 | 1 |  | - | 6 | 8
Goal - LP Distribution | 2 | 1 | 0 | 0 |  | 3 | 3
Actual - LP Distribution | 2 | 0 | 0 | 0 |  | 2 | 2
Goal - Distribution Main Total | 4 | 1 | 0 | 2 |  | 5 | 7
Actual - Distribution Main Total | 2 | 2 | 2 | 4 |  | 6 | 8
Goal - Distribution Services Total | 4 | 1 | 0 | 2 |  | 5 | 7
Actual - Distribution Services Total | 2 | 2 | 2 | 4 |  | 6 | 8
Goal - Transmission | 2 | 2 | 3 | 3 |  | 7 | 10
Actual - Transmission | 0 | 3 | 2 | 3 |  | 5 | 8
Goal - All Large Excursions1 | 2 | 0 | 0 | 2 |  | 2 | 4
Actual - Large Excursions - HP Distrib | 0 | 2 | 2 | 2 |  | 6 | 6
Actual - Large Excursions - LP Distrib | 0 | 0 | 0 | 0 |  | 0 | 0
Actual - Large Excursions - Transmission | 0 | 2 | 0 | 2 |  | 4 | 4
Actual - Total All Large Excursions | 0 | 4 | 2 | 4 |  | 10 | 12
Goal - All Equipment Failure | 3 | 2 | 1 | 3 |  | 6 | 9
Actual - All Equipment Failure | 2 | 1 | 2 | 3 |  | 5 | 8
Goal - All Operator Error | 3 | 1 | 2 | 1 |  | 6 | 7
Actual - All Operator Error | 0 | 4 | 2 | 4 |  | 6 | 7
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 |  | 0 | 0
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 1 |  | 0 | 0
1 - Large Excursions are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% |  |  |  | 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig |  |  |  | 192.619-621
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MAOP + 10% or 25 psig
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
1st Quarter
Large Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1 | 2016 Q1 | 2017 Q1
HP Distribution | 2 | 2 | 2 | 2 | 2 | 0 | 1
LP Distribution | 1 | 0 | 0 | 0 | 1 | 0 | 0
Transmission | 6 | 1 | 2 | 1 | 0 | 0 | 0
Grand Total | 9 | 3 | 4 | 3 | 3 | 0 | 1
Small Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1 | 2016 Q1 | 2017 Q1
HP Distribution | 4 | 2 | 3 | 0 | 0 | 0 | 0
LP Distribution | 172 | 179 | 0 | 1 | 0 | 2 | 0
Transmission | 35 | 45 | 6 | 2 | 4 | 0 | 1
Grand Total | 211 | 226 | 9 | 3 | 4 | 2 | 1
Total OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1 | 2016 Q1 | 2017 Q1
HP Distribution | 6 | 4 | 5 | 2 | 2 | 0 | 1
LP Distribution | 173 | 179 | 0 | 1 | 1 | 2 | 0
Transmission | 41 | 46 | 8 | 3 | 4 | 0 | 1
Grand Total | 220 | 229 | 13 | 6 | 7 | 2 | 2
Metric Comparison - Prior Years - 1st Quarter
OP Events by Apparent Cause - First Quarter
2015 Total OP - 0 Events as of 3/31/14 | [7 empty] | 2015 Large Excursion OP Events - 0 Events
2nd Quarter
Large Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2 | 2016 Q2
HP Distribution | 5 | 0 | 1 | 0 | 0 | 0
LP Distribution | 1 | 0 | 0 | 0 | 0 | 0
Transmission | 1 | 1 | 0 | 0 | 0 | 0
Grand Total | 7 | 1 | 1 | 0 | 0 | 0
Small Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2 | 2016 Q2
HP Distribution | 7 | 0 | 2 | 1 | 4 | 0
LP Distribution | 147 | 46 | 1 | 1 | 0 | 0
Transmission | 34 | 15 | 4 | 2 | 0 | 0
Grand Total | 188 | 61 | 7 | 4 | 4 | 0
Total OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2 | 2016 Q2
HP Distribution | 12 | 0 | 3 | 1 | 4 | 0
LP Distribution | 148 | 46 | 1 | 1 | 0 | 0
Transmission | 35 | 16 | 4 | 2 | 0 | 0
Grand Total | 195 | 62 | 8 | 4 | 4 | 0
Metric Comparison - Prior Years - 2nd Quarter
OP Events by Apparent Cause - Second Quarter
2015 Total OP- 0 Events as of 7/1/14
3rd Quarter
Large Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3 | 2016 Q3
HP Distribution | 1 | 1 | 1 | 0 | 1 | 0
LP Distribution | 0 | 0 | 1 | 0 | 1 | 0
Transmission | 1 | 0 | 1 | 2 | 2 | 0
Grand Total | 2 | 1 | 3 | 2 | 4 | 0
Small Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3 | 2016 Q3
HP Distribution | 10 | 0 | 0 | 1 | 2 | 0
LP Distribution | 164 | 46 | 0 | 0 | 0 | 0
Transmission | 21 | 15 | 3 | 1 | 3 | 0
Grand Total | 195 | 61 | 3 | 2 | 5 | 0
Total OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3 | 2016 Q3
HP Distribution | 11 | 1 | 1 | 1 | 3 | 0
LP Distribution | 164 | 46 | 1 | 0 | 1 | 0
Transmission | 22 | 15 | 4 | 3 | 5 | 0
Grand Total | 197 | 62 | 6 | 4 | 9 | 0
Metric Comparison - Prior Years - 3rd Quarter
OP Events by Apparent Cause - 4th Quarter
2013 Total OP- 13 Events as of 3/31/13 | [5 empty] | 2013 Large Excursion OP Events - 5 Events
4th Quarter
Large Excursion OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4 | 2016 Q4
HP Distribution | 2 | 1 | 0 | 2 | 0 | 2
LP Distribution | 1 | 0 | 0 | 0 | 0 | 0
Transmission | 0 | 1 | 1 | 0 | 0 | 2
Grand Total | 3 | 2 | 1 | 2 | 0 | 4
Small Excursion OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4 | 2016 Q4
HP Distribution | 8 | 1 | 0 | 0 | 4 | 2
LP Distribution | 138 | 3 | 1 | 0 | 1 | 0
Transmission | 14 | 6 | 3 | 2 | 5 | 1
Grand Total | 160 | 10 | 4 | 2 | 10 | 3
Total OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4 | 2016 Q4
HP Distribution | 10 | 2 | 0 | 2 | 4 | 4
LP Distribution | 139 | 3 | 1 | 0 | 1 | 0
Transmission | 14 | 7 | 4 | 2 | 5 | 3
Grand Total | 163 | 12 | 5 | 4 | 10 | 7

## Tracking2016 by Month (hidden)
2016 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Expected Path: Goal OP events* | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 |  |  | 16 | 16
Amber Goal - Lowest end of range* | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 |  |  | 25 | 28
Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Goal - HP Distribution Mains | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | 4 | 4
Actual - HP Distribution Mains | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 8 | 8 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 3 | 3
Actual - LP Distribution | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 3 |  |  |  |  | change these colors at End of Month |  |  |  | 0
Goal - Distribution Main Total | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | 7 | 7 | [8 empty] | 1
Actual - Distribution Main Total | 2 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10 |  |  |  |  | change these colors at End of Month |  |  |  | 2
Goal - Distribution Services Total | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | 7 | 7
Actual - Distribution Services Total | 2 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10 |  |  |  |  | change these colors at End of Month |  |  |  | 3
Goal - Transmission | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 |  |  | 9 | 9
Actual - Transmission | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 | 1 |  |  | 8 | 8 |  |  |  |  | change these colors at End of Month
Goal - All Large Excursions1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  | 3 | 4 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 1 | 1 | 0 |  |  | 6 | 6
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | 4 | 4
Actual - Total All Large Excursions | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
Goal - All Equipment Failure | 2 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 2 |  |  | 9 | 9
Actual - All Equipment Failure | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 0 | 1 |  |  | 8 | 8
Goal - All Operator Error | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 |  |  | 7 | 7
Actual - All Operator Error | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 2 | 0 | 1 | 2 | 1 |  |  | 10 | 10
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  |  | 1 | 1
1 - Large Excursions are defined as: | bar: Oct to Dec
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MAOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events; Oct: Large Excursion OP Events | [5 empty] | Small Excursion OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2016 Goal |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2016 Goal |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2016 Goal
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 16 |  |  | 21 | 7 | 10 | 7 | 7 | 10 | 4 |  | 754 | 302 | 22 | 11 | 22 | 8 | 12
these tables are auto generated from the Charts tab
Charts tab must be updated monthly
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
2016 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 722 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 303 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 16 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
2016 Goal OP events | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 |  |  | 16 | 16
2011 Actual - Total All Large Excursions | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 18 | 21
2012 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Excursions | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 1 |  |  | 10 | 10
2014 Actual - Total All Large Excursions | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Excursions | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2016 Goal - All Large Excursions1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  | 4 | 4
| Jan: Total OP Events; Aug: Large Excursion OP Events | Large |  | Small Excursion OP Events |  |  |  |  | Small
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 |  | 10 | 4 | 4 | 4 | 3 | 6 |  | 29 | 3 | 5 | 2 | 10 | 2
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 |  | 3 | 0 | 1 | 0 | 2 | 0 |  | 621 | 228 | 2 | 2 | 1 | 2
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 |  | 13 | 4 | 5 | 4 | 5 | 6 |  | 650 | 231 | 7 | 4 | 11 | 4
Trans | 112 | 74 | 20 | 10 | 13 | 8 |  | 8 | 4 | 6 | 3 | 2 | 4 |  | 104 | 70 | 14 | 7 | 11 | 4
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 |  | 21 | 8 | 11 | 7 | 7 | 10 |  | 754 | 301 | 21 | 11 | 22 | 8
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A54: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on AB59: Singer, Kevin D: update topics and year to date totals in concert with the table below
Note on P117: Singer, Kevin D: move pre month report
Note on P125: Singer, Kevin D: move per month report
Note on U129: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14

## Tracking2015 by Month (hidden)
2015 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
Expected Path: Goal OP events* | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  | 16 | 16
Amber Goal - Lowest end of range* | 4 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 |  | 28 | 28
Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  | 29 | 29 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
Goal - HP Distribution Mains | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 4 | 4
Actual - HP Distribution Mains | 1 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 2 | 2 | 0 | 2 |  | 13 | 13 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 3
Actual - LP Distribution | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 |  | 3 | 3 |  |  |  |  | change these colors at End of Month | 0
Goal - Distribution Main Total | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 7 | 7 | [5 empty] | 1
Actual - Distribution Main Total | 2 | 0 | 1 | 1 | 2 | 1 | 0 | 2 | 2 | 3 | 0 | 2 |  | 16 | 16 |  |  |  |  | change these colors at End of Month | 2
Goal - Distribution Services Total | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 7 | 7
Actual - Distribution Services Total | 2 | 0 | 1 | 1 | 2 | 1 | 0 | 2 | 2 | 3 | 0 | 2 |  | 16 | 16 |  |  |  |  | change these colors at End of Month | 3
Goal - Transmission | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 |  | 9 | 9
Actual - Transmission | 1 | 2 | 1 | 0 | 0 | 0 | 3 | 1 | 1 | 0 | 2 | 2 |  | 13 | 13 |  |  |  |  | change these colors at End of Month
Goal - All Large Excursions1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 |  | 4 | 4 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 3 | 3
Actual - Large Excursions - LP Dist | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 2 | 2
Actual - Large Excursions - Trans | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 2 | 2
Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  | 7 | 7
Goal - All Equipment Failure | 2 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 2 |  | 9 | 9
Actual - All Equipment Failure | 2 | 1 | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 |  | 16 | 16
Goal - All Operator Error | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 |  | 7 | 7
Actual - All Operator Error | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 1 | 1 | 1 | 0 | 2 |  | 13 | 13
Goal - At Compressor Stn or Storage | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |  | 4 | 4
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 |  | 2 | 2
1 - Large Excursions are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events; Aug: Large Excursion OP Events |  | Small Excursion OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2015 Goal |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2015 Goal | 2011 | 2012 | 2013 | 2014 | 2015 | 2015 Goal
T&D Total | 775 | 309 | 32 | 18 | 29 | 16 |  | 21 | 7 | 9 | 7 | 7 | 4 | 754 | 302 | 23 | 11 | 22 | 12
these tables are auto generated from the Charts tab
Charts tab must be updated monthly
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
2015 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  | 29 | 29
2015 Goal OP events | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  | 12 | 16
2011 Actual - Total All Large Excursions | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  | 21 | 21
2012 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  | 7 | 7
2013 Actual - Total All Large Excursions | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  | 9 | 9
2014 Actual - Total All Large Excursions | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  | 7 | 7
2015 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  | 7 | 7
2015 Goal - All Large Excursions1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 |  | 4 | 4
| Jan: Total OP Events; Aug: Large Excursion OP Events |  | Small Excursion OP Events
| 2011 Actuals | 2012 Actuals | 2013 Actuals | 2014 Actual | 2015 YTD | 2015 Goal |  | 2011 | 2012 | 2013 Actuals | 2014 Actual | 2015 YTD | 2015 Goal | 2011 | 2012 | 2013 Actuals | 2014 Actual | 2015 YTD | 2015 Goal
HP Dist | 39 | 7 | 9 | 6 | 13 | 4 |  | 10 | 4 | 4 | 4 | 3 |  | 29 | 3 | 5 | 2 | 10
LP Dist | 624 | 228 | 3 | 2 | 3 | 3 |  | 3 | 0 | 1 | 0 | 2 |  | 621 | 228 | 2 | 2 | 1
Dist Total | 663 | 235 | 12 | 8 | 16 | 16 |  | 13 | 4 | 5 | 4 | 5 |  | 650 | 231 | 7 | 4 | 11
Trans | 112 | 74 | 20 | 10 | 13 | 9 |  | 25 | 4 | 6 | 3 | 2 |  | 87 | 70 | 14 | 7 | 11
T&D Total | 775 | 309 | 32 | 18 | 29 | 25 |  | 38 | 8 | 11 | 7 | 7 |  | 737 | 301 | 21 | 11 | 22
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A54: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on Y59: Singer, Kevin D: update topics and year to date totals in concert with the table below
Note on P116: Singer, Kevin D: move pre month report
Note on P123: Singer, Kevin D: move per month report
Note on U127: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14

## 2019 OP Rag Status (hidden)
Sulfur-gon Filters |  | Contact: Nicolyn Hernandez
Total Stations w/Filters: | 563 | Notes: [9/24] [KDSD] Per JZ. Please note that the total number of Sulfur-gon Installation at Pilot-operated Sites is 380, there were some duplications that were taken out. I do not have any further updates as yet due to the fact that the efforts to get updates from the divisions were put on hold. I just got the go ahead to obtain further updates but, its going be at least a few weeks till I will start receiving updates from the divisions. I will keep you posted. [3/28] [KWB] Per Corine e-mail 3/27, formal count not available, estimated 300+ installs completed
Existing: | 250
2017 Installed: | 75
2018 Installed: | 238
2019 Installed: | 0
Slam Shut Installations (50N) |  | Contact: Sophia Curiel / Ramon Gonzalez
Total | 100 | Notes: [9/26] [KDSD] Updated in September [3/29] [KWB] Per Ramon e-mail 3/29, need clarification. F/U/W Tim on path forward
Completed | 7
2019 Remaining | 93
Mini AT Data into Abnormal Pressure Report |  | Contact: Matt Pace
Total | 343 | Notes: [9/24] [KDSD] Per Sergio, the implementation will initiate this week with 25 sites, 19 complete. [3/28] [KWB] Per Matt pace e-mail 3/28; working with control room to start migration. Not yet started.
2018 Completed | 174
2019 Completed | 169
LVCR Rebuild |  | Contact: Sophia Curiel / Ramon Gonzalez
Total | 16 | Notes: [9/26] [KDSD] Updated in September [9/24] [KDSD] Per Sophia, the group is only researching for data on 96 sites (with the understanding there are ~105) [3/29] [KWB] Per Ramon e-mail 3/29, vendor taking photos to support JUNE desktop condition assessment
2019 Completed | 1
2019 Remaining | 15
Legacy ERX to Control Room |  | Contact: Nishal Gupta
Total Legacy ERX | 135 | Notes: [8/24] [KDSD] Per Nishal, on schedule to complete by EOY [7/1] [KWB] Per Nishal e-mail 7/1, updated.
Completed Legacy ERX | 134
Remaining Legacy ERX | 1
Station Retrofits |  | Contact: Corine Hermann
Total Population | 30 | Notes: [3/29] [KWB] Per Corine, we have not started this effort. [6/26] [KDSD] Met with DIMP team, JANT will prcoess information pending GSP review, and create CAP notification.
Completed | 0
Remaining | 0
updates made for monthly op update
Precent Completion
[10 empty] | Legacy | 99.2593
| last month | [8 empty] | Condition | 7
|  |  | Metrics | 2019 Target | Previous | Change | YTD
|  | 1 | Large OP Events (MAOP-S +10%) | 6 | 1 | 0 | 1 | kevin
|  | 2 | Small OP Events | 16 | 2 | 2 | 4 | kevin
| 1/16 update | 3 | Sulfur-gon Installation at Pilot-operated Sites | 800 | 563 | 0 | 563 | jz | jmahmood@specservices.com
|  | 4 | Slam Shut Installations by 50N | 100 | 0 | 7 | 7 | jack price
|  | 5 | Slam Shut FCOs | 100 | 0 | 4 | 4 | jack price
|  | 6 | Legacy ERX to Control Room | 135 | 134 | 0 | 134 | nishal
|  | 7 | Mini AT Data into Abnormal Pressure Report | 450 | 174 | 169 | 343 | david
|  | 8 | LVCR Rebuilds | 14 | 0 | 1 | 1 | corine
|  | 9 | Station Retrofits (including secondary OPP) | 30 | 0 | 0 | 0
|  | 10 | LVC Condition Assessment Data Gathering | 379 | 379 | 0 | 379 | sophia
|  | 11 | LVCR Field Assessment | 96 | 96 | 0 | 96 | sophia
|  |  | Metrics | 2018 Target | Previous | Change | YTD
|  | 1 | Large OP Events (MAOP-S +10%) | 8 | 4 | 1 | 5
|  | 2 | Small OP Events | 16 | 15 | 3 | 18
|  | 3 | Sulfur-gon Installation at Pilot-operated Sites | 800 | 499 | 26 | 525
|  | 4 | Slam Shut Installations by Population | 30 | 5 | 1 | 6
|  | 5 | Legacy ERX to Control Room | 135 | 128 | 6 | 134
|  | 6 | Mini AT Data into Abnormal Pressure Report | 450 | 50 | 131 | 181
|  | 7 | LVCR Rebuilds | 4 | 2 | 2 | 4
|  | 8 | Station Retrofits (including secondary OPP) | 30 | 0
|  | 9 | LVC Condition Assessment Data Gathering | 379 | 301 | 64 | 365
|  | 10 | LVCR Field Assessment | 96 | 84 | 9 | 93

## 2018 OP Rag Status (hidden)
Sulfur-gon Filters (Transmission) |  | Contact: Nicolyn Hernandez
Total Stations w/Filters: | 499 | Notes: [9/24] [KDSD] Per JZ. Please note that the total number of Sulfur-gon Installation at Pilot-operated Sites is 380, there were some duplications that were taken out. I do not have any further updates as yet due to the fact that the efforts to get updates from the divisions were put on hold. I just got the go ahead to obtain further updates but, its going be at least a few weeks till I will start receiving updates from the divisions. I will keep you posted. [3/28] [KWB] Per Corine e-mail 3/27, formal count not available, estimated 300+ installs completed
Existing: | 250
2017 Installed: | 75
2018 Installed: | 174
2018 Remaining: | 0
LVC MSA Condition Assessment |  | Contact: Sophia Curiel / Ramon Gonzalez
Station Total | 379 | Notes: [9/26] [KDSD] Updated in September [3/29] [KWB] Per Ramon e-mail 3/29, need clarification. F/U/W Tim on path forward
Completed | 365
2018 Remaining | 14
Mini AT Data into Abnormal Pressure Report |  | Contact: Matt Pace
Total | 450 | Notes: [9/24] [KDSD] Per Sergio, the implementation will initiate this week with 25 sites, 19 complete. [3/28] [KWB] Per Matt pace e-mail 3/28; working with control room to start migration. Not yet started.
2018 Completed | 181
2018 Remaining | 269
LVCR Field Assessment |  | Contact: Sophia Curiel / Ramon Gonzalez
Station Total (105) | 96 | Notes: [9/26] [KDSD] Updated in September [9/24] [KDSD] Per Sophia, the group is only researching for data on 96 sites (with the understanding there are ~105) [3/29] [KWB] Per Ramon e-mail 3/29, vendor taking photos to support JUNE desktop condition assessment
2018 Completed | 93
2018 Remaining | 3
Legacy ERX to Control Room |  | Contact: Nishal Gupta
Total Legacy ERX | 135 | Notes: [8/24] [KDSD] Per Nishal, on schedule to complete by EOY [7/1] [KWB] Per Nishal e-mail 7/1, updated.
Completed Legacy ERX | 134
Remaining Legacy ERX | 1
MAOP Separation Valves |  | Contact: Corine Hermann
Total Population | 0 | Notes: [3/29] [KWB] Per Corine, we have not started this effort. [6/26] [KDSD] Met with DIMP team, JANT will prcoess information pending GSP review, and create CAP notification.
Mitigated | 0
Remaining | 0
updates made for monthly op update
Precent Completion
[10 empty] | Legacy | 99.2593
| last month | [8 empty] | Condition | 96.3061
|  |  | Metrics | 2019 Target | Previous | Change | YTD
|  | 1 | Large OP Events (MAOP-S +10%) | 6 | 1 | 0 | 1 | kevin
|  | 2 | Small OP Events | 16 | 2 | 2 | 4 | kevin
| 1/16 update | 3 | Sulfur-gon Installation at Pilot-operated Sites | 800 | 563 | 0 | 563 | jz | jmahmood@specservices.com
|  | 4 | Slam Shut Installations by 50N | 100 | 0 | 7 | 7 | jack price
|  | 5 | Slam Shut FCOs | 100 | 0 | 4 | 4 | nishall
|  | 6 | Legacy ERX to Control Room | 135 | 134 | 0 | 134 | sergio
|  | 7 | Mini AT Data into Abnormal Pressure Report | 450 | 174 | 169 | 343 | corine
|  | 8 | LVCR Rebuilds | 14 | 0 | 1 | 1
|  | 9 | Station Retrofits (including secondary OPP) | 30 | 0 | 0 | 0
|  | 10 | LVC Condition Assessment Data Gathering | 379 | 379 | 0 | 379 | sophia
|  | 11 | LVCR Field Assessment | 96 | 96 | 0 | 96 | sophia
|  |  | Metrics | 2018 Target | Previous | Change | YTD
|  | 1 | Large OP Events (MAOP-S +10%) | 8 | 4 | 1 | 5
|  | 2 | Small OP Events | 16 | 15 | 3 | 18
|  | 3 | Sulfur-gon Installation at Pilot-operated Sites | 800 | 499 | 26 | 525
|  | 4 | Slam Shut Installations by Population | 30 | 5 | 1 | 6
|  | 5 | Legacy ERX to Control Room | 135 | 128 | 6 | 134
|  | 6 | Mini AT Data into Abnormal Pressure Report | 450 | 50 | 131 | 181
|  | 7 | LVCR Rebuilds | 4 | 2 | 2 | 4
|  | 8 | Station Retrofits (including secondary OPP) | 30 | 0
|  | 9 | LVC Condition Assessment Data Gathering | 379 | 301 | 64 | 365
|  | 10 | LVCR Field Assessment | 96 | 84 | 9 | 93

## Tracking2017 by Month (hidden)
2017 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Expected Path: Goal OP events* | 4 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 16 | 16
Amber Goal - Lowest end of range* | 5 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 22 | 28
Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Goal - HP Distribution Mains | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |  |  | 6 | 6
Actual - HP Distribution Mains | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 |  |  | 6 | 6 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 1 | 1 |  |  |  |  | change these colors at End of Month |  |  |  |  | 0
Goal - Distribution Main Total | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |  |  | 6 | 6 | [9 empty] | 1
Actual - Distribution Main Total | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 1 | 1 | 0 |  |  | 7 | 7 |  |  |  |  | change these colors at End of Month |  |  |  |  | 2
Goal - Distribution Services Total | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |  |  | 6 | 6
Actual - Distribution Services Total | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 1 | 1 | 0 |  |  | 7 | 7 |  |  |  |  | change these colors at End of Month |  |  |  |  | 3
Goal - Transmission | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 |  |  | 6 | 6
Actual - Transmission | 0 | 0 | 1 | 2 | 2 | 0 | 0 | 4 | 0 | 4 | 0 | 1 |  |  | 14 | 14 |  |  |  |  | change these colors at End of Month
Goal - All Large Excursions1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 4 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 |  |  | 4 | 4
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 3 | 0 | 0 |  |  | 7 | 7
Actual - Total All Large OP | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 8
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 |  |  | 7 | 7
Actual - All Equipment Failure | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 1 | 1 | 1 | 0 | 0 |  |  | 12 | 7
Goal - All Operator Error | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 |  |  | 5 | 5
Actual - All Operator Error | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 |  |  | 3 | 3
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Actual - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Goal - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Actual - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MAOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events; Oct: Large OP Events | [5 empty] | Small OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 YTD | 2017 Goal |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 YTD | 2017 Forecast |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 YTD | 2017 Goal
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 16 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 8 |  | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 8
these tables are auto generated from the Charts tab
Charts tab must be updated monthly
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
2017 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 1 | 3 | 2 | 2 |  |  | 19 | 19
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2017 Goal OP events | 4 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 5 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 3 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 4 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 4 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 3 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 1 | 2 | 1 | 1 |  |  | 11 | 11
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2017 Goal - All Large OPs1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 4
| Jan: Total OP Events; Oct: Large Excursion OP Events | [5 empty] | Small Excursion OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual |  |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 |  |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 |  | 29 | 3 | 5 | 2 | 10 | 2 | 2
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 |  |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 |  | 621 | 228 | 2 | 2 | 1 | 2 | 1
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 |  |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 |  | 650 | 231 | 7 | 4 | 11 | 4 | 3
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 12 |  |  | 8 | 4 | 6 | 3 | 2 | 4 | 7 |  | 104 | 70 | 14 | 7 | 11 | 4 | 5
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 19 |  |  | 21 | 8 | 11 | 7 | 7 | 10 | 11 |  | 754 | 301 | 21 | 11 | 22 | 8 | 8
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 21
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 11
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A60: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on AB65: Singer, Kevin D: update topics and year to date totals in concert with the table below
Note on P124: Singer, Kevin D: move pre month report
Note on P133: Singer, Kevin D: move per month report
Note on X137: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14
Note on Y137: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14

## Tracking2018 by Month (hidden)
2018 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Expected Path: Goal OP events* | 8 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 15 | 16
Amber Goal - Lowest end of range* | 4 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 22 | 24
Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 19 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Goal - HP Distribution Mains | 4 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 8 | 8
Actual - HP Distribution Mains | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 2 |  |  | 6 | 6 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 |  |  |  |  | change these colors at End of Month |  |  |  |  | 0
Goal - Distribution Main Total | 4 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 8 | 8 | [9 empty] | 1
Actual - Distribution Main Total | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 0 | 2 | 2 |  |  | 9 | 9 |  |  |  |  | change these colors at End of Month |  |  |  |  | 2
Goal - Distribution Services Total | 4 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 8 | 8
Actual - Distribution Services Total | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 0 | 2 | 2 |  |  | 9 | 9 |  |  |  |  | change these colors at End of Month |  |  |  |  | 3
Goal - Transmission | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 8 | 8
Actual - Transmission | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 2 | 1 |  |  | 9 | 9 |  |  |  |  | change these colors at End of Month
Goal - All Large Excursions1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8 | 8 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 |  |  | 2 | 2
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 |  |  | 3 | 3
Actual - Total All Large OP | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 5 | 5
Goal - All Equipment Failure | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 4
Actual - All Equipment Failure | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 4 | 4
Goal - All Operator Error | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 4 | 4
Actual - All Operator Error | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 2 | 2
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 4 | 4 | New for 2018
Actual - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Goal - All Safety | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 4 | New for 2018
Actual - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 1
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events; Nov: Large OP Events | [8 empty] | Small OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2018 Goal |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 Target |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 YTD | 2018 Goal
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 16 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 6 |  | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 16
these tables are auto generated from the Charts tab
Charts tab must be updated monthly
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
2017 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 1 | 3 | 2 | 2 |  |  | 19 | 19
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 18
2018 Goal OP events | 8 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 1 |  |  | 10 | 10
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 0 | 5
2018 Goal - All Large OPs1 | 4 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8 | 8
| Jan: Total OP Events; Oct: Large Excursion OP Events | [5 empty] | Small Excursion OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 2 |  | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 |  | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 2 |  | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 |  | 8 | 4 | 6 | 3 | 2 | 4 | 6 | 3 |  | 104 | 70 | 14 | 7 | 11 | 4 | 6 | 6
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 |  | 21 | 8 | 11 | 7 | 7 | 10 | 10 | 5 |  | 754 | 301 | 21 | 11 | 22 | 8 | 9 | 13
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18; 10 ‘17: 21
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10; 10 ‘17: 11
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A60: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on P125: Singer, Kevin D: move pre month report
Note on P135: Singer, Kevin D: move per month report
Note on Y139: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14
Note on Z139: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14

## Tracking2014 by Month (hidden)
2014 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Expected Path: Goal OP events* | 3 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 3 |  |  | 24 | 24
Amber Goal - Lowest end of range* | 4 | 4 | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 4 | 4 |  |  | 36 | 36
Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18 |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Goal - HP Distribution Mains | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 2 | 1 |  |  | 9 | 9
Actual - HP Distribution Mains | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 |  |  | 5 | 5 |  |  | change these colors at End of Month
Goal - LP Distribution | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2
Actual - LP Distribution | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 |  |  | change these colors at End of Month | 0
Goal - Distribution Main Total | 2 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 2 | 1 |  |  | 11 | 11 |  |  |  | 1
Actual - Distribution Main Total | 3 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 |  |  | 7 | 7 |  |  | change these colors at End of Month | 2
Goal - Distribution Services Total | 2 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 2 | 1 |  |  | 11 | 11
Actual - Distribution Services Total | 3 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 |  |  | 7 | 7 |  |  | change these colors at End of Month | 3
Goal - Transmission | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 13 | 13
Actual - Transmission | 1 | 2 | 0 | 0 | 0 | 2 | 1 | 2 | 0 | 0 | 0 | 2 |  |  | 10 | 10 |  |  | change these colors at End of Month
Goal - All Large Excursions1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 9 | 9 |  |  | change these colors at End of Month
Actual - Large Excursions - HP Distrib | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 3 | 3
Actual - Large Excursions - LP Distrib | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Transmission | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  |  | 3 | 3
Actual - Total All Large Excursions | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
Goal - All Equipment Failure | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 |  |  | 12 | 12
Actual - All Equipment Failure | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 2 |  |  | 7 | 7
Goal - All Operator Error | [14 empty] | 12 | 12 | bar: Jan to Dec
Actual - All Operator Error | 1 | 2 | 0 | 0 | 1 | 2 | 0 | 2 | 0 | 0 | 0 | 0 |  |  | 8 | 8
Goal - At Compressor Stn or Storage | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |  |  | 4 | 4
Actual - At Compressor Stn or Storage | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  | 2 | 2
1 - Large Excursions are defined as:
HP Distribution = P ≥ MAOP + 10%
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MOP + 10 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events - Jan to Dec; Jul: Large Excursion OP Events - Jan to Dec | Small Excursion OP Events - Jan to Dec
| 2011 Actuals | 2012 Actuals | 2013 Actuals | 2014 Actuals | 2014 Goal |  | 2011 | 2012 | 2013 | 2014 | 2014 Goal |  | 2011 | 2012 | 2013 | 2014 | 2014 Goal
T&D Total | 774 | 308 | 32 | 18 | 24 |  | 36 | 8 | 10 | 7 | 9 |  | 738 | 300 | 22 | 11 | 15
these tables are auto generated from the Charts tab
Charts tab must be updated monthly
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
2014 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 66 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 774 | 774
2012 Actual - All Events | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 308 | 308
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 3 | 1 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2014 Goal OP events | 3 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 3 |  |  | 24 | 24
2011 Actual - Total All Large Excursions | 6 | 5 | 3 | 2 | 6 | 4 | 2 | 1 | 4 | 1 | 2 | 0 |  |  | 36 | 36
2012 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 8 | 8
2013 Actual - Total All Large Excursions | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 10 | 10
2014 Actual - Total All Large Excursions | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2014 Goal - All Large Excursions1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 9 | 9
| Jan: Total OP Events; Jul: Large Excursion OP Events | Small Excursion OP Events
| 2011 Actuals | 2012 Actuals | 2013 Actuals | 2014 YTD | 2014 Goals |  | 2011 | 2012 | 2013 Actuals | 2014 YTD | 2014 Goals |  | 2011 | 2012 | 2013 Actuals | 2014 YTD | 2014 Goals
HP Dist | 38 | 7 | 9 | 5 | 9 |  | 8 | 4 | 4 | 3 | 4 |  | 30 | 3 | 5 | 2 | 5
LP Dist | 624 | 228 | 3 | 2 | 2 |  | 3 | 0 | 1 | 0 | 0 |  | 621 | 228 | 2 | 2 | 2
Dist Total | 662 | 235 | 12 | 7 | 11 |  | 11 | 4 | 5 | 3 | 4 |  | 651 | 231 | 7 | 4 | 7
Trans | 112 | 73 | 19 | 10 | 13 |  | 25 | 4 | 5 | 3 | 5 |  | 87 | 69 | 14 | 7 | 8
T&D Total | 774 | 308 | 31 | 17 | 24 |  | 36 | 8 | 10 | 6 | 9 |  | 738 | 300 | 21 | 11 | 15
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A54: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on V59: Singer, Kevin D: update topics and year to date totals in concert with the table below
Note on P122: Singer, Kevin D: move pre month report
Note on P128: Singer, Kevin D: move per month report
Note on U132: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14

## CA's Tracking Report (hidden)
CAP ID | CAP Notification Text Title | Point Description/Location | OP/Near Hit | Date of Event | Task No. | Task Code | CAP Task Text Title | Short Description of Corrective Action/Task | Task Processor | Task WrkCtr | Task Status | Task Start Date | Task Due Date | Task Completed By | Task Completion Date | Risk | Notif WrkCenter | Notif Due Date | WT Group | WT Code | Notification Owner | Process | Asset Family | Division/District | Close Call? | Notif Owner Status | Notification System Stat | Extension # | Extension Authorize | Additional Comments
7000006 | Over Pressure - Low Pressure system | not present | OP | not present | 2 | CA | IA Audit - Low Pressure Reg Stn Inspect | All below grade LP Regulator and system relief stations will be inspected. Those that don’t have vents extended above ground will be modified. | MJKQ | GEPDG | TSRL | 2012-04-25 | 2016-12-31 |  |  | Medium 3-B | GESS | 2016-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL |  | unknown | ACCP | OSNO OSTS | 0
7000090 | Over Pressure - Low Pressure system - SJ | not present | OP | 2013-09-10 12:38 | 4 | CA | Upgrade valve system | Upgrade valve system to prevent valve from being operated beyond the closed position. Per recent audit of the corrective actions for this over pressure event (7005804) it has been determiend that the valve will be replaced during the beginning of December. See Email by Edgardo Ochoa | OXG3 |  | TSRL | 2014-10-31 | 2014-12-31 |  |  | High | GESS | 2015-01-31 | GAWTOPER | WOOP | DKM4 | PRGS | DISTMAINS | SJ | unknown | ACCP | NOPR NOPT OSTS | 0 |  | Reference Notification 7005804
7000046 | Network Issues Impacting Gas SCADA Oper | not present | Other | not present | 3 | CA | Upgrade/Replace Existing Gas SCADA |  | RPM4 | GESSO | TSRL | 2013-12-17 | 2016-01-31 |  |  | Medium 3-B | GESSO | 2016-01-31 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 0
7000046 | Network Issues Impacting Gas SCADA Oper | not present | Other | not present | 4 | CA | Verify and Doc Status of CAs | Verify and Document Status of Corrective Actions Identified in July 2013 Analysis Report: Many of the Corrective Action have been completed. Need to document actions, dates and any status of any outstanding corrective actions. Note that the Corrective Actions identified in July 2013 report were are recommendations and all are not necessarily prudent. | G1CR |  | TSRL | 2014-06-26 | 2014-11-01 |  |  | Medium 3-B | GESSO | 2016-01-31 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 3 | CA | Evaluate existing maintenance procedure | No additional Description | JLR9 | GEDT | TSRL | 2014-03-06 | 2015-03-20 |  |  | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 5.15.14 Design criteria has been initiated (Stations Group)
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 4 | CA | Gas Standard H-14 to be looked at | No additional Description | J011 | GACSG | TSRL | 2014-03-06 | 2015-03-20 |  |  | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 5.15.14 Design criteria has been initiated (Stations Group)
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 5 | CA | Clearances to reflect Mooney Regulation | Clearance committee to address Mooney regulation issues as to low differential lock up in regards to special instructions on clearance | KAS5 | GEST | TSRL | 2014-03-06 | 2015-03-20 |  |  | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 5.15.14 Design criteria has been initiated (Stations Group)
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 6 | CA | New OPP other than Mooney | New OPP for Mooney regulation other than Mooney to prevent drifting | JLR9 | GEDT | TSRL | 2014-03-06 | 2015-03-20 |  |  | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 5.15.14 Design criteria has been initiated (Stations Group)
7000131 | OP_Britton Ranch Washoe Ave Firebaugh | not present | OP | not present | 3 | CA | OPP not installed | OPP added to bypass run D/S of V-3 at Brittan "Y" | M8CN | GEPT | TSRL | 2013-06-17 | 2015-01-15 |  |  | Medium 3-B | GESS | 2015-01-30 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | YO | unknown | ACCP | OSNO OSTS | 2 |  | 6/19/14 - Email reminder sent out to responsible party - awaiting response.
7000132 | 3628_LT-177A_Over Pressurization | not present | OP | not present | 1 | CA | Tighter regulation controls | Replace the Mooney regulators (one regulation run) at Cummings Creek PLS with another 1/4" turn plug valve with a Becker Controller for better setpoint control on low flow situations on L-177 | MRDN | GAIFP | TSRL | 2013-06-19 | 2015-12-31 |  |  | Medium 3-B | GESS | 2016-01-15 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | HB | unknown | ACCP | OSNO OSTS | 0 |  | 6/19/14 - Email reminder sent out to responsible party - awaiting response.
7000279 | Over Pressure - Transmission - Modesto | not present | OP | not present | 2 | CA | Upgrade pipeline capacity | The recommendation is for LT&DP to add additional gas pipeline (gas supply) to the Ripon/Modesto DFM. There is to be additional gas supply added to Ripon/Modesto DFM by 2017. | RLP7 | GESPN | TSRL | 2013-05-16 | 2018-01-04 |  |  | Medium 3-B | GESS | 2018-02-04 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | TR | unknown | ACCP | OSNO OSTS | 0
7000784 | Erroneous SCADA alarms upon deployment | not present | Other | N/A | 4 | TA | Implement solution if feasible | There may not be a feasible solution | RPM4 | GESSO | TSRL | 2014-09-10 | 2014-12-20 |  |  | Low 4-B | GESSO | 2014-10-01 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 0
7000784 | Erroneous SCADA alarms upon deployment | not present | Other | N/A | 3 | TA | Identify possible solutions | No note at this time | RPM4 | GESSO | TSRL | 2014-08-10 | 2014-12-15 |  |  | Low 4-B | GESSO | 2014-10-01 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 0
7000784 | Erroneous SCADA alarms upon deployment | not present | Other | N/A | 2 | TA | Analyze cause of alarm floods | Settings reviewed and verified correct. Diagnostic code/logiging written and installed, however no alarm flood occurred on 8/27 deployment so no diagnositic info gathered. Analysis extended to 9/10 to caputure next flood | RPM4 | GESSO | TSRL | 2014-07-01 | 2014-11-30 |  |  | Low 4-B | GESSO | 2014-10-01 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | #REF! | OP | #REF! | 7 | CA | CA: Replace Station | Lomita Park station will be replaced in 2014… as the other two (Martin and Sullivan) have been replaced in the last two years… this is the final one on the list to be replaced on this system. This order number is 30859799. | SDK2 | GESS | TSRL | 2014-03-05 | 2015-01-30 |  |  | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0 |  | 4.14.14 Station is to be replaced in 2014
7002930 | SCADA Emerg Resp Valve Info Issues | not present | Other | N/A | 2 | CA | Update Area L2&L3 Area Displays |  | C2PP |  | TSRL | 2014-05-19 | 2014-11-01 |  |  | Medium 3-B | GESS | 2014-10-01 | GAWTOPER | WOSC | RPM4 | PRER | TRANSPIPE |  | unknown | ACCP | OSNO OSTS | 0
7003212 | Gas SCADA Change Requests | not present | Other | not present | - | - | Gas SCADA Change Requests | There is no form or process in place for requesting or tracking changes to the gas SCADA system beyond email exchanges with Gas Control Strategy & Support and the requesting party. With all of the rapid changes taking place with the gas system, we need a formal process for requesting display changes and corrections, and it would probably be a good idea to incorporate a formal review of these change requests to be sure they are correct before they are executed. In the past, a TSC form was used for this process, but no longer is being used, and it may not be adequate to the task anyway. http://www/tsconline/forms/ScadaGas/DispChangeOther. aspx | [7 empty] | Low 4-C | GESSO | 2014-12-31 |  |  | RPM4 | PRGS | OTHER
7003563 | Operating Modes of Topock and Hinkley | Topock Compressor Station Topock1 Plant B K Suct Press | OP | 2014-01-10 17:44 | 1 | CA | Operating Modes of Topock and Hinkley | Perform an assessment of Gas Control requested operating modes of Topock and Hinkley compressor stations to determine which requested modes are not documented and/or present significant risk for an operating error. Determine mitigation for risks and implement mitigation. For all other compressor stations around the system, survey the operating supervisors of those stations to determine if some operating modes at those stations create risk and what mitigation may be necessary. | DKM4 | GESS | TSRL | 2014-06-25 | 2017-12-31 |  |  | Medium 3-B | GESS | 2017-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | TP | unknown | REVW | OSNO OSTS | 0 |  | 6/26/2014 - During the Weekly OP Status Meeting on Thursday, Larry mentioned that CA's weren't assigned to a individual. Request for the appropriate task owner
7003563 | Perform PHA to Identify Safegaurds | Topock Compressor Station Topock1 Plant B K Suct Press | OP | 2014-01-10 17:44 | 3 | CA | Perform PHA to Identify Safegaurds | Perform PHA to identify and recommend appropriate safeguards for overpressure hazards for all modes of operation of the Topock compressor stations. Then, driven by the results of the survey, Gas Operations to establish procedures and training content for the most often encountered equipment specific abnormal operating condition | ARDD | GESS | TSRL | 2014-06-25 | 2017-12-31 |  |  | Medium 3-B | GESS | 2017-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | TP | unknown | REVW | OSNO OSTS | 0 |  | 6/26/2014 - During the Weekly OP Status Meeting on Thursday, Larry mentioned that CA's weren't assigned to a individual. Request for the appropriate task owner
7003563 | Reinforce Procedures on Gauging Ops | Topock Compressor Station Topock1 Plant B K Suct Press | OP | 2014-01-10 17:44 | 2 | CA | Reinforce Procedures on Gauging Ops | Reinforce procedures (with messaging to Gas T&D Operations) on gauging valves prior to manual operations, especially when valves are MAOP protection devices and are automatically controlled. | MDFL | GESS | TSRL | 2014-06-25 | 2017-12-31 |  |  | Medium 3-B | GESS | 2017-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | TP | unknown | REVW | OSNO OSTS | 0 |  | 6/26/2014 - During the Weekly OP Status Meeting on Thursday, Larry mentioned that CA's weren't assigned to a individual. Request for the appropriate task owner
7003662 | Gas Operations Technology Records | not present | Other | not present | - | - | Gas Operations Technology Records | Gas Control Strategy and Support does not have a system to create and centrally file records of technology and technology projects and initiatives for the control room. For example, records of the SCADA system, supporting technology and the video wall are not available proactively as part of projects. Sometimes they are created after a project is complete. The lack of records creates a knowledge gap when, for example experts leave the department and when clearances are to be evaluated. The records are a combinatio of inadequate, unavailable and incomplete. | [7 empty] | Low 4-C | GESSI | 2014-12-31 |  |  | GEG4 | PRIT | OTHER | EB
7004145 | M&C Gas JSSA & Tailboard Briefing | Vienna & Avalon SF | OP | 2013-05-06 10:00 | - | - | CA: Add language to inidcate the importance of over pressure event awareness in the Job Site Safety Tailboard | Add language to inidcate the importance of over pressure event awareness in the Job Site Safety Tailboard | [7 empty] | Low 4-C | GASCS | 2016-12-31 | [5 empty] | SF |  | ACCP |  |  |  | GCSS submitted a CAP suggesting JSSA document should have some context associated with bagging process and/or possible risk of OP
7004164 | C-37 Tapping, Bagging, etc - LP Gas Lines | Vienna & Avalon SF | OP | 2013-05-06 10:00 | - | - | CA: Last update was 1989 - update to current technologies or standard to modern time, to address over pressure events | Last update was 1989 - update to current technologies or standard to modern time, to address over pressure events | [7 empty] | Low 4-B | GASCD | 2016-12-31 | [5 empty] | SF |  | ACCP |  |  |  | GCSS submitted a CAP suggesting that Standard C-37 may need to be revised accordingly.
7004175 | Need Console Set up for GLS access | not present | Other | not present | - | - | Need Console Set up for GLS access | Request that gas strategy and support set up consoles that are not operational to have access to all GLS entries. At the present time if you are not logged in to a console you are unable to review GLS entries from alternate locations. 06/13/2014 09:15:55 Felina Lim (FPL3) Phone 925/328-5732 Risk Rationale: No threat to continuity of service 07/11/2014 10:38:02 Robert Mathews (RPM4) Phone 925/244-4573 Due date set at 9/1/14. Work on this has been in progress since Feb 2104 and is still undergoing testing. GDCC has the ability to look at the logs from SF or Brentwood from the log repository. The repository has all logs from all locations and all the operators have access to this shared drive. (Link: \\appgas01\Gas01\OPC\SHARE\GOCS) | [7 empty] | Low 4-B | GESSO | 2014-10-01 |  |  | RPM4 | PRGS | OTHER
7004358 | OP Event L172/169/167 N. of Hershey Sta | #REF! | OP | #REF! | 2 | CA | Removal of CROP on L172 | L-172, 167, and 169 are currently under a CROP of 708 psig. The removal of the CROP would potential restores MAOP/MOP of 800 psig that provides additional flexibility in avoiding OP events or near hits. The removal of the CROP on L-172, 167, 169 is to be determine. | K1BY |  | TSRL | 2014-07-09 | 2015-06-25 |  |  | Medium 3-B | GESS | 2015-06-25 |  | WOOP | DKM4 | PRIN | MEASCRTL | SA |  |  | OSNO OSTS
7004510 | Over pressure event -M-01 | #REF! | OP | #REF! | 4 | CA | Review Station Configuration | It was recommended by the local supervisor and also other subject matter experts during an OP Elimination Team meeting that Engineering design should review the reg station configuration. 08/14/2014 11:13:33 Jeffrey Cho (JHCQ) Phone 530/889-3191 THE FOLLOWING DOCUMENTATION WAS REQUESTED FROM T&R (G.ROBERTSON & J.GRACE). THIS DOCUMENTATION IS NECESSARY TO PERFORM ENGINEERING REVIEW: 1. Flow data at the time of the excursion, if available. 2. Pressure chart. 3. Did the RV activate? 4. Station configuration diagram (a sketch showing components and distances between them). 5. The CAP item comments (G.Robertson) state that a B-inspection was performed on this station in 2013 due to a similar event. We'll need the details of the event that triggered the B-inspection. | JHCQ |  | TSRL | 2014-07-29 | 2015-07-30 |  |  | Low 4-B | GESS | 2015-07-30 | GAWTOPER | WEER | DKM4 | PRIN | MEASCRTL | SI | unknown | ACCP | OSNO OSTS | 0 |  | Task Owner TBD
7004583 | OP Event Herrmann Station L-21 | #REF! | OP | #REF! | 7 | CA | CA: Rebuild Station | Currently there is a design critera to rebuild Herrmann Station, and convert its existing regulation to a dual run station. Rebuild station - there is a current design criteria to assess the rebuild of Herrmann Station. Based on the discussion with the Facilities engineer this will have the due date pushed out to 12/31/15 per past occurrences. the attached document is attached - and has not currently been approved in EDRS, but after this OP event, there will probably be additional push to complete the work. | JBCT |  | TSRL | 2014-07-15 | 2016-06-30 |  |  | Medium 3-B | GESS | 2016-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | NB |  | ACCP | OSNO OSTS
7004583 | OP Event Herrmann Station L-21 | #REF! | OP | #REF! | 6 | CA | CA: Update Documentation Consistency | Clarify the discrepancy between the OP diagram (MAOP 397 psig), and 086868 (from Crockett to MP 1.07 - MOP/MAOP 400/473 psig & MP 1.07 to Herrmann Station - MOP/MAOP 400/675 psig) Make the documentation consistent with the design criteria, op diagram, and 086868 | J3FB |  | TSRL | 2014-07-15 | 2016-06-30 |  |  | Medium 3-B | GESS | 2016-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | NB |  | ACCP | OSNO OSTS
7005066 | OP Near Hit Chestnut and Clay DREG | #REF! | Near Hit | #REF! | 6 | TA | TA: Engineering Analysis | Examine all stations (in the district) with SCADA and ER to determine if we have an OP risk. Special focus on those stations with common tap and sense lines and parallel runs. | BWW1 |  | TSRL | 2014-09-05 | 2015-11-01 |  |  | Medium 4-A | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | DISTMAINS | FR | true | ACCP | OSNO OSTS | 0
7005066 | OP Near Hit Chestnut and Clay DREG | #REF! | Near Hit | #REF! | 5 | CA | CA: Move SCADA tap line | Long term - Move the tap for SCADA to a location on the outlet pipe that is well downstream of the sense lines and outlet valves. | DABQ |  | TSRL | 2014-09-05 | 2015-11-01 |  |  | Medium 4-A | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | DISTMAINS | FR | true | ACCP | OSNO OSTS | 0
7005066 | OP Near Hit Chestnut and Clay DREG | #REF! | Near Hit | #REF! | 4 | CA | CA: Field Confirmation Testing | 1. Short term - Ensure that the following procedure is use for checking pressure at this station a. Check running reg and adjust pressure using the standard short line method. b. Switch the running reg and the standby reg by lowering the running reg set point to the standby reg set point. Then raise the standby reg to the normal running set point. c. Check the new running reg and adjust pressure using the short line method. | DABQ |  | TSRL | 2014-09-05 | 2015-11-01 |  |  | Medium 4-A | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | DISTMAINS | FR | true | ACCP | OSNO OSTS | 0
7005140 | DOLAN RD MAOP EXCEEDANCE L-301B V-0.01 | #REF! | OP | #REF! | 4 | TA | Review Gas Control Call-Out Process | The Dolan Rd Station Overpressure Event occurred after normal business hours, at approximately 0202. Gas Control did not contact the On-Call pipeline engineer per the current On-Call Schedule and process typically used. Gas Control called the area engineer, his supervisor, and an additional engineer from a nearby area. This delayed the response and could have resulted in further safety impacts. The on-call engineer was never contacted by Gas Control. Pipeline Services to communicate with Gas Control leadership and ensure all operators and coordinators are aware of the On-Call process and how to access the latest On-Call Schedule. | SRFA |  | TSOS | 2014-08-19 | 2014-12-31 |  |  | Medium 3-B | GESS | 2015-07-31 | GAWTOPER | WOGC | DKM4 | PRGS | MEASCRTL | CC | unknown | ACCP | OSNO OSTS | 0
7005190 | OP Near Hit Milpitas Terminal | #REF! | Near Hit | #REF! | 7 | CA | CA: Sequence of Operations | There have been instances in the recent past at Milpitas Terminal where valve operations by the control room, have led to near hit over pressure events (precautions to OP Events). Upon switching the primary feeds to back up - it would be beneficial for the GSO to review a sequence of operations relating to this terminal specifically. This sequence should be provided to the control room and additionally be reiterated in a tailboard fashion. | AJW2 |  | TSRL | 2014-12-31 | 2015-06-01 |  |  | Medium 4-A | GESS | 2015-06-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | MH | true | ACCP | OSNO OSTS | 0
7005190 | OP Near Hit Milpitas Terminal | #REF! | Near Hit | #REF! | 6 | CA | CA: Load/Trimmer Control | There was discussion of ways to optimize the load/trimmer valves control. We discussed split range control and modifications to the existing algorithm. We agreed that modifications to the existing algorithm is best; split range control has been implemented at any site and it is best to implement it first at a simpler site. Changing the algorithm will take several steps. Mark Kazimirsky will create the modification and we will bench test it prior to implementation on site. After bench testing, we will implement it with one load/trimmer set on site. We will test it an confirm its operation; this will require district and GSO support. Once its been tested, Mark will modify the remaining load/trimmer sets off site. We'll have a return trip implement the remaining load/trimmer sets This again will require district and GSO support. The estimates time required for this work - 7/5 calendar days, and 12.5 man-days. Project impact - This will provide improved operation of the load trimmer valves. Their control is functional now, but can be improved. | DXH0 |  | TSRL | 2015-03-01 | 2015-06-01 |  |  | Medium 4-A | GESS | 2015-06-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | MH | true | ACCP | OSNO OSTS | 0
7005190 | OP Near Hit Milpitas Terminal | #REF! | Near Hit | #REF! | 5 | CA | CA: MOP Limits | The MOP at the station are used to limit set point entries. The set point limits are currently based upon an MOP list that does not reflect operational restrictions. These set point limits must be reviewed and perhaps modified. Additionally, the MOP change seasonally, so the program may need to be modified to accommodate seasonal changes. Mark Kazimirsky will provide a list of the current set point limits and the MPs used to create them. Sherkan will review this list, and work with GSO to establish set point limit criteria. Once that is complete, we'll make any changes. Project impact - the programming effort will be small. | DXH0 |  | TSRL | 2014-12-31 | 2015-06-01 |  |  | Medium 4-A | GESS | 2015-06-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | MH | true | ACCP | OSNO OSTS | 0
7005190 | OP Near Hit Milpitas Terminal | #REF! | Near Hit | #REF! | 4 | CA | CA: Set point Ramp Rate | Currently there is a set point ramp rate, which ramps the actual set point to desired (operator entered)set point value, rather than instantly changing I to the desired set point. This means that, following a significant set point change, the actual set point takes up an hour to reach the desired set point. We decided to consider changing this to allow quicker set point changes. Sherkan, Steven and GSO will discuss this to determine whether to: modify the program to allow changes to the ramp rate, change the ramp rate, change the GSO methodology, or leave the system as is. Once they're completed their review, we'll make any changes. There will be no actions taken until that review and recommendation is complete. Project impact - if we move forward with program changes, there will be some impact on the current project. | SXEV |  | TSRL | 2014-12-31 | 2015-06-01 |  |  | Medium 4-A | GESS | 2015-06-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | MH | true | ACCP | OSNO OSTS | 0
7005261 | UDN computer lock-up | not present | Other | not present | - | - | UDN computer lock-up | UDN network computers at GDCC back-up site @ 77 Beale st require administrator access to diable the screen saver feature to keep maps and other needed information on the screen without them locking us out. Screen saver feature needs to be disabled or the time needs to be extended. | [7 empty] | Low 4-C | GESSO | 2014-10-31 |  |  | RPM4 | PRIT | OTHER
7005263 | OP Near Hit 2290 14th Ave ERX, SF | #REF! | Other | #REF! | 5 | CA | CA: New ERX Location | Does this ERX require a new location? OR we will be leaving it where it is. Due date moved out to June to give time to provide discussion if this is the right place for the ERX, comments should encompass this upon reaching a solution. | K2BB | GESS | TSRL | 2014-09-03 | 2015-06-12 |  |  | Medium 4-A | GESSC | 2015-06-12 | GAWTEQU | WETE | DKM4 | PRIN | MEASCRTL | SF | true | ACCP | OSNO OSTS | 0 |  | Reference Notification # 7005255
7005524 | OP Near Hit C Street Martinez | C Street, L191 Martinez | Near Hit | 2014-08-20 11:26 | 4 | TA | Update the OP diagram | Task: Update the OP diagram This task is to update the OP diagram with the most recent changes that have occurred since the last revision based on the redlines drawings. Responsible: Lanthy Le Date: 12/1/14 | L1LO |  | TSRL | 2014-10-01 | 2015-12-01 |  |  | Medium | GESS | 2015-12-25 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | DI | unknown | ACCP | OSNO OSTS | 0
7005431 | OP Event Acacia Station | Acacia Station | OP | 2014-08-16 08:50 | 2 | TA | TA: CAP to perform RC under 7005698 | A CAP item has been initiated (7005698) for a RCA to be preformed on this - as there have been 5 events in 2014 This will be assigned to Larry Rochholz | LNR3 | GESS | TSRL | 2014-09-03 | 2015-09-18 |  |  | Medium 3-B | GESS | 2015-09-18 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | ST | unknown | ACCP | OSNO OSTS | 0 |  | Reference Notification # 7005698
7005527 | 445 Wawona St. ERX | #REF! | Near Hit | #REF! | 5 | CA | CA: New ERX Location | (SF_SF_S026) Does this ERX require a new location? OR we will be leaving it where it is. | K2BB |  | TSRL | 2014-09-04 | 2015-06-12 |  |  | Medium 4-A | GESS | 2015-08-26 | GAWTEQU | WETE | DKM4 | PRIN | MEASCRTL | SF | true | ACCP | NOPT OSNO OSTS | 0 |  | Reference Notification # 7005255
7005721 | OP Near Hit Kettleman Compressor Station | #REF! | Near Hit | #REF! | 5 | TA | Evaluate Station Controlled Configs | Please add a task to evaluate the use of the station configurations that are controlled by the station PLC. See attached. If we do decide to utilize the configurations, testing will need to be performed to verify the configurations work correctly, since they haven't been used since the station was built | RPG8 |  | TSRL | 2014-10-17 | 2015-12-01 |  |  | Medium 4-A | GESS | 2014-12-01 | GAWTOPER | WOGC | DKM4 | PRGS | COMPPROC | KT | true | ACCP | OSNO OSTS | 0
7005804 | Effective Assessment CAPN 7000090 | not present | Near Hit | not present | 1 | TA | Create Effectiveness Evaluation | Upon completion of this CAP item, create a new notification due in 6 to 12 months to evaluate whether the corrective actions implemented to address this issue had the desired effect. The notification should include a plan to review the corrective actions for effectiveness. The effectiveness assessment should consider: a. Any effectiveness measures established in the cause evaluation, b. Whether the corrective actions have been properly integrated into controlling the processes/procedures to ensure the corrective actions are sustained over time, c. That corrective actions did not result in any new performance problems, d. Any potential weaknesses in the corrective actions. | DKM4 | GESS | TSRL | 2014-09-10 | 2015-02-01 |  |  | Non-CAP | GESS | 2015-03-01 | GAWTEVAL | WEOO | DKM4 | PRGS | DISTMAINS | SJ | unknown | ACCP | NOPT OSNO OSTS | 0 |  | Reference Notification # 7000090
7006231 | Gas SCADA Telecom Resiliency | not present | Near Hit | not present | 1 | CA | Develop Overall Plan to address |  | D3WN |  | TSOS | 2014-12-01 | 2015-02-01 |  |  | Medium | GESSO | 2015-03-01 | GAWTEQU | WETE | RPM4 | PRGS | MEASCRTL | ZS | unknown | ACCP | NOPT OSNO OSTS | 0
7006072 | OP Near Hit Crockett Station | Crockett Station | Near Hit | 2014-09-24 12:04 | 11 | CA | CA: Update OM&I | 1. The OM&I needs to provide adequate information of how the blow down piping is used and definitely needs to instruct that V-23 be closed prior to a transmission blow down if there is no OPP. The following language was provided by Harpreet Johal: "If V-23 is OPEN, the section of pipe between V-24, V-26, & V-30 should be considered distribution (MAOP 27.5 psig). If V-23 is CLOSED, the section of pipe between V-24, V-26, & V-30 can be considered transmission (MAOP 473 psig)." | TWS4 |  | TSRL | 2014-10-27 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | EB | unknown | ACCP | NOPT OSNO OSTS | 0
7006072 | OP Near Hit Crockett Station | Crockett Station | Near Hit | 2014-09-24 12:04 | 10 | CA | CA: Tag blow down valves at station | 2. Temporarily (or possibly even long term), it might be a good idea to put a tag on V-24, V-26 and V-30 instructing any operator to ensure V-23 is closed prior to opening these valves. | HSJ3 |  | TSRL | 2014-10-27 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | EB | unknown | ACCP | NOPT OSNO OSTS | 0
7006072 | OP Near Hit Crockett Station | Crockett Station | Near Hit | 2014-09-24 12:04 | 8 | CA | CA: Design - Plant Engineering | There was a recent over pressure near hit at Herrmann & Crockett Stations caused by some valve sequences - OP diagrams were not updated to show that a blow off stack was shared by distribution, and transmission pressures. Additionally the distribution pressure feed into the stack remained open during the transmission valve throttling without any specific OPP device. Distribution Gas Incident, Notification, and Abnormal Report: 092414 Crocket Overpressure Event Basically, by the OP Diagram at Crockett Station (284254.pdf), V-23 is kept open to maintain pressure in the blow down stack, and V-30 was throttled. The stack pipe is rated for the transmission pressure, in throttling V-30 caused pressure to back into the distribution system almost over pressuring it. OP diagram will be submitted for updating in the near future by the PLE. " Is there any consideration to update the design of the station and installation of an OPP device on the D system if V23 is normally open? o An alternate solution to OPP and create two valve separation between transmission and distribution pressure systems would be to install a valve between the tap valve location of V-23, and where the pipe from V-24 ties into the blow down stack pipe. " Does a situation like V-23 (open valve between GD and GT blowdown piping) occur at any other stations within our gas system? | DTY1 |  | TSRL | 2014-10-15 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | EB | unknown | ACCP | NOPT OSNO OSTS | 0
7006072 | OP Near Hit Crockett Station | Crockett Station | Near Hit | 2014-09-24 12:04 | 6 | CA | CA: Update the Operating Diagram | During the fact finding in this event, you guys mentioned you had made some updates to the operating diagram. I would like to capture, that the OP diagram is being updated - this will be accounted for through a task in CAP. Once the OP diagram has been updated by the mapping group, you can go in and close out the item (or send one of us an email). | TWS4 |  | TSRL | 2014-10-14 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | EB | unknown | ACCP | NOPT OSNO OSTS | 0
7006220 | OP Near Hit Ryer Island, Los Medanos | Los Medanos Ryer Island | Near Hit | 2014-09-26 21:23 | 5 | CA | CA: Controls Engineering | In response to the OP Near Hit (More Details mentioned below), a corrective action has come out of the fact finding session: - Engage Controls Engineering team to evaluate the Ryer Island controls, monitoring points and alarm limits for appropriateness and identification of potential improvements - Since gas is being supplied by a 3rd party do we want to address the pressure alarm limitss and better to the MAOP as opposed to a listed MOP? - Or since the BTU ratio controls that V-716, Hown can we better this situation so more events are not forthcoming? | L1LO |  | TSRL | 2014-10-02 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | LM | unknown | ACCP | NOPT OSNO OSTS | 0
7006220 | OP Near Hit Ryer Island, Los Medanos | Los Medanos Ryer Island | Near Hit | 2014-09-26 21:23 | 4 | CA | CA: Long term corrective actions | The following corrective actions are to be analyzed by the PLE for their use and purpose of updating and maintaing the system. - Currently there is no contract with Vintage about gas delivery specifications (pressure, BTU content) - Potentially install regulation - Update OP diagram/map with current information relating to the owner being Vintage (not Shell/Chevron) | L1LO |  | TSRL | 2014-10-02 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | LM | unknown | ACCP | NOPT OSNO OSTS | 0
7006929 | OP Near Hit Atwater ERX, YO | Atwater (ERX) | Near Hit | 2014-11-07 | 2 | TA | AC: Reg did not lock up |  |  |  | TSOS |  |  |  |  | Medium | GESS | 2015-01-15 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | YO | unknown | ACCP | NOPT OSNO OSTS | 0
7006929 | OP Near Hit Atwater ERX, YO | Atwater (ERX) | Near Hit | 2014-11-07 | 1 | TA | EC: Equipment - Sulfur |  |  |  | TSOS |  |  |  |  | Medium | GESS | 2015-01-15 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | YO | unknown | ACCP | NOPT OSNO OSTS | 0
7003740 | Network Outage at San Ramon ODN | not present | Other | N/A | 3 | CA | Corrective Actions for CE report |  | RPM4 | GESSO | TSRL | 2014-11-01 | 2014-12-31 |  |  | Low | GESSO | 2014-12-31 | GAWTEQU | WETE | RPM4 | PRGS | OTHER |  | true | ACCP | OSNO OSTS | 0
7006880 | Potential OP Event-Sunnyvale HP Syst | not present | Other | N/A | - | - | 11/05/2014 10:08:34 Boris Andino (BFA1) Phone 925/244-4505 Lo-Lo Alarm breached at 19 psig on 11/3/14. C16 reg point raised by 1 psig for capacity reasons. Concern that the MAOP of the system could be breached given that the NOP is 27, and MAOP 30 psig. Setting the regulator to 28 psig leaves only 2 psig as buffer potentially creating an OP event if the regulator droop for more than 2 psig. update 11/19/2014 Spoke with Planning Engineer Justin Lau regarding this issue. Alarm limits were originally set too high and have been adjusted down. 19 psig was still low for the system during this time of year and further investigation revealed that the regulator setpoints had drooped from 25 psig. They were reset to 25 psig later in the week. No further action should be needed. |  | - |  | COMP | - | - | MND4 | 2014-12-02 | Medium | GESS | 2014-12-06 | GAWTOPER | WOGC | FWM1 | PRIN | MEASCRTL | SJ | unknown
7003740 | Network Outage at San Ramon ODN | not present | Other | N/A | 1 | CE | psig for capacity reasons. Concern that the MAOP of the system could be | Create a CE report for the incident requested by SCADA Manager for Gas Ops 5/29/2014 | LNR3 | GFSC | TSCO | 2014-10-01 | 2014-11-01 | LNR3 | 2014-08-25 | Low 4-B | GESSO | 2014-12-31 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER |  | true | ACCP | OSNO OSTS | 0
7003679 | OP Near Hit PLS-6A, 300A | #REF! | Near Hit | #REF! | 5 | CA | breached given that the NOP is 27, and MAOP 30 psig. Setting the | Through investigation of the relief valve it was determined that the SCADA transmitter from the relief valve was faulty and malfunctioning. This is what caused the second alarm. It was determined that this should be replaced. | M7CV | GESS | TSCO | 2014-05-14 | 2015-01-31 | AMFQ | 2014-11-18 | Medium 3-B | GESS | 2015-03-30 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 1 | CA | regulator to 28 psig leaves only 2 psig as buffer potentially creating | Implement better control scheme using "Valve Max" and pressure set point control algorithm similar to PLS 1,2, and 3 RTUs. | GPJ6 | GEDTS | TSCO | 2013-10-11 | 2014-12-01 | GPJ6 | 2014-11-25 | Medium 3-B | GESS | 2015-01-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 1 | JGP1 | Recently reassigned to Geoffrey Jarpe (GJP6) per comments from CAP as a part of personnel changes - email sent 4/24/14
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 2 | CA | an OP event if the regulator droop for more than 2 psig. | Controls Engineering to review potential for similar problem for other PLS stations that do not have the PLS 3 type RU ramp program applied. | GPJ6 | GEDTS | TSCO | 2013-10-11 | 2014-12-01 | GPJ6 | 2014-11-25 | Medium 3-B | GESS | 2015-01-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 1 | JGP1 | Recently reassigned to Geoffrey Jarpe (GJP6) per comments from CAP as a part of personnel changes - email sent 4/24/14
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 3 | CA | Frank,can you please complete in less than 2 weeks if possible. | No additional Description | GPJ6 | GEDTS | TSCO | 2013-10-11 | 2014-12-01 | GPJ6 | 2014-11-25 | Medium 3-B | GESS | 2015-01-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 1 | JGP1 | Recently reassigned to Geoffrey Jarpe (GJP6) per comments from CAP as a part of personnel changes - email sent 4/24/14
7005932 | OP Near Hit Ridgecrest Town, Kern | #REF! | Near Hit | #REF! | 4 | CA | Thanks | Transducer is believed to be the issue, a new one has been ordered to replace existing | R2GT |  | TSCO | 2014-09-19 | 2014-12-01 | KDSD | 2014-11-26 | Medium 4-A | GESS | 2015-02-25 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | KE | unknown | ACCP | NOPT OSNO OSTS | 0
7002952 | OP Near Hit Harding & Hunter LP Stockton | Harding & Hunter LP | Near Hit | 2014-04-09 02:25 | 2 | CA | CA: Contact Planning Regarding SetPoints | According to the Abnormal Incident Report, Harding and Hunter HIHI alarm breach was due to the setpoints changed for summer operation. GDCC will let planning know. E-mail has been sent out to GDCC for some follow ups/updates, see attachment list. | TRST |  | TSCO | 2014-04-23 | 2014-12-09 | AMFQ | 2014-10-24 | Medium 3-B | GESS | 2014-12-09 | GAWTOPER | WOOP | DKM4
7004510 | Over pressure event -M-01 | #REF! | OP | #REF! | 3 | TA | Notifying Gas Control of OP Events | After the OP event was discovered, the local supervisor submitted a CAP Notification regarding the pressure excursion at Reg Station M-01 (American Rice Dryer) that meet standard TD-4413P-02 Section 3.10: "All over pressurization events must be entered in the CAP database by the responsible department supervisor, manager, or delegate in accordance with Utility Procedure TD-4020P-01, "Gas Operations Corrective Action Program (CAP) Instructions"" However, GDCC wasnt notified of the pressure excursion at Reg Station M-01. Lesson Learned - Upon determining that a potential over pressurization event has occurred, it must be immediately notify to Gas Transmission Control Center or Gas Distribution Control Center. (Per TD-4413P-02 Section 3.3) | BSS2 |  | TSCO | 2014-07-09 | 2014-12-06 | AMFQ | 2014-11-17 | Low 4-B | GESS | 2015-07-30 | GAWTEVAL | WEER | DKM4 | PRIN | MEASCRTL | SI | unknown | ACCP | OSNO OSTS | 0
7005059 | OP Near Hit Alameda SHP ERX | #REF! | Near Hit | #REF! | 3 | CA | CA: System Review | Division will review the system, and see if pressure should be lowered on other stations to prevent future alarming. | E1H7 | GESS | TSCO | 2014-09-19 | 2014-11-15 | KDSD | 2014-10-16 | Medium 4-A | GESS | 2014-11-15 | GAWTOPER | WOGC | DKM4 | PRGS | TRANSPIPE | EB | true | ACCP | OSNO OSTS | 0
7005059 | OP Near Hit Alameda SHP ERX | #REF! | Near Hit | #REF! | 6 | TA | TA: 5MM Bulleting about Settings | 5MM/Bulletin on Winter/Summer operations may need to be distributed |  |  | Unknown |  |  |  |  | Medium 4-A | GESS | 2014-11-15 | GAWTOPER | WOGC | DKM4 | PRGS | TRANSPIPE | EB | true | ACCP | OSNO OSTS | 0 |  | Task #6 is not in SAP CAP; this task will be considered remove
7005059 | OP Near Hit Alameda SHP ERX | #REF! | Near Hit | #REF! | 5 | TA | TA: Summer and Winter Settings | GDCC notify Divisions of Summer Winter Settings. - What is the process that has been developed? What needs to be done to affirm this gets done? Schedule through SAP as a task annually. (May be through temporary clearances or temporary operational set point changes). Local Engineering - GDCC - I&R |  |  | TSCO |  |  | KDSD | 2014-09-19 | Medium 4-A | GESS | 2014-11-15 | GAWTOPER | WOGC | DKM4 | PRGS | TRANSPIPE | EB | true | ACCP | OSNO OSTS | 0
7005059 | OP Near Hit Alameda SHP ERX | #REF! | Near Hit | #REF! | 4 | TA | TA: Historical Charts | Is there any additional historical reading throughout the summer that will show the over pressure event is accurate? Or chart? - Request from May 1st moving forward |  |  | TSCO |  |  | KDSD | 2014-09-19 | Medium 4-A | GESS | 2014-11-15 | GAWTOPER | WOGC | DKM4 | PRGS | TRANSPIPE | EB | true | ACCP | OSNO OSTS | 0
7005140 | DOLAN RD MAOP EXCEEDANCE L-301B V-0.01 | #REF! | OP | #REF! | 5 | CA | CA: PSRS 28501 - Dolan Rd Stat Rebuild | Option 2 - Expand scope of PSRS 28501 Dolan Rd Station Rebuild project scheduled for 2015 to include strength testing of this section of L-301B. Current scope is limited of valve extensions/gauge tap lines and atmosheric corrosion | SRFA |  | TSCO | 2014-08-26 | 2016-12-31 | KDSD | 2014-11-13 | Medium 3-B | GESS | 2016-12-31 | GAWTOPER | WOGC | DKM4 | PRGS | MEASCRTL | CC | unknown | ACCP | NOPT OSNO OSTS | 0 |  | Reference Notification # 80001790
7005258 | OP Near Hit Swingle Station | #REF! | Near Hit | #REF! | 3 | TA | CA: Mention Hand Throttling in Next 5MM | The apparent cause of this HIHI breach was due to the qiuck hand throttling of L-119A (V-11.07). In Clearance 80000549 it stated "Slowly Open" V-11.07, it appears the crew opened V -11.07 too quickly causing a HIHI at Swingle Station. When re-energizing a line, extra pre-caution should be considered in valve operation. In the next 5MM, valve operation (reopening and/or closing of valves) will be mentioned to remind field crew of potential OP. | AMFQ |  | TSCO | 2014-08-26 | 2015-12-31 | AMFQ | 2014-10-20 | Medium 4-A | GESS | 2015-12-31 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | SA | true | ACCP | OSNO OSTS | 0
7005489 | East Bay North SCADA Screen - ERRORS | not present | Other | not present | - | - | East Bay North SCADA Screen - ERRORS | There are errors on the East Bay North Citect SCADA screens. This is misleading and unsafe. The screen title is: East Bay - North (Lv3) There are two fields (one pressure and one flow) above the Herrmann field that are incorrect. The Vine Hill flows are also incorrect. Please reach out to me, KBH4, for more clarification. | [7 empty] | Low 4-B | GESSO | 2014-09-21 |  |  | RPM4 | PRGS | MEASCRTL | [6 empty] | Notification with no tasks/CA has been completed
7005556 | ERX HiHI alarm in SF | #REF! | Near Hit | #REF! | 3 | CA | CA: Share system pressure data with GDCC | See email attached... Way Ahead Work with Mike Fernande z and the GDCC to obtain approval for alarm set point increase at SCADA sites of higher elevation (IP) 09/16/2014 16:24:31 Michael Fernandez (MSFA) Phone 415/695-3312 Per email sent on 9/15/2014, Hi alarm set to 10"w.c. and Hi-Hi alarm set to 10.5"w.c. (consistent with Melissa Dunlap's email on alarm guidelines); however, the exception will be that if pressures exceed 10.5"w.c., immediate physical response would not be required by I &R. GDCC will notify local planner and I<(>&<)>R supervisor the next business day to coordinate response.These alarm set points can be also applied to the LP SCADA location at Taraval and Wawona as long as it is included as a location with the immediate response exception. | MSFA |  | TSCO | 2014-09-04 | 2014-12-29 | MSFA | 2014-09-16 | Medium 4-A | GESS | 2014-12-29 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | SF | true | ACCP | OSNO OSTS | 0
7005721 | OP Near Hit Kettleman Compressor Station | #REF! | Near Hit | #REF! | 4 | CA | CA: Address Training | Supervisor to address training in concerning this operating situation in the future with the GSO o Emphasis to use spill valves during the compression process during times when this operation is required in the future. | AJW2 |  | TSCO | 2014-09-04 | 2015-12-01 | KDSD | 2014-10-20 | Medium 4-A | GESS | 2014-12-01 | GAWTOPER | WOGC | DKM4 | PRGS | COMPPROC | KT | true | ACCP | OSNO OSTS | 0
7001410 | SCADA legacy field equip not reliable | not present | Other | not present | 1 | TA | EB Concentrator resolution plan | In talking with Wayne Fong this plan has been developed. As of 5/20 we are only waiting on Distribution to create orders for funding. | GPJ6 | GEDTS | TSCO | 2014-03-20 | 2014-05-01 | GPJ6 | 2014-05-20 | Medium 3-B | GESSO | 2015-06-01 |  |  | RPM4 | PRGS | MEASCRTL | EB |  | ACCP
7005161 | 1st Relo Exercise to SF Backup CTL CTR | not present | Other | not present | - | - | 1st Relo Exercise to SF Backup CTL CTR | SCADA Console on North desk was not functioning properly. The operator, Ray Cullins, reported that the SCADA Console was not abl to view data at Antioch terminal. Ray also reported all flows were displayed as #com. This issue was only visible on the North Console SCADA terminal. The reason this was a top priority was there was a major pigging operation occurring and it was imperativ that the operator was able to actively monitor pressures and flows. | [5 empty] | RPM4 | 2014-08-24 | Low 4-C | GESSO | 2014-09-07 | 5161 |  | RPM4 | PRGS | OTHER
7000371 | Over Pressure - Transmission - DFM 1024 | not present | OP | not present | 2 | CA | Clearance monitoring on DFM 1024-01 | Monitor system while on clearances. Possible solutions include install permanent or daily pressure check | J5LG | GAIFP | TSCO | 2013-09-30 | 2014-09-30 | KDSD | 2014-09-03 | Medium 3-B | GESS | 2014-09-30 | GAWTEQU | WEIR | DKM4 | PRIN | TRANSPIPE | NV | unknown | ACCP | OSNO OSTS | 0 |  | 6/19/14 - Email reminder sent out to responsible party - awaiting response.
7001745 | OP Near Hit Carmel Valley Reg Station | #REF! | Near Hit | #REF! | 1 | CA | CA: Confirm On-Call List | Confirm Carmel Valley on-call list has been establish | AMFQ |  | TSCO | 2014-02-18 | 2014-11-01 | AMFQ | 2014-08-27 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | CC | true | ACCP | NOPT OSNO OSTS | 0 |  | 4/24/14 - Emailed corrective action item owner to notify them of closing date is approaching soon 4/25/2014 - Emailed Tom Donabedian who was listed on TRAC's Need Help section for "Data Issues". Tom responsed on the same day that he hasn't been in the TRAC On-Call list loop for a while. He recommends that I contact TSC. A TSC Request Form was submitted and waiting for a response from TSC.
7005061 | OP Event Los Medanos SP3 | #REF! | Near Hit | #REF! | 4 | CA | CA: Replace Transducer | During the investigation - it was deteremined that the transducer (I to P) failed, affecting the regulator valve, and causing the station to go on monitor control. It is necessary to replace the transducer | DDT8 |  | TSCO | 2014-07-28 | 2014-12-01 | DDT8 | 2014-08-28 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | LM | unknown | ACCP | OSNO OSTS | 0
7005431 | OP Event Acacia Station | Acacia Station | OP | 2014-08-16 08:50 | 1 | TA | Update PSRS 27086 job to rebuild station | PSRS should track this in the future… See email from WAG8 attached. This task will be closed out | WAG8 |  | TSCO | 2014-08-19 | 2014-09-18 | KDSD | 2014-09-03 | Medium 3-B | GESS | 2015-09-18 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | ST | unknown | ACCP | OSNO OSTS | 0
7000006 | Over Pressure - Low Pressure system | not present | OP | not present | 1 | CA | QA Audit-Revise WP 4540-01 dwnstrm-mon |  | GES6 |  | TSCO TSSC | 2012-04-25 | 2013-12-31 | FPL3 | 2013-10-24 | Medium 3-B | GESS | 2016-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL |  | unknown | ACCP | OSNO OSTS | 0
7000006 | Over Pressure - Low Pressure system | not present | OP | not present | 3 | TA | Created in error |  |  |  | TSCO | 2013-10-28 | 2013-10-28 | G1W6 | 2013-10-28 | Medium 3-B | GESS | 2016-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL |  | unknown | ACCP | OSNO OSTS | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 1 | CA | Clearance rights suspended |  | KCC7 |  | TSCO | 2013-05-29 | 2013-05-30 | A3L2 | 2013-08-02 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 10 | CA | QC of Clearance Coordinator work |  | RBQ2 |  | TSCO | 2013-06-10 | 2014-03-30 | FPL3 | 2013-12-23 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 1 | CMPN
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 11 | CE | Create CE Report |  | LNR3 | GFSC | TSCO | 2013-04-11 | 2013-05-29 | RTG6 | 2013-06-11 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 12 | TA | coordinate |  | A3L2 |  | TSCO | 2013-11-12 | 2014-11-12 | A3L2 | 2014-02-25 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 13 | TA | EC: HF/WPE - Field O&M |  | KDSD | GESS | TSCO | 2014-03-06 | 2014-04-01 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 14 | TA | AC: Valves turned past stops |  | KDSD | GESS | TSCO | 2014-03-06 | 2014-04-01 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 2 | CA | Clearance identification points |  | KCC7 |  | TSCO | 2013-06-10 | 2013-06-24 | FPL3 | 2013-06-10 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 3 | CA | JSSA mandates |  | KCC7 |  | TSCO | 2013-06-10 | 2013-06-24 | TSN2 | 2013-06-10 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 4 | CA | Clearance Coordinator responsibilities |  | KAS5 |  | TSCO | 2013-06-10 | 2013-12-31 | FPL3 | 2013-12-24 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 5 | CA | Engineer review of clearances |  | RBQ2 | GEST | TSCO | 2013-06-10 | 2014-03-30 | LNR3 | 2014-03-25 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 1 | CMPN
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 6 | CA | Clearance qualifications |  | D0MN |  | TSCO | 2013-06-10 | 2013-06-17 | A3L2 | 2013-08-01 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 7 | CA | Inattention |  | D0MN |  | TSCO | 2013-06-10 | 2013-06-24 | A3L2 | 2013-08-12 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 8 | CA | Clearance detail |  | D0MN |  | TSCO | 2013-06-10 | 2013-07-31 | A3L2 | 2013-08-01 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 9 | CA | Workload for clearance writing |  | D0MN |  | TSCO | 2013-06-10 | 2013-09-09 | A3L2 | 2013-08-01 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 13 | TA | Develop action plan to address inadequate design validation | The action plan will detail the following, including assignment and due dates: Include confirmation of response to all regulator failure modes in the commissioning process. | JGP1 | GEDTS | TSCO | 2014-04-09 | 2014-12-31 | K1F7 | 2014-07-09 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 3 | JGP1 | • Due date changed from Jan 31st, 2014 to Dec 31st, 2014 by John Phillips • Further Discussion with William Mojica and other Directors
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 1 | CA | Incorporate lesons learned in CAP |  | SEP1 | GFSC | TSCO | 2013-04-09 | 2013-07-31 | TSN2 | 2013-08-07 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 10 | TA | Prepare action plan to address ineffective design verification | The action plan will detail the following (including assignments and due dates): 1. Develop a more formal design review process that requires sign-off by PG&E Engineering Supervision Evaluate current process for review and approval of Design Criteria, Construction Drawings and other engineering/design deliverables. 2. Update process to require sign-off by the appropriate engineering/design supervisor Prepare an Action Plan. | DTY1 | GEDTT | TSCO | 2013-04-09 | 2014-01-31 | K1F7 | 2014-05-01 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14 closed out: Mojica has reviewed and approved. Need to review and obtain approval from issue owner, Dan Menegus- (4/14/14 from Don)
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 11 | TA | Develop an action plan to develop and issue a standard design | The action plan will detail the following (including assignments and due dates): Develop and issue a standard design, including commissioning procedures, for the use of speed controls and DNGPs on regulator and monitor valves a) Prepare a guideline for Regulator Station Design. | DTY1 | GEDTT | TSCO | 2013-04-09 | 2014-01-31 | K1F7 | 2014-05-01 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14 closed out: Close this action after meeting with Dan Menegus
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 12 | TA | Develop an action plan to develop and issue a standard design | The action plan will detail the following including assignments and due dates: Develop and issue a standard design, including commissioning procedures, for the use of speed controls and DNGPs on regulator and monitor valves a) Prepare a guideline for Commissioning Regulator Stations. Needs to consider existing Utility Procedure TD-4550P-07, Gas Transmission Station Commissioning. Require sign-off approval of the Functional Checkout Procedure (FCP) prior to testing, and test acceptance upon completion of the testing, by both Engineering and Operations | JGP1 | GEDTS | TSCO | 2014-04-09 | 2014-12-31 | KDSD | 2014-06-25 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 3 | JGP1 | • Due date changed from Jan 31st, 2014 to Dec 31st, 2014 by John Phillips • Further Discussion with William Mojica and other Directors
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 14 | TA | Develop a weekly OP Event status call |  | SEP1 | GFSC | TSCO | 2013-04-09 | 2013-04-09 | TSN2 | 2013-04-09 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 15 | TA | Determine sourcing lead | Develop a receipt inspection process that assigns clear accountability for inspection of products/material received to assure compliance with what was ordered and is based on approved vendor drawings | DTY1 | GEDTT | TSCO | 2013-04-09 | 2014-01-31 | K1F7 | 2014-05-08 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14: Recommend opening a new notification and C/A - Follow up with Randy's successor, Ashikur Khan. 05/08/2014 it was closed out.
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 16 | TA | Determine appropriate owner within Gas C |  | SEP1 | GFSC | TSCO | 2013-04-09 | 2013-04-19 | SEP1 | 2013-10-29 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 2 | CA | Legacy Event 4009: Failure 1 Action 3 |  | K2MJ |  | TSCO | 2013-03-27 | 2013-03-27 | FPL3 | 2013-09-03 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 3 | CA | Legacy Event 4009: Failure 1 Action 1 |  | RRMV |  | TSCO | 2013-03-27 | 2013-03-27 | G1W6 | 2013-03-27 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 4 | CA | Legacy Event 4009: Failure 1 Action 2 |  | J1KS |  | TSCO | 2012-12-23 | 2012-12-23 | G1W6 | 2012-12-23 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 5 | CA | Ambiguous procedural requirements |  | DTY1 |  | TSCO | 2013-07-24 | 2013-08-31 | TSN2 | 2013-08-14 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 6 | CA | Ambiguous procedural requirements |  | DTY1 |  | TSCO | 2013-07-24 | 2013-09-30 | FPL3 | 2013-09-04 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 7 | CE | Create CE Report |  | RTG6 | GFSC | TSCO | 2013-03-20 | 2013-03-25 | RTG6 | 2013-03-20 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 8 | CE | Create CE Report |  | JXVB | GFSC | TSCO | 2013-05-28 | 2013-06-02 | RTG6 | 2013-06-11 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 9 | TA | Prepare action plan to address inadequat |  | MDO1 |  | TSCO | 2013-04-09 | 2013-12-31 | MDO1 | 2013-11-05 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | 2012-12-23 00:45 | 17 | CA | Research industry regs for press control | "Research industry rules and regulations, industry association guidelines, company standards and other sources of information" regarding the design, maintenance, and operation of pressure regulation stations. Terry White has hired an outside industry expert to perform this assessment. | TGW5 | GAIF | TSCO | 2013-12-16 | 2014-06-30 | TGW5 | 2014-06-06 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0 |  | Further Discussion with William Mojica and other Directors
7000046 | Network Issues Impacting Gas SCADA Oper | not present | Other | not present | 1 | TA | Coordinate |  | FPL3 | GFSC | TSCO | 2013-12-13 | 2014-12-31 | FPL3 | 2014-02-12 | Medium 3-B | GESS | 2016-01-31 | GAWTOPER | WOSC | DKM4 | PRGS |  |  | unknown | ACCP | OSNO OSTS | 0
7000046 | Network Issues Impacting Gas SCADA Oper | not present | Other | N/A | 2 | CA | Develop Corrective Action | Corrective Actions Identified in Cause Analysis: Analysis completed in July 2013 | RPM4 | GESSO | TSCO | 2013-11-15 | 2014-07-01 | RPM4 | 2013-08-01 | Medium 3-B | GESSO | 2016-01-31 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 2 | FPL3
7000090 | Over Pressure - Low Pressure system - SJ | not present | OP | not present | 1 | CE | Perform Cause Evaluation |  | JXVB | GFSC | TSCO | 2013-10-29 | 2013-11-08 | JXVB | 2013-11-07 | High 2-B | GESS | 2015-01-31 | GAWTOPER | WOOP | DKM4 | PRGS | DISTMAINS | SJ | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 4/21/14 Complete/Closed
7000090 | Over Pressure - Low Pressure system - SJ | not present | OP | not present | 2 | CA | Non-std locking device | Remove existing chain locking device. Install standard new locking device | OXG3 | GEOTA | TSCO | 2013-11-07 | 2013-12-31 |  | 2014-04-21 | High 2-B | GESS | 2015-01-31 | GAWTOPER | WOOP | DKM4 | PRGS | DISTMAINS | SJ | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 4/21/14 Complete/Closed E-mails has been sent out several time regarding this Corrective Action. It has been escalated to Manger. Frank will be contacting Kelly Ball regarding this overdue CA.
7000090 | Over Pressure - Low Pressure system - SJ | not present | OP | not present | 3 | CA | Upgrade valve system | Upgrade valve system to prevent valve from being operated beyond the closed position | OXG3 | GEOTA | TSCO | 2013-11-07 | 2014-12-31 |  | 2014-04-21 | High 2-B | GESS | 2015-01-31 | GAWTOPER | WOOP | DKM4 | PRGS | DISTMAINS | SJ | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 4/21/14 Complete/Closed E-mails has been sent out several time regarding this Corrective Action. It has been escalated to Manger. Frank will be contacting Kelly Ball regarding this overdue CA.
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 2 | CA | Update TD-4125P-06 for updates on relief | Standards and procedures to update standard TD-4125P-06 to address gas relief valves specifically | J011 | GACSG | TSCO | 2014-03-06 | 2015-03-20 | J011 | 2014-07-17 | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 0 |  | Jennifer Scroggins "Information in this CAP Notification is being transferred to ECTS document number TD-4125P-06 for further action"
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 1 | CE | Root Cause evaluation |  | LNR3 | GFSC | TSCO | 2013-10-29 | 2014-03-01 | LNR3 | 2014-03-06 | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 1 | A3L2
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 4 | TA | EC: HF/WPE - Gas Control |  | KDSD | GESS | TSCO | 2014-03-06 | 2014-05-31 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-05-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 0
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 5 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-06 | 2014-05-31 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-05-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 0
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 6 | TA | AC: Relief valve stuck 'open' position |  | KDSD | GESS | TSCO | 2014-03-06 | 2014-05-31 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-05-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 0
7000130 | 3669_LT-210C_ | not present | Other | 2013-05-21 14:38 | 5 | CA | Establish two MSAs | Entered on behalf of Roy Green. Establish 2 Master Service Agreements, one with Team Industrial and second with TDW for Gas Hot Tapping and Plugging Services. | RCGP | GECTN | TSRL | 2014-01-14 | 2014-06-30 | Reassigned to Pierre Bigras | Notification Reassigned | Medium 3-C |  | 2014-07-19 |  |  | DKM4 |  |  | NB | unknown | ACCP |  |  |  | 6/19/2014 - a reminder was sent via e-mail to the task owner regarding this item. On 07/09/2014, Larry contacted GCSS that this has been reassigned to any other Notification Owner Pierre Bigras. This line item will be considered others/not associated with GCSS and will not be track at this point.
7000130 | 3669_LT-210C_ | not present | Other | 2013-05-21 14:38 | 2 | TA | Develop Corrective Action Plan | Changed finish date per verbal from Pierre Bigras | JYB9 | GECTN | TSCO | 2013-11-06 | 2014-06-30 | AMFQ | 2014-07-07 | Medium 3-C |  | 2014-07-19 |  |  | DKM4 |  |  | NB | unknown | ACCP |  |  |  | 6/19/2014 - a reminder was sent via e-mail to the task owner regarding this item
7000130 | 3669_LT-210C_ | not present | Other | 2013-05-21 14:38 | 3 | CA | Contractor Vetting | Contractors to have certifications, job skills, and qualifications, checked prior to being awarded contracts. Changed finish date per verbal from Pierre Bigras | J2TA | GFC | TSCO | 2013-11-20 | 2014-06-30 | AMFQ | 7/3/014 | Medium 3-C |  | 2014-07-19 |  |  | DKM4 |  |  | NB | unknown | ACCP |  |  |  | 6/19/2014 - a reminder was sent via e-mail to the task owner regarding this item
7000131 | OP_Britton Ranch Washoe Ave Firebaugh | not present | OP | not present | 1 | CA | Communication gap |  | DRWI |  | TSCO | 2013-06-17 | 2013-06-28 | FPL3 | 2013-08-28 | Medium 3-B | GESS | 2014-09-18 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | YO | unknown | ACCP | OSNO OSTS | 0
7000131 | OP_Britton Ranch Washoe Ave Firebaugh | not present | OP | not present | 2 | CA | OPP not provided |  | DRWI |  | TSCO | 2013-06-17 | 2013-07-31 | FPL3 | 2013-08-28 | Medium 3-B | GESS | 2014-09-18 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | YO | unknown | ACCP | OSNO OSTS | 0
7000131 | OP_Britton Ranch Washoe Ave Firebaugh | not present | OP | not present | 4 | CE | Create CE Report |  | LNR3 | GFSC | TSCO | 2013-05-02 | 2013-06-27 | RTG6 | 2013-06-19 | Medium 3-B | GESS | 2014-09-18 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | YO | unknown | ACCP | OSNO OSTS | 0
7000132 | 3628_LT-177A_Over Pressurization | not present | OP | not present | 2 | CE | Create CE Report |  | LNR3 | GFSC | TSCO | 2013-04-30 | 2013-07-03 | RTG6 | 2013-06-18 | Medium 3-B | GESS | 2014-09-18 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | HB | unknown | ACCP | OSNO OSTS | 0
7000134 | Reg Stat Maint - Unplanned Outage/Fresno | not present | Other | not present | 1 | CE | Create CE Report |  | SMW7 | GFSC | TSCO | 2013-04-24 | 2013-06-26 | RTG6 | 2013-06-12 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOUP | DKM4 | PRGS | TRANSPIPE | FR | unknown | ACCP | ATCO OSNO | 0
7000134 | Reg Stat Maint - Unplanned Outage/Fresno | not present | Other | not present | 2 | CE | CE Please use HFACS |  | SMW7 | GFSC | TSCO | 2013-04-24 | 2013-06-26 | RTG6 | 2013-06-12 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOUP | DKM4 | PRGS | TRANSPIPE | FR | unknown | ACCP | ATCO OSNO | 0
7000136 | Over Pressure - Transmission Sacramento | not present | OP | not present | 1 | CA | Recalibrate |  | EKK4 |  | TSCO | 2013-07-01 | 2013-08-02 | TSN2 | 2013-08-19 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | SA | unknown | ACCP | OSNO OSTS | 0
7000136 | Over Pressure - Transmission Sacramento | not present | OP | not present | 2 | CA | design / Construct |  | RJWS | GAIFP | TSCO | 2013-07-01 | 2014-03-31 | TGW5 | 2014-03-28 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | SA | unknown | ACCP | OSNO OSTS | 0
7000136 | Over Pressure - Transmission Sacramento | not present | OP | not present | 3 | CA | Assessment |  | DRJ4 |  | TSCO | 2013-07-02 | 2013-12-31 | KLCP | 2013-12-30 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | SA | unknown | ACCP | OSNO OSTS | 0
7000136 | Over Pressure - Transmission Sacramento | not present | OP | not present | 4 | CE | Create CE Report |  | JXVB | GFSC | TSCO | 2013-04-08 | 2013-06-20 | RTG6 | 2013-06-20 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | SA | unknown | ACCP | OSNO OSTS | 0
7000136 | Over Pressure - Transmission Sacramento | not present | OP | not present | 5 | CA | Reduce NOP | No additional Description | TMRO | GEOTC | TSCO | 2013-12-30 | 2014-03-07 |  | 2014-04-18 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | SA | unknown | ACCP | OSNO OSTS | 0 |  | A reminder e-mail was sent out; however, Frank will be contacting Todd Rehrer regarding this overdue CA.
7000240 | Novato Blvd DFM Overpressure | not present | OP | not present | 1 | TA | Coordinate |  | KWD3 |  | TSCO | 2013-12-02 | 2014-12-02 | KWD3 | 2013-12-02 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | NB | unknown | ACCP | ATCO NOPT OSNO | 0
7000240 | Novato Blvd DFM Overpressure | not present | OP | not present | 2 | TA | AC: Excessive Sulfur that plugged plilot |  | AMFQ |  | TSCO | 2014-03-12 | 2014-03-12 | AMFQ | 2014-03-12 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | NB | unknown | ACCP | ATCO NOPT OSNO | 0
7000240 | Novato Blvd DFM Overpressure | not present | OP | not present | 3 | TA | AC: Low or No-Flow Conditions Mooney |  | AMFQ |  | TSCO | 2014-03-12 | 2014-03-12 | AMFQ | 2014-03-12 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | NB | unknown | ACCP | ATCO NOPT OSNO | 0
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 1 | CA | Design Criteria | Require that design criteria consider all regulator failure modes | KMKU | GEDTD | TSCO | 2013-07-12 | 2014-03-31 | KDSD | 2014-05-15 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0 |  | Confirm with Jarpe and Menegus. 5/15/2014 it was closed out.
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 2 | CA | Design Review Process | Develop a more formal design review process that requires sign-off by PG&E Engineering Supervision | DTY1 | GEDTT | TSCO | 2013-07-12 | 2014-01-31 | KDSD | 2014-05-08 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14 closed out: Close this action item after meeting with Dan Menegus
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 3 | CA | Develop Standard Design (GE/Becker) | Corrective action plan requires discussion to confirm scope of work. Develop and issue a standard design, including commissioning procedures for the GE-Becker DNGPs on regulator and monitor valves\. | DTY1 | GEDTT | TSCO | 2013-07-12 | 2014-01-31 | KDSD | 2014-05-08 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14 closed out: Refer to CAP Notification 7000728 description for discussion of changing from pressure control to flow control and impact on operatio of the regulator
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 4 | CA | Functional Checkout Procedure (FCP) |  | JGP1 |  | TSCO | 2013-07-12 | 2013-07-15 | FPL3 | 2013-09-06 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 5 | CA | Corrective Action Program |  | SEP1 | GFSC | TSCO | 2013-07-12 | 2013-07-15 | TSN2 | 2013-08-07 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 6 | CA | Power Gas Controls Configuration | Corrective action plan requires discussion to confirm scope of work. Develop and implement a process to verify power gas controls are configured correctly for all similar actuator configurations. | DTY1 | GEDTT | TSCO | 2013-07-12 | 2014-01-31 | KDSD | 2014-05-08 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 1 | FPL3 | 5/6/14: closed out: Confirm with Dan Menegus
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 7 | CA | Validation | Corrective action plan requires discussion to confirm scope of work. The action plan will detail the following: 1. Verification of response to all regulator failure modes 2. Verification of response in all environmental conditions 3. Continue RCA of GE-Becker actuator system | DTY1 | GEDTT | TSCO | 2013-07-12 | 2014-01-31 | KDSD | 2014-05-08 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 1 | FPL3 | 5/8/14 closed out: Close this action item after meeting with Dan Menegus
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 8 | CA | Validation | Corrective action plan requires discussion to confirm scope of work. The action plan will detail the following: 1. Determine if new regulation is required at Creed Station if TD-4430-B rev. 1 cannot be implemented on L-210. 2. Continue to investigation as to origin of unanticipated system upset | DTY1 | GEDTT | TSCO | 2013-07-12 | 2014-01-31 | KDSD | 2014-04-28 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14 closed out: Close this action item after meeting with Dan Menegus
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 9 | CE | Create CE Report |  | JXVB | GFSC | TSCO | 2013-06-04 | 2013-06-09 | RTG6 | 2013-06-19 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000279 | Over Pressure - Transmission - Modesto | not present | OP | not present | 1 | CA | Gauging inadequate |  | JGJ4 |  | TSCO | 2013-05-16 | 2013-05-29 | FPL3 | 2013-08-02 | Medium 3-B | GESS | 2018-02-04 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | TR | unknown | ACCP | OSNO OSTS | 0
7000279 | Over Pressure - Transmission - Modesto | not present | OP | not present | 3 | CA | Supervisory observation |  | JGJ4 |  | TSCO | 2013-05-16 | 2013-07-17 | FPL3 | 2013-09-01 | Medium 3-B | GESS | 2018-02-04 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | TR | unknown | ACCP | OSNO OSTS | 0
7000279 | Over Pressure - Transmission - Modesto | not present | OP | not present | 4 | CE | Create CE Report |  | LNR3 | GFSC | TSCO | 2013-04-11 | 2013-06-28 | RTG6 | 2013-05-16 | Medium 3-B | GESS | 2018-02-04 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | TR | unknown | ACCP | OSNO OSTS | 0
7000330 | Over Pressure - Low Pressure system | not present | Near Hit | not present | 1 | CA | CA: Replacing RTU at the location | The existing RTU at 34th and Telegraph, Oakland is to be replaced with a new RTU | LXPM | GECDE | TSCO | 2013-04-29 | 2014-05-16 | M4S6 | 2014-03-31 | Medium 3-B | GESS | 2014-05-31 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | EB | unknown | ACCP | OSNO OSTS | 1 | AMFQ | 4/24/14 - JO number 30988380 was provided on 4/3/14 - check back if comepleted at the beginning of May. SAP does not show this is completed as of 4/24/14 4/30/14 - E-mailed Tasha Capen to obtain an update on the RTU replacement at 34th and Telegraph 5/21/14 - Closed out by Matt Sanders and suggest a new task for Michael Graham (MRG2) should be created to follow up on bringing the RTU back online.
7000330 | Over Pressure - Low Pressure system | not present | Near Hit | not present | 2 | CE | Create CE Report |  | LNR3 | GFSC | TSCO | 2013-04-11 | 2013-05-03 | RTG6 | 2013-04-29 | Medium 3-B | GESS | 2014-05-31 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | EB | unknown | ACCP | OSNO OSTS | 0
7000330 | Over Pressure - Low Pressure system | not present | Near Hit | not present | 3 | TA | AC: Comm Failure |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-05-31 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | EB | unknown | ACCP | OSNO OSTS | 0
7000330 | Over Pressure - Low Pressure system | not present | Near Hit | not present | 4 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-05-31 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | EB | unknown | ACCP | OSNO OSTS | 0
7000333 | Over Pressure - Transmission - Antioch | not present | OP | not present | 1 | CA | Communication |  | AJW2 |  | TSCO | 2012-12-13 | 2012-12-13 | FPL3 | 2013-07-29 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | LM | unknown | ACCP | OSNO OSTS | 0
7000333 | Over Pressure - Transmission - Antioch | not present | OP | not present | 2 | CA | Communication/Change settings |  | AJW2 |  | TSCO | 2012-12-13 | 2012-12-13 | FPL3 | 2013-07-29 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | LM | unknown | ACCP | OSNO OSTS | 0
7000333 | Over Pressure - Transmission - Antioch | not present | OP | not present | 3 | CA | Implement 5/20 plan | Implement 5/20 rule for SP3 to potentially prevent future over pressure events | GJG3 | GESPB | TSCO | 2012-12-13 | 2014-03-31 |  | 2014-04-01 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | LM | unknown | ACCP | OSNO OSTS | 0
7000333 | Over Pressure - Transmission - Antioch | not present | OP | not present | 4 | CE | Complete Causal evaluation |  | LNR3 | GFSC | TSCO | 2012-12-13 | 2013-01-18 | LNR3 | 2012-12-13 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | LM | unknown | ACCP | OSNO OSTS | 0
7000371 | Over Pressure - Transmission - DFM 1024 | not present | OP | not present | 1 | CA | Adjust Regs to meet manufacturers specs | Establish a regulation and safety system that ensures operational load meets manufacturer's spec. Possible solutions include: 1. Replace regulators with recommended manufacturer's spec (correct size) 2. Uprate L-177B and DFM 1024-01 with L-177A MAOP at 819 psig and eliminate Grape Way Reg Station | J5LG | GAIFP | TSCO | 2013-09-30 | 2014-09-30 | KDSD | 2014-06-19 | Medium 3-B | GESS | 2014-09-30 | GAWTEQU | WEIR | DKM4 | PRIN | TRANSPIPE | NV | unknown | ACCP | OSNO OSTS | 0 |  | 6/19/14 - Email reminder sent out to responsible party - awaiting response. 6/19/2014 - Completed
7000723 | Gas Control/Gas Dispatch Phone Issues | N/A | Other | N/A | 2 | TA | Develop Corrective Action Plan |  | NXF5 | GESSO | TSCO | 2013-12-16 | 2014-07-01 | FPL3 | 2014-06-25 | Medium 4-A | GESSO | 2014-08-01 | GAWTOPER | WOGC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 2 | RPM4
7001195 | OP Near Hit Station # R-H02 Richmond | #REF! | Near Hit | #REF! | 1 | TA | Coordinate Corrective Actions |  | LNR3 |  | TSCO | 2014-01-09 | 2014-03-01 | LNR3 | 2014-02-28 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | EB | true | ACCP | ATCO OSNO | 0
7001195 | OP Near Hit Station # R-H02 Richmond | #REF! | Near Hit | #REF! | 2 | TA | AC: Work Procedure |  | KDSD | GESS | TSCO | 2014-03-12 | 2014-03-12 | KDSD | 2014-03-12 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | EB | true | ACCP | ATCO OSNO | 0
7001195 | OP Near Hit Station # R-H02 Richmond | #REF! | Near Hit | #REF! | 3 | CA | CA: Training Tailboard |  | KDSD |  | TSCO | 2014-03-12 | 2014-12-02 | AMFQ | 2014-03-24 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | EB | true | ACCP | ATCO OSNO | 0
7001210 | OP near hit - Paramount Farm D/S of V-18 | #REF! | Near Hit | #REF! | 1 | TA | Coordinate |  | JXVB |  | TSCO | 2014-01-07 | 2014-12-31 | JXVB | 2014-01-07 | Low 4-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | YO | true | ACCP | ATCO OSNO | 0
7001210 | OP near hit - Paramount Farm D/S of V-18 | #REF! | Near Hit | #REF! | 2 | CA | CA: Update MOP on Op Diagram |  | TXPS | GESS | TSCO | 2014-01-07 | 2014-06-30 | TXPS | 2014-03-20 | Low 4-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | YO | true | ACCP | ATCO OSNO | 0
7001210 | OP near hit - Paramount Farm D/S of V-18 | #REF! | Near Hit | #REF! | 3 | TA | AC: Leaking Valve |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Low 4-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | YO | true | ACCP | ATCO OSNO | 0
7001210 | OP near hit - Paramount Farm D/S of V-18 | #REF! | Near Hit | #REF! | 4 | TA | EC: Equpiment - Other |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Low 4-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | YO | true | ACCP | ATCO OSNO | 0
7001210 | OP near hit - Paramount Farm D/S of V-18 | #REF! | Near Hit | #REF! | 5 | TA | EC: HF/WPE - Other |  | AMFQ |  | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Low 4-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | YO | true | ACCP | ATCO OSNO | 0
7001256 | OPE Concord Mtr Station D/S of V-12 & 13 | #REF! | OP | #REF! | 1 | TA | Coordinate |  | LNR3 |  | TSCO | 2014-01-10 | 2015-01-10 | LNR3 | 2014-03-14 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | DI | unknown | ACCP | ATCO OSNO | 0
7001315 | Topock Suction Pipe OP 2 Events-1/10/14 | not present | OP | not present | 1 | TA | Coordinator for OP at Topock |  | LNR3 |  | TSCO | 2014-01-15 | 2014-03-01 | LNR3 | 2014-02-27 | Medium 3-B | GESS |  | GAWTOPER | WOOP | DKM4 | PRGS | COMPPROC | TP | unknown | ACCP | ATCO OSNO | 0
7001315 | Topock Suction Pipe OP 2 Events-1/10/14 | not present | OP | not present | 2 | CE | Coordinate interviews. |  | LNR3 |  | TSCO | 2014-01-17 | 2014-03-16 | LNR3 | 2014-03-07 | Medium 3-B | GESS |  | GAWTOPER | WOOP | DKM4 | PRGS | COMPPROC | TP | unknown | ACCP | ATCO OSNO | 1 | LNR3
7001340 | OP Eureka LP System | #REF! | OP | #REF! | 1 | TA | Gas OP on LP system in Eureka |  | LNR3 |  | TSCO | 2014-01-16 | 2014-03-01 | LNR3 | 2014-02-27 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | HB | unknown | COMP | ATCO NOPT OSNO | 0
7001340 | OP Eureka LP System | #REF! | OP | #REF! | 2 | TA | AC: Reg & Monitor set point too close |  | AMFQ |  | TSCO | 2014-03-11 | 2014-03-11 | AMFQ | 2014-03-11 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | HB | unknown | COMP | ATCO NOPT OSNO | 0
7001340 | OP Eureka LP System | #REF! | OP | #REF! | 3 | CA | CA: Reg Set Point Lowered to 8" WC |  | WDBA |  | TSCO | 2014-03-19 | 2014-03-19 | AMFQ | 2014-03-19 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | HB | unknown | COMP | ATCO NOPT OSNO | 0
7001340 | OP Eureka LP System | #REF! | OP | #REF! | 4 | CA | CA: Increase MAOP to 14" WC |  |  |  | TSCO | 2014-03-19 | 2014-03-19 | AMFQ | 2014-03-19 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | HB | unknown | COMP | ATCO NOPT OSNO | 0
7001390 | Overpressure Event 4022- El Dorado Hills | not present | OP | not present | 1 | CA | Ensure facilities comply w/ Gas Std H-14 | Develop program to bring Mooney Regs max 350psig differential in compliance with GS H-80.3 | TGW5 |  | TSCO | 2014-04-01 | 2014-05-01 |  | 2014-04-22 | Medium 3-B | GESS | 2014-05-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | SI | unknown | ACCP | NOPR OSTS | 0
7001442 | Swingle Station "Overpressure" 1-29-14 | #REF! | Near Hit | #REF! | 1 | TA | AC: Hand Throttle Valve |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GAIFP |  | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SA | unknown | REVW | OSNO OSTS | 0
7001442 | Swingle Station "Overpressure" 1-29-14 | #REF! | Near Hit | #REF! | 2 | TA | EC: HF/WPE - Field O&M |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GAIFP |  | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SA | unknown | REVW | OSNO OSTS | 0
7001442 | Swingle Station "Overpressure" 1-29-14 | #REF! | Near Hit | #REF! | 3 | CA | CA: Tailboard Prior to the Clearance |  | OXM1 |  | TSCO | 2014-03-05 | 2014-03-31 |  | 2014-04-02 | Medium 3-B | GAIFP |  | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SA | unknown | REVW | OSNO OSTS | 0
7001532 | OP Event Center St. DFM Press | #REF! | OP | #REF! | 1 | TA | AC: 8" Mooney Reg Optimum Range 10-80% |  | AMFQ |  | TSCO | 2014-03-19 | 2014-03-19 | AMFQ | 2014-03-19 | Medium 3-B | GESS | 2014-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | EB | unknown | ACCP | ATCO NOPT OSNO | 0
7001532 | OP Event Center St. DFM Press | #REF! | OP | #REF! | 2 | CA | CA: Lowered Reg Down |  | DMRU |  | TSCO | 2014-03-19 | 2014-03-19 | AMFQ | 2014-03-19 | Medium 3-B | GESS | 2014-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | EB | unknown | ACCP | ATCO NOPT OSNO | 0
7001546 | OP Near Hit Brentwood Terminal | #REF! | Near Hit | #REF! | 2 | TA | AC: Leaking Valve |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | DI | true | ACCP | OSNO OSTS | 0
7001546 | OP Near Hit Brentwood Terminal | #REF! | Near Hit | #REF! | 3 | TA | EC: Equipment - Other |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | DI | true | ACCP | OSNO OSTS | 0
7001546 | OP Near Hit Brentwood Terminal | #REF! | Near Hit | #REF! | 1 | CA | CA: Validate & Update MAOP Doc | Validate the MAOP D/S of V-65 in Brentwood Terminal to be 867 psig in accordance with PG&E standards and work with Mapping in updating operating diagram | SXEV |  | TSCO | 2014-02-19 | 2014-06-30 | SXEV | 2014-06-26 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | DI | true | ACCP | OSNO OSTS | 0 |  | 4/25/2014 - Sherkan has contacted the lead Map Tech and waiting for a response from the Map Tech. More follow up from Sherkan is anticipated regarding this CA. 5/30/2014 - Will be completed within the next couple of weeks from an email sent by the task owner
7001745 | OP Near Hit Carmel Valley Reg Station | #REF! | Near Hit | #REF! | 2 | TA | AC: Gauge Accuracy |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | CC | true | ACCP | NOPT OSNO OSTS | 0
7001745 | OP Near Hit Carmel Valley Reg Station | #REF! | Near Hit | #REF! | 3 | TA | EC: Equipment - Other |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | CC | true | ACCP | NOPT OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | #REF! | OP | #REF! | 1 | TA | AC: Mon. and Reg. set points too close |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | #REF! | OP | #REF! | 2 | TA | AC: Monitor set incorrectly: clearance? |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | #REF! | OP | #REF! | 3 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | #REF! | OP | #REF! | 4 | TA | EC: HF/WPE - Field O&M |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | #REF! | OP | #REF! | 5 | TA | EC: Set Point to close to MOP |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | #REF! | OP | #REF! | 6 | CA | CA: Immediate Response |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7002021 | OP Near Hit at West Capital & 5th in Sac | #REF! | Near Hit | #REF! | 1 | CA | CA: Repair Phone Line |  | TMRO | GESS | TSCO | 2014-02-25 | 2014-08-31 |  | 2014-04-18 | Low 4-D | GESS | 2014-12-01 | GAWTOPER | WOSC | DKM4 | PRIN | MEASCRTL | SA | unknown | ACCP | OSNO OSTS | 0 |  | A reminder e-mail was sent out; however, Frank will be contacting Todd Rehrer regarding this overdue CA.
7002021 | OP Near Hit at West Capital & 5th in Sac | #REF! | Near Hit | #REF! | 2 | TA | AC: Phone Line Failure |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Low 4-D | GESS | 2014-12-01 | GAWTOPER | WOSC | DKM4 | PRIN | MEASCRTL | SA | unknown | ACCP | OSNO OSTS | 0
7002021 | OP Near Hit at West Capital & 5th in Sac | #REF! | Near Hit | #REF! | 3 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Low 4-D | GESS | 2014-12-01 | GAWTOPER | WOSC | DKM4 | PRIN | MEASCRTL | SA | unknown | ACCP | OSNO OSTS | 0
7002166 | OP Near Hit Los Banos #4 | #REF! | Near Hit | #REF! | 1 | TA | AC: Calibration Issues |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-07-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | YO | true | ACCP | OSNO OSTS | 0
7002166 | OP Near Hit Los Banos #4 | #REF! | Near Hit | #REF! | 2 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-07-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | YO | true | ACCP | OSNO OSTS | 0
7002166 | OP Near Hit Los Banos #4 | #REF! | Near Hit | #REF! | 3 | CA | CA: Replace transducer at reg station | Transducer is to be replaced | JNL4 | GESS | TSCO | 2014-03-05 | 2014-06-01 |  | 2014-04-24 | Medium 3-B | GESS | 2014-07-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | YO | true | ACCP | OSNO OSTS | 0 |  | 4/24/14 - JO number 42078493 was provided on 3/6/14 - check back if comepleted at the beginning of May. Construction complete 4/8/14 - task not yet closed in SAP, CAP will close this out based on the information provided
7002167 | OP Near Hit 22nd and 24th Dist, SAC | #REF! | Near Hit | #REF! | 1 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-07 | 2014-06-06 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRGS | MEASCRTL | SA | true | COMP | ATCO NOPR | 0
7002167 | OP Near Hit 22nd and 24th Dist, SAC | #REF! | Near Hit | #REF! | 2 | TA | AC: Gauge Accuracy/Calibration |  | KDSD | GESS | TSCO | 2014-03-07 | 2014-06-07 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRGS | MEASCRTL | SA | true | COMP | ATCO NOPR | 0
7002167 | OP Near Hit 22nd and 24th Dist, SAC | #REF! | Near Hit | #REF! | 3 | CA | CA: Replace Transducer |  | TMRO | GESS | TSCO | 2014-03-07 | 2014-03-07 | AMFQ | 2014-03-07 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRGS | MEASCRTL | SA | true | COMP | ATCO NOPR | 0
7002300 | OP Near Hit Los Medanos Ryer Island | #REF! | Near Hit | #REF! | 1 | TA | AC: Typical Operation |  | AMFQ |  | TSCO | 2014-03-19 | 2014-04-01 |  | 2014-04-01 | Medium 3-B | GESS |  | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | DI | true | ACCP | OSNO OSTS | 0
7002301 | OP Near Hit Aborn & White L100 San Jose | #REF! | Near Hit | #REF! | 1 | TA | AC: Low or No-Flow Conditions |  | AMFQ |  | TSCO | 2014-03-19 | 2014-03-25 | AMFQ | 2014-03-25 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | ATCO OSNO | 0
7002301 | OP Near Hit Aborn & White L100 San Jose | #REF! | Near Hit | #REF! | 2 | CA | CA: Lowered Mixer Press Milpitas Term |  | AMFQ |  | TSCO | 2014-03-19 | 2014-03-19 | AMFQ | 2014-03-19 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | ATCO OSNO | 0
7002401 | Over pressure event Rocklin 3-12-14 | #REF! | OP | #REF! | 1 | TA | AC: Low or No-Flow Conditions |  | AMFQ |  | TSCO | 2014-03-19 | 2014-03-19 |  | 2014-04-01 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | SI | unknown | REVW | NOPT OSNO OSTS | 0
7002454 | OP Near Hit Almaden & Redmond San Jose | #REF! | Near Hit | #REF! | 1 | TA | AC: SP Too Close to MOP/HiHi |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-12-31 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-12-31 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002454 | OP Near Hit Almaden & Redmond San Jose | #REF! | Near Hit | #REF! | 2 | TA | EC: Within SCADA Accuracy |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-12-31 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-12-31 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002454 | OP Near Hit Almaden & Redmond San Jose | #REF! | Near Hit | #REF! | 3 | CA | CA: Maintenance Required | Maintenance to establish 0-100% calibration | OXG3 | GESS | TSCO | 2014-03-21 | 2014-12-31 |  | 2014-04-21 | Medium 3-B | GESS | 2014-12-31 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out E-mails has been sent out several time regarding this Corrective Action. It has been escalated to Manger. Frank will be contacting Kelly Ball regarding this overdue CA.
7002455 | OP Near Hit Almaden & Redmond San Jose | #REF! | Near Hit | #REF! | 1 | TA | AC: SP Too Close to MOP/HiHi |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-04-21 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-04-21 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002455 | OP Near Hit Almaden & Redmond San Jose | #REF! | Near Hit | #REF! | 2 | TA | EC: SP Too Close to MOP |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-04-21 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-04-21 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002455 | OP Near Hit Almaden & Redmond San Jose | #REF! | Near Hit | #REF! | 3 | TA | AC: Within SCADA Accuracy |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-04-21 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-04-21 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002455 | OP Near Hit Almaden & Redmond San Jose | #REF! | Near Hit | #REF! | 4 | CA | CA: Maintenance Required | Maintenance to establish 0-100% calibration | OXG3 |  | TSCO | 2014-03-24 | 2014-04-21 |  | 2014-04-21 | Medium 3-B | GESS | 2014-04-21 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out E-mails has been sent out several time regarding this Corrective Action. It has been escalated to Manger. Frank will be contacting Kelly Ball regarding this overdue CA.
7002457 | OP Near Hit Redding Tap L-402 | #REF! | Near Hit | #REF! | 1 | TA | EC: Design Issue - Other |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-06-30 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE |  | true | REVW | ATCO OSNO | 0
7002457 | OP Near Hit Redding Tap L-402 | #REF! | Near Hit | #REF! | 2 | TA | AC: Low flow or no flow conditions |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-06-30 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE |  | true | REVW | ATCO OSNO | 0
7002457 | OP Near Hit Redding Tap L-402 | #REF! | Near Hit | #REF! | 3 | TA | AC: Typical Operations |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-06-30 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE |  | true | REVW | ATCO OSNO | 0
7002458 | OP Near Hit Ryer Island - Los Medanos St | #REF! | Near Hit | #REF! | 1 | TA | EC: Design Issue - Other |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-06-21 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | COMPPROC |  | unknown | REVW | ATCO OSNO | 0
7002458 | OP Near Hit Ryer Island - Los Medanos St | #REF! | Near Hit | #REF! | 2 | TA | AC: Typical Operations |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-06-21 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | COMPPROC |  | unknown | REVW | ATCO OSNO | 0
7002461 | OP Near Hit Felton Reg Station D/S Press | #REF! | Near Hit | #REF! | 1 | TA | AC: Within SCADA Accuracy |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 | AMFQ | 2014-03-18 | Medium 3-B | GESS | 2014-04-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SA | true | ACCP | OSNO OSTS | 0
7002461 | OP Near Hit Felton Reg Station D/S Press | #REF! | Near Hit | #REF! | 2 | CA | CA: Reg Set Point Lowered to 46 psig |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 |  | 2014-04-01 | Medium 3-B | GESS | 2014-04-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SA | true | ACCP | OSNO OSTS | 0
7002464 | OP Near Hit Almaden & Redmond | #REF! | Near Hit | #REF! | 1 | TA | AC: Within SCADA Accuracy |  |  |  | TSCO | 2014-03-18 | 2014-03-18 | AMFQ | 2014-03-18 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002464 | OP Near Hit Almaden & Redmond San Jose | #REF! | Near Hit | #REF! | 2 | TA | Contacted T&R Sup and Planner | Contacted the local T&R Supervisor on 03/12/2014 to determine Almaden & Redmond reg and monitor set point. The reg was set at 51 psig and monitor was set at 56 psig.. After contacting the T&R Supervisor, an e-mail was sent out to the local planner for further discussion on CA's. | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 |  | 2014-04-03 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002464 | OP Near Hit Almaden & Redmond San Jose | #REF! | Near Hit | #REF! | 3 | CA | CA: Maintenance Required | Maintenance to establish 0-100% calibration | OXG3 |  | TSCO | 2014-03-24 | 2014-03-24 |  | 2014-04-21 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out E-mails has been sent out several time regarding this Corrective Action. It has been escalated to Manger. Frank will be contacting Kelly Ball regarding this overdue CA.
7002465 | OP Near Hit Clarksburg Prim | #REF! | Near Hit | #REF! | 1 | TA | AC: Operating Close to MOP/HIHI |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 | AMFQ | 2014-03-18 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SA | true | ACCP | OSNO OSTS | 0
7002465 | OP Near Hit Clarksburg Prim | #REF! | Near Hit | #REF! | 2 | TA | Contacted T&R Sup |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 |  | 2014-04-01 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SA | true | ACCP | OSNO OSTS | 0
7002466 | OP Near Hit Brentwood Terminal | #REF! | Near Hit | #REF! | 1 | TA | AC: Hand Throttle Valve |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 | AMFQ | 2014-03-18 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | LM | true | ACCP | OSNO OSTS | 0
7002466 | OP Near Hit Brentwood Terminal | #REF! | Near Hit | #REF! | 2 | CA | CA: Checked Valve Positions & Close V-42 |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 |  | 2014-04-01 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | LM | true | ACCP | OSNO OSTS | 0
7002795 | Alarm inadvertently generated in GDCC | not present | Other | not present | 2 | TA | Complete Separation of Dev and Prod | Complete separation of Development and Production to the extend feasible with existing system | RPM4 |  | TSCO | 2014-04-11 | 2014-08-01 | RPM4 | 2014-07-29 | Low 4-C | GESSO | 2014-08-01 | GAWTOPER | WOSC | RPM4 | PRTR | OTHER | MI | unknown | ACCP | OSNO OSTS
7002795 | Alarm inadvertently generated in GDCC | not present | Other | N/A | 1 | TA | Training Issues with SCADA | Ensure training modules do not affect SCADA information or screens | RPM4 | GESSO | TSCO | 2014-04-11 | 2014-06-29 | RPM4 | 2014-06-01 | Low 4-C | GESSO | 2014-08-01 | GAWTOPER | WOSC | RPM4 | PRTR | OTHER | MI | unknown | ACCP | OSNO OSTS | 1 | LNR3 |  | JO15 | 2014-08-12 | GASCAPCPIC | LNR3 | 2014-08-20
7002930 | SCADA Emerg Resp Valve Info Issues | not present | Other | N/A | 1 | CA | Upgrade SCADA Screens |  | MWH7 |  | TSCO | 2014-04-08 | 2014-08-01 | RPM4 | 2014-07-29 | Medium 3-B | GESS | 2014-08-01 | GAWTOPER | WOSC | RPM4 | PRER | TRANSPIPE |  | unknown | ACCP | OSNO OSTS | 0 |  | Work reassigned to Carlos Penner. Task 1 work performed by Mike Henscey considered completed.
7002936 | OP Near Hit Congo & Flood SF | Congo & Flood | Near Hit | 2014-04-08 23:52 | 2 | CA | CA: Check SF Load Center Set Points | San Francisco Gas OM&C Supervisor has requested the Milpitas District that maintain SF Load Center to come up and check the station. | JGJ4 |  | TSCO | 2014-04-23 | 2014-08-25 |  |  | Medium 3-B | GESS | 2014-08-25 | GAWTOPER | WOOP | DKM4 |  | DISTSERVS | [6 empty] | 6/19/14 - Email reminder sent out to responsible party - awaiting response. 6/26/2014 - Upon review, all CA's have been completed and is ready for trending
7003089 | OP Near Hit French Camp, Stockton | #REF! | Near Hit | #REF! | 3 | CA | CA: Immediate Response | Immediate actions were done during the HIHI breach which included: GTCC contacted the Field Supervisor regarding the HI alarm and asked to have Vernalis Regulations to be checked, Supervisor contacted the Tech, and Tech checked the regulations at Vernalis | KDSD | GESS | TSCO | 2014-04-17 | 2014-04-17 | KDSD | 2014-04-17 | Medium 3-B | GESS | 2014-12-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | ST | true | ACCP | OSNO OSTS
7003181 | OP Near Hit Skyline & Rischell, EB | #REF! | Near Hit | #REF! | 2 | CA | CA: Immediate Actions Followed | Immediate actions were done during the HIHI breach. At this point, no further actions are required. |  |  | TSCO | 2014-05-06 | 2014-12-01 | AMFQ | 2014-12-01 | Medium 3-B | GESS | 2014-12-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | PN | true | ACCP | OSNO OSTS
7003420 | Inefficient new Dist SCADA system | not present | Other | not present | 1 | TA | Response to D SCADA Cost Effectiveness | Response on CAP Item 7003420 - Questions about D SCADA Cost Effectiveness The Gas Distribution Control Center (GDCC) Project is intended to provide significant benefits to PG&E and its customers by improving Company operations, reliability, and emergency response. The deployment of Supervisory Control and Data Acquisition (SCADA) and control center processes provides improved visibility into the status and state of the system and allows quicker and more informed decision making when events occur on the system. PG&E's gas distribution SCADA system is focused on monitoring key pipeline pressures (e.g. low pressure points) and monitoring and control applications at gas pressure regulator stations.... | AMFQ |  | TSCO | 2014-08-25 | 2014-09-06 | AMFQ | 2014-08-25 | Low 4-C | GESSO | 2014-09-06 | GAWTOPER | WOGC | FWM1 | PRGS | MEASCRTL | NB |  | ACCP |  |  |  | On Friday Aug 22nd, Frank sent the response for this CAP to Me (Alvin Flores). A CAP task was created and the response has been uploaded into CAP.
7003538 | OP Near Hit Redding Tap L-402 | #REF! | Near Hit | #REF! | 3 | CA | CA: Immediate Actions Followed | Immediate actions were taken during the incident that included the following: GTCC conacted the on call supervisor, a tech was sent out to the location, and the tech reducded the pressure set point to 585 psig | AMFQ | GESS | TSCO | 5/27/214 | 2014-05-27 | AMFQ |  | Medium 3-B | GESS | 2015-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | NV | [5 empty] | 5/27/2014 - the CA was closed out
7003638 | BR Bldg Y IGCC SCADA Workstation Failure | not present | Other | N/A | 1 | CA | Manually Update all 4 workstations (TIG | 1) Manually Update all 4 workstations (TIGCC1,TIGCC2,DIGCC1,DIGCC2) | JUHM |  | TSCO | 2014-05-19 | 2014-05-19 | JUHM | 5/19/014 | Low 4-C | GESSO | 2014-07-01 | GAWTOPER | WOSC | RPM4 |  | OTHER |  | unknown | ACCP | OSNO OSTS | 0
7003730 | OP Near Hit Sacramento GLC | #REF! | Near Hit | #REF! | 3 | CA | CA: Immediate Response | Immediate Response: Local Supervisor sent out a Tech to the location first thing in the morning and the Tech completed a Sulfagon Filters installation at Sac GLC. | KDSD | GESS | TSCO | 5/14/014 | 2014-05-14 | KDSD |  | Medium 3-B | GESS | 2014-05-19 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | SA | [5 empty] | 5/14/2014 - it was closed out
7004203 | ERX Testing | not present | Other | not present | - | - | ERX Testing | ERX testing alarms coming out of SCADA lad at Bishop Ranch are going into live SCADA system. There needs to be a sand box for thes alarms coming out of the test lab during the testing phase of new equipment. Please assign to Bob Matthews | [5 empty] | RPM4 | 2014-08-01 | Low 4-B | GESSO | 2014-07-19 |  |  | RPM4 | PRIT | OTHER
7004755 | OP Near Hit Irvington Station | #REF! | Near Hit | #REF! | 2 | TA | AC: Valve Operation |  | KDSD | GESS | TSCO | 2014-07-29 | 2014-07-29 | LNR3 | 2014-07-29 | Medium 4-A | GESS | 2015-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | MI | true | SUBM | OSNO OSTS
7004755 | OP Near Hit Irvington Station | #REF! | Near Hit | #REF! | 1 | TA | EC: HF/WPE-Manual Operations |  | KDSD | GESS | TSCO | 2014-07-29 | 2014-07-29 | LNR3 | 2014-07-29 | Medium 4-A | GESS | 2015-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | MI | true | SUBM | OSNO OSTS
| Today | 2024-03-07 |  | not present
7005868 | OP Near Hit at Enrico Station, L-105 | #REF! | Near Hit | #REF! | 2 | CA | CA: Remove TROP on L105N | L105N has an MOP/MAOP of 150/198 psig respectively. It is currently being held down by a crop to have an MOP of 121psig. By the comments on the latest version of 086868 it describes the TROP as being caused by unscheduled crane movement along L105A. "A TROP was issued due to unscheduled crane movement along L105A on Hollis St between Powell St and 59th. Engineering requested a 10% reduction until further review can be made." This does not seem to actually affect pipe specifications (just increased wheel loading forces on the surface). Removing this TROP will return the MOP back to 150 psig. | TWS4 |  | TSCO | 2014-09-22 | 2015-02-01 | KDSD | 2014-10-17 | Medium 4-A | GESS | 2015-09-16 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | EB | unknown | ACCP | OSNO OSTS | 0
Some CAP notes:
2014-07-16

## Checklist (hidden)
Count | Engineer | Event Location/Title | Notification to Dan | OP/Near Hit | 48-hour report complete | Update Master | CAP Number | Quick Hit | Weekly CAP Meeting | Apparent/Root Cause | OP Elimination meeting | CA enter to CAP | Final Report/Root Cause/CA communication | 5 MM | CA Complete
1 | K1D7 | Corning | 2014-01-07 | OP | 2014-01-07 | 2014-01-07 | 7001252 | [5 empty] | k1d7 | Liquids
2 | K1D7 AMFQ | Topock | 2014-01-10 | OP | 2014-01-14 | 2014-01-14 | 7001315 7003563 | [5 empty] | CAP |  | CAP 7003563
3 | K1D7 | Corning | 2014-01-13 | OP | 2014-01-13 | 2014-01-13 | 7001312 | [5 empty] | k1d7 | Liquids
4 | P5B7 | 9th and I | 2014-01-15 | OP | 2014-01-16 | 2014-01-16 | 7001340 | [5 empty] | kdsd
5 | MND4 | Center St | 2014-02-02 | OP | 2014-02-04 | 2014-02-04 | 7001532 | [5 empty] | kdsd
6 | KDSD | Lomita Park | 2014-02-24 | OP | 2014-02-24 | 2014-02-24 | 7001977 | [5 empty] | kdsd |  | 7001977
7 | AMFQ | Avalon & Vienna | 2014-05-08 | OP | 2014-05-20 | 2014-05-16 | 7003511 | [7 empty] | CAP 7004145 CAP 7004164
8 | AMFQ | L172 North at Hershey Station | 2014-06-23 | OP |  | 2014-06-25 | 7004358
9 | KDSD | Herrmann Station | 2014-06-30 | OP | 2014-07-01 | 2014-06-30 | 7004583 | [5 empty] | kdsd |  | 7004583
10 | AMFQ | American Rice Dryer | 2014-06-16 | OP | 2014-07-03 | 2014-07-03 | 7004510
11 | AMFQ | L134A Herdon Junction | 2014-07-18 | NH | 2014-07-21 | 2014-07-21 | 7004896
12 | AMFQ | Monolith Cement | 2014-07-18 | NH | 2014-07-21 | 2014-07-21 | 7004934
13 | KDSD | Los Medanos | 2014-07-21 | OP | 2014-07-22 | 2014-07-22 | 7004884 | [7 empty] | 7004884
| KDSD | Alameda SHP | 2014-07-30 | OP | 2014-07-30 | 2014-07-30 | 7005059
14 | KDSD | Dolan Rd | 2014-08-04 | OP | 2014-08-05 | 2014-08-04 | 7005140 | [7 empty] | 7005431
15 | AMFQ | Acacia Station | 2014-08-16 | OP | 2014-08-16 | 2014-08-16 | 7005431 | 2014-08-27 |  | 8/26/14 CAP
16 | AMFQ | Enrico | 2014-09-13 | NH | 2014-09-25 | 2014-09-23 | 7005868 |  | 2014-09-18 | 09/22/14 CAP
17 | AMFQ | Cemex | 2014-09-11 | NH |  | 2014-09-13 | 70006071
18 | AMFQ | Swingle Station | 2014-08-12 | NH | 2014-08-11 | 2014-08-14 | 7005258 | [6 empty] | Mention Hand Throttle Valve in the next theme 5MM. This event will be noted and CA will be closed out
19
20
21 | [15 empty] | Formal Communication Checklist
22 | [15 empty] | 1 | 48-hour report
23 | [15 empty] | 2 | Final 48-hour Report (with Root Cause and CAs)
[16 empty] | 3 | EOM meetings with Dan to deliver closed out Notifications, and the CAs related to the notifications
|  | no action needed | [13 empty] | Steps to follow with the checklist in mind
incomplete
|  | pending | [14 empty] | Engineer writes the report and notifies Dan for next 7 am meeting
|  | complete | [14 empty] | 48 hour report is completed
Update the 2011-2014 master excursion spreadsheet
Establish the report has a CAP number, add this to the report
At the Thursday meetings with CAP team to discuss
If not resolved establish root cause
and corrective actions for the event
These two should be sepecified into the CAP tool and 48-hour report
This should finalize the 48-hour report, and mass communication can be delivered
The OP event will be discussed at the next OP Elimination meeting
Track CA to completion
Note on J1: Flores, Alvin: Clarification: CAP Meeting means Thursday Meeting?

## Pivots (hidden)
# of OP events by Division
Year | (Multiple Items)
Gas Log Event | (All)
Count of Percent over MOP | Month
Division | 1 | 2 | 3 | 4 | 5 | 6 | 8 | 9 | 10 | 11 | Grand Total
Central Coast | [7 empty] | 1 |  |  | 1 |  |  |  | Central Coast
Diablo | [9 empty] | 1 | 1 |  |  |  | Diablo
East Bay |  |  | 1 | [7 empty] | 1 |  |  |  | East Bay
Fresno | 1 |  |  |  |  | 1 |  |  |  | 2 | 4 |  |  |  | Fresno
Kern | 1 |  |  | 1 | [6 empty] | 2 |  |  |  | Kern
Mission |  | 1 | [8 empty] | 1 |  |  |  | Mission
North Bay | [5 empty] | 2 |  |  | 1 |  | 3 |  |  |  | North Bay
North Coast |  |  |  | 1 | [6 empty] | 1 |  |  |  | North Coast
North Valley | 2 | [5 empty] | 2 |  |  |  | 4 |  |  |  | North Valley
Peninsula |  | 1 | [8 empty] | 1 |  |  |  | Peninsula
Sacramento | 3 |  | 1 | 1 |  | 1 | 1 |  |  |  | 7 |  |  |  | Sacramento
San Francisco |  |  |  |  | 2 | [5 empty] | 2 |  |  |  | San Francisco
San Jose | [7 empty] | 1 |  |  | 1 |  |  |  | San Jose
Sierra |  |  |  |  | 1 | 1 | 1 |  |  |  | 3 |  |  |  | Sierra
Stockton | 1 | 2 | [8 empty] | 3 |  |  |  | Stockton
Yosemite |  | 1 |  | 1 | [6 empty] | 2 |  |  |  | Yosemite
(blank) | [14 empty] | Year
Hollister | 1 | [9 empty] | 1 |  |  |  | Gas Log Event
Year | (Multiple Items) | [13 empty] | 0
Gas Log Event | (Multiple Items) | [13 empty] | Count of Percent over MOP
Specific OP Metric Group
Count of Percent over MOP | Group | [13 empty] | Design
Specific OP Metric Group | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total | [10 empty] | Equipment Failure
Design |  | 1 |  | 1 | [10 empty] | Operator Error
Equipment Failure | 5 | 2 | 3 | 10
Operator Error | 8 | 7 | 7 | 22
SP too close to MOP | 2 | 1 |  | 3
Grand Total | 15 | 11 | 10 | 36
Gas Log Event
Year | (Multiple Items)
Gas Log Event | (Multiple Items)
Count of Percent over MOP | Trans/Dist
Specific OP Metric Group | HP Distribution | LP Distribution | Transmission | Grand Total
Design |  |  | 1 | 1
Equipment Failure | 6 |  | 4 | 10
Operator Error | 3 | 3 | 16 | 22
SP too close to MOP | 1 | 1 | 1 | 3
Grand Total | 10 | 4 | 22 | 36
# of OP Events by System
Year | (Multiple Items)
Count of Percent over MOP | Study Group
Trans/Dist |  | Trans P > MOP+10 | HP Distribution > MOP+10% | LP > 16 | Grand Total
HP Distribution | 5 |  | 6 |  | 11
LP Distribution | 3 |  |  | 1 | 4
Transmission | 16 | 6 |  |  | 22
Grand Total | 24 | 6 | 6 | 1 | 37
# of OP Events by System
Year | (Multiple Items)
Count of Percent over MOP | Study Group
Trans/Dist |  | Trans P > MOP+10 | HP Distribution > MOP+10% | LP > 16 | Grand Total
HP Distribution | 5 |  | 6 |  | 11
LP Distribution | 3 |  |  | 1 | 4
Transmission | 16 | 6 |  |  | 22
Grand Total | 24 | 6 | 6 | 1 | 37
# of OP Events by System | [12 empty] | # of OP Events by System by Quarter | [30 empty] | # of OP Events by System by Month
Year | (Multiple Items)
Count of Percent over MOP | Study Group | [11 empty] | Count of Percent over MOP | Year | Quarter | [28 empty] | Count of Percent over MOP | Year | Month
Trans/Dist |  | Trans P > MOP+10 | HP Distribution > MOP+10% | LP > 16 | Grand Total | [8 empty] | 2011 |  |  |  | 2011 Total | 2012 |  |  |  | 2012 Total | 2013 |  |  |  | 2013 Total | 2014 |  | 2014 Total | [13 empty] | 2011 | [11 empty] | 2011 Total | 2012 | [11 empty] | 2012 Total | 2013 | [9 empty] | 2013 Total | 2014 |  |  |  | 2014 Total
HP Distribution | 5 |  | 6 |  | 11 | [7 empty] | Trans/Dist | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | [13 empty] | Trans/Dist | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 8 | 9 | 10 | 11 |  | 1 | 2 | 5 | 6
LP Distribution | 3 |  |  | 1 | 4 | [7 empty] | HP Distribution | 5 | 12 | 11 | 10 | 38 | 4 |  | 1 | 2 | 7 | 5 | 3 | 1 |  | 9 | 2 |  | 2 | [12 empty] | HP Distribution |  | 3 | 2 | 1 | 7 | 4 | 3 | 2 | 6 | 1 | 5 | 4 | 38 | 3 | 1 | [6 empty] | 1 |  |  | 2 | 7 | 4 | 1 |  | 2 | 1 |  | 1 |  |  |  | 9 | 2 |  |  | 1 | 3
Transmission | 16 | 6 |  |  | 22 | [7 empty] | LP Distribution | 173 | 148 | 164 | 139 | 624 | 179 | 46 |  | 3 | 228 |  | 1 | 1 | 1 | 3 | 1 |  | 1 | [12 empty] | LP Distribution | 53 | 45 | 75 | 37 | 56 | 55 | 67 | 43 | 54 | 70 | 28 | 41 | 624 | 53 | 60 | 66 | 37 | 9 | [6 empty] | 3 | 228 |  |  |  |  | 1 |  |  | 1 |  | 1 | 3 | 1 |  |  |  | 1
Grand Total | 24 | 6 | 6 | 1 | 37 | [7 empty] | Transmission | 41 | 35 | 22 | 14 | 112 | 45 | 16 | 5 | 7 | 73 | 8 | 4 | 4 | 3 | 19 | 3 | 2 | 5 | [12 empty] | Transmission | 13 | 17 | 11 | 13 | 10 | 12 | 13 | 7 | 2 | 4 | 2 | 8 | 112 | 12 | 7 | 26 | 10 | 4 | 2 | 2 | 2 | 1 | 5 | 1 | 1 | 73 | 4 | 2 | 2 | 2 |  | 2 | 3 | 1 | 1 | 2 | 19 | 1 | 2 |  | 2 | 5
[13 empty] | LP Distribution | [16 empty] | 1 | 1 | [12 empty] | LP Distribution | [39 empty] | 1 |  | 1
[13 empty] | Grand Total | 219 | 195 | 197 | 163 | 774 | 228 | 62 | 6 | 12 | 308 | 13 | 8 | 6 | 4 | 31 | 6 | 3 | 9 | [12 empty] | Grand Total | 66 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 | 774 | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 | 308 | 8 | 3 | 2 | 4 | 2 | 2 | 4 | 2 | 1 | 3 | 31 | 4 | 2 | 1 | 3 | 10
Small/Large Excursions OP Events | [12 empty] | Large Excursions OP Events by Quarter | [14 empty] | Small Excursions OP Events by Quarter | [15 empty] | Large Excursions OP Events by Quarter
Year | 2014 | [42 empty] | Large Excursion/Small Excursion | 2011 1: Small Excursion
Count of Percent over MOP |  | Month | [10 empty] | Count of # over MOP |  | Year | Quarter | [11 empty] | Count of # over MOP |  | Year | Quarter | [12 empty] | Count of # over MOP | 2011 2: Month
Large Excursion/Small Excursion | Trans/Dist | 1 | 2 | Grand Total | [10 empty] | 2011 |  |  |  | 2012 |  |  |  | 2013 |  |  |  | 2014 |  |  | 2011 |  |  |  | 2011 Total | 2012 |  |  |  | 2012 Total | 2013 |  |  |  | Year | Trans/Dist | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Grand Total
Large Excursion | HP Distribution | 2 |  | 2 | [8 empty] | Large Excursion/Small Excursion | Trans/Dist | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Large Excursion/Small Excursion | Trans/Dist | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 | 2011 | HP Distribution |  | 2 | 2 | 1 | 3 | 3 | 3 | 2 | 6 |  | 5 | 3 | 30
| Transmission | 1 |  | 1 | [8 empty] | Large Excursion | HP Distribution | 1 | 5 |  | 2 | 2 |  | 1 | 1 | 2 | 1 | 1 |  | 2 | Small Excursion | HP Distribution | 4 | 7 | 11 | 8 | 30 | 2 |  |  | 1 | 3 | 3 | 2 |  |  |  | LP Distribution | 53 | 45 | 74 | 37 | 55 | 55 | 67 | 43 | 54 | 69 | 28 | 41 | 621
Small Excursion | LP Distribution | 1 |  | 1 | [9 empty] | LP Distribution | [14 empty] | LP Distribution | 172 | 147 | 164 | 138 | 621 | 179 | 46 |  | 3 | 228 |  | 1 |  | 1 |  | Transmission | 7 | 13 | 9 | 11 | 9 | 9 | 11 | 6 | 2 | 2 | 1 | 7 | 87 | bar: Q1 to Q1
| Transmission |  | 2 | 2 | [9 empty] | Transmission | 12 | 6 | 3 | 4 | 1 | 2 |  | 1 | 3 |  | 1 | 1 | 1 |  | Transmission | 29 | 29 | 19 | 10 | 87 | 44 | 14 | 5 | 6 | 69 | 5 | 4 | 3 | 2 | 2011 Total |  | 60 | 60 | 85 | 49 | 67 | 67 | 81 | 51 | 62 | 71 | 34 | 51 | 738
Grand Total |  | 4 | 2 | 6 | [8 empty] | Small Excursion | HP Distribution | 4 | 7 | 11 | 8 | 2 |  |  | 1 | 3 | 2 |  |  |  |  | LP Distribution | [14 empty] | 2012 | HP Distribution | 1 | 1 | [9 empty] | 1 | 3
[14 empty] | LP Distribution | 172 | 147 | 164 | 138 | 179 | 46 |  | 3 |  | 1 |  | 1 | 1 | Grand Total |  | 205 | 183 | 194 | 156 | 738 | 225 | 60 | 5 | 10 | 300 | 8 | 7 | 3 | 3 |  | LP Distribution | 53 | 60 | 66 | 37 | 9 | [6 empty] | 3 | 228
[14 empty] | Transmission | 29 | 29 | 19 | 10 | 44 | 14 | 5 | 6 | 5 | 4 | 3 | 2 | 2 | [17 empty] | Transmission | 12 | 7 | 25 | 10 | 2 | 2 | 2 | 2 | 1 | 5 | 1 |  | 69
[14 empty] | LP Distribution | [29 empty] | 2012 Total |  | 66 | 68 | 91 | 47 | 11 | 2 | 2 | 2 | 1 | 5 | 1 | 4 | 300
[13 empty] | Grand Total |  | 219 | 195 | 197 | 163 | 228 | 62 | 6 | 12 | 13 | 8 | 6 | 4 | 6 | [16 empty] | 2013 | HP Distribution | 2 | 1 |  | 1 | 1 | [7 empty] | 5
OP Events by Apparent Cause | [44 empty] | LP Distribution |  |  |  |  | 1 | [5 empty] | 1 |  | 2
Year | 2014 | [43 empty] | Transmission | 3 | 1 | 1 | 2 |  | 2 |  | 2 | 1 | 1 | 1 |  | 14
[44 empty] | 2013 Total |  | 5 | 2 | 1 | 3 | 2 | 2 |  | 2 | 1 | 1 | 2 |  | 21
Count of Percent over MOP | Month | [11 empty] | Count of Percent over MOP | Year | Q1: Quarter | [16 empty] | 2014 | HP Distribution | [5 empty] | 1 | [6 empty] | 1
Specific OP Metric Group | 1 | 2 | Grand Total | [10 empty] | 2011 | Q4: 2011 Total; Q1: 2012; Q1: 2012 Total; Q2: 2013 | 2013 Total | 2014 |  |  | 2014 Total | Grand Total | [11 empty] | LP Distribution | 1 | [11 empty] | 1
Design | 1 |  | 1 | [9 empty] | Specific OP Metric Group | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | (blank) | [13 empty] | Transmission |  | 2 |  |  |  | 2 | [6 empty] | 4
Equipment Failure | 2 | 2 | 4 | [9 empty] | Design | 13 | 4 | 6 | 4 | 27 | 1 |  |  | 2 | 3 |  |  |  | 1 | 1 |  |  |  |  | 31 | [11 empty] | LP Distribution |  |  |  |  | 1 | [7 empty] | 1
Operator Error | 1 |  | 1 | [9 empty] | Equipment Failure | 12 | 14 | 7 | 2 | 35 | 13 | 2 | 3 | 8 | 26 | 3 | 4 | 2 |  | 9 | 2 |  |  | 2 | 72 | [10 empty] | 2014 Total |  | 1 | 2 |  |  | 1 | 3 | [6 empty] | 7
Grand Total | 4 | 2 | 6 | [9 empty] | Operator Error | 14 | 21 | 10 | 7 | 52 | 12 | 13 | 2 | 2 | 29 | 8 | 4 | 4 | 3 | 19 | 3 | 3 |  | 6 | 106 | [10 empty] | Grand Total |  | 132 | 132 | 177 | 99 | 81 | 74 | 83 | 55 | 64 | 77 | 37 | 55 | 1066
[13 empty] | SP too close to MOP |  | 1 |  | 5 | 6 | 26 | 6 | 1 |  | 33 | 2 |  |  |  | 2 | 1 |  | 1 | 2 | 43
[13 empty] | Unknown/ Not Reported | 180 | Q1: 155; Q2: 174; Q3: 145; Q4: 654; Q1: 176; Q2: 41; Q1: 217 | [5 empty] | 871
[13 empty] | Grand Total | 219 | 195 | 197 | 163 | 774 | 228 | 62 | 6 | 12 | 308 | 13 | 8 | 6 | 4 | 31 | 6 | 3 | 1 | 10 | 1123
OP Events by Apparent Cause by large/small excursion
Year | 2014
Count of Percent over MOP | Large Excursion/Small Excursion | [11 empty] | Count of Percent over MOP |  | Q1: Year; Q2: Quarter
Specific OP Metric Group | Large Excursion | Small Excursion | Grand Total | [11 empty] | Q1: 2014; Q2: 2014 Total; Q3: Grand Total
Design |  | 1 | 1 | [9 empty] | Large Excursion/Small Excursion | Specific OP Metric Group | Q1: (blank)
Equipment Failure | 2 | 2 | 4 | [9 empty] | Small Excursion | SP too close to MOP | bar: Q1 to Q3
Operator Error | 1 |  | 1 | [9 empty] | Grand Total | bar: Q1 to Q3
Grand Total | 3 | 3 | 6
# of OP Events by At Storage or Compr Station | [12 empty] | # of OP Events by At Storage or Compr Station
Count of Percent over MOP |  | Month | [10 empty] | Count of Percent over MOP | Year | Q1: quarter
Year | At Compr Stn or Storage | 1 | [11 empty] | 2011 | Q1: 2011 Total; Q2: 2012; Q3: 2012 Total; Q4: 2014; Q1: 2014 Total
2014 | yes | 1 | [10 empty] | At Compr Stn or Storage | Q1 | bar: Q2; Q4
2014 Total |  | 1 | [10 empty] | yes | 11 | Q1: 11; Q2: 1; Q3: 1; Q4: 1; Q1: 1
Grand Total |  | 1 | [10 empty] | Grand Total | 11 | Q1: 11; Q2: 1; Q3: 1; Q4: 1; Q1: 1
Small/Large Excursions OP Events
Count of Percent over MOP |  | Year | Month
|  | 2011 | [11 empty] | 2011 Total | Q1: 2012; Q1: 2012 Total | 2013 | [9 empty] | 2013 Total | 2014 |  | 2014 Total | (blank) | Grand Total
Large Excursion/Small Excursion | Trans/Dist | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 8 | 9 | 10 | 11 |  | 1 | 2
Large Excursion | HP Distribution | 2011 2: 1; 2011 5: 4; 2011 6: 1; 2011 10: 1; 2011 12: 1 | 8 | 2 | [7 empty] | 1 |  |  | 1 | 4 | 2 |  |  | 1 |  |  | 1 |  |  |  | 4 | 2 |  | 2 |  | 18
| LP Distribution | [12 empty] | 3 | [20 empty] | 1 |  |  | 1 |  |  |  |  | 4 | bar: 2011 3; 2011 5; 2011 10
| Transmission | 6 | 4 | 2 | 2 | 1 | 3 | 2 | 1 |  | 2 | 1 | 1 | 25 |  |  | 1 |  | 2 | [6 empty] | 1 | 4 | 1 | 1 | 1 |  |  |  | 1 |  |  | 1 | 5 | 1 |  | 1 |  | 35
Small Excursion | HP Distribution |  | 2 | 2 | 1 | 3 | 3 | 3 | 2 | 6 |  | 5 | 3 | 30 | 1 | 1 | [9 empty] | 1 | 3 | 2 | 1 |  | 1 | 1 | [5 empty] | 5 |  |  |  |  | 38
| LP Distribution | 53 | 45 | 74 | 37 | 55 | 55 | 67 | 43 | 54 | 69 | 28 | 41 | 621 | 53 | 60 | 66 | 37 | 9 | [6 empty] | 3 | 228 |  |  |  |  | 1 |  |  |  |  | 1 | 2 | 1 |  | 1 |  | 852
| Transmission | 7 | 13 | 9 | 11 | 9 | 9 | 11 | 6 | 2 | 2 | 1 | 7 | 87 | 12 | 7 | 25 | 10 | 2 | 2 | 2 | 2 | 1 | 5 | 1 |  | 69 | 3 | 1 | 1 | 2 |  | 2 | 2 | 1 | 1 | 1 | 14 |  | 2 | 2 |  | 172
(blank) | (blank)
Grand Total |  | 66 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 | 774 | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 | 308 | 8 | 3 | 2 | 4 | 2 | 2 | 4 | 2 | 1 | 3 | 31 | 4 | 2 | 6 |  | 1119

## Charts (hidden)
2015 | [15 empty] | fill key:
|  | UPDATE THE TABLES BELOW | [14 empty] | autofill
2015 OP Events for entire year | [16 empty] | manual
Reason | Large Excursions | Small Excursions | Grand Total | Key
Design
Equipment Failure |  |  | 6
Operator Error |  |  | 8
SP too close to MOP |  |  | 3
Unknown/ Not Reported
Grand Total
| 2015 Large Excursion OP Events - 0 Events | 2015 Small Excursion OP Events - 0 Events | 2015 Total OP - 17 Events
Operator Error - HP/WPE (Field, Manual Operations, Eng Review)
[7 empty] | 2015 Total OP - 17 Events |  |  |  |  | 2015 Large Excursion OP Events - 0 Events
2015 OP Events for quarter - First Quarter
Reason | Large Excursions | Small Excursions | Grand Total | Key
Design |  |  | 0
Equipment Failure |  |  | 0
Operator Error |  |  | 0
SP too close to MOP |  |  | 0
Unknown/ Not Reported |  |  | 0
Grand Total | 0 | 0 | 0
2014 Total OP Events - 17 Events
| 2015 Large Excursion OP Events - 0 Events | 2015 Small Excursion OP Events - 0 Events | 2015 Total OP - 0 Events as of 3/31/14
2015 OP Events for quarter - Second Quarter
Reason | Large Excursions | Small Excursions | Grand Total | Key
Design |  |  | 0
Equipment Failure |  |  | 0
Operator Error |  |  | 0
SP too close to MOP |  |  | 0
Unknown/ Not Reported |  |  | 0
Grand Total | 0 | 0 | 0 |  |  | 2015 Total OP- 0 Events as of 7/1/14 | [6 empty] | 2014 Total OP Events - 17 Events
| 2015 Large Excursion OP Events - 0 Events | 2015 Small Excursion OP Events - 0 Events | 2015 Total OP- 0 Events as of 7/1/14 | [8 empty] | 0
2015 OP Events for quarter - Third Quarter
Reason | Large Excursions | Small Excursions | Grand Total | Key
Design |  |  | 0
Equipment Failure |  |  | 0
Operator Error |  |  | 0
SP too close to MOP |  |  | 0
Unknown/ Not Reported |  |  | 0
Grand Total | 0 | 0 | 0
| 2015 Large Excursion OP Events - 0 Events | 2015 Small Excursion OP Events - 0 Events | 2013 Total OP- 0 Events as of 9/30/14
2015 OP Events for quarter - Fourth Quarter
Reason | Large Excursions | Small Excursions | Grand Total | Key
Design |  |  | 0
Equipment Failure |  |  | 0
Operator Error |  |  | 0
SP too close to MOP |  |  | 0
Unknown/ Not Reported |  |  | 0
Grand Total | 0 | 0 | 0
| 2015 Large Excursion OP Events - 0 Events | 2015 Small Excursion OP Events - 0 Events | 2015 Total OP- 0 Events as of 9/30/14
2011/2012 OP Events on LP Distribution
Trans/Dist | LP Distribution
Count of Percent over MOP | Year
Month | 2011 | 2012
Jan | 53 | 53
Feb | 45 | 60
Mar | 75 | 66
Apr | 37 | 37
May | 56 | 9
Jun | 55 | 0
Jul | 67 | 0
Aug | 43 | 0
Sep | 54 | 0
Oct | 70 | 0
Nov | 28 | 0
Dec | 41 | 3
Grand Total | 624 | 228
2012 OP Events - Gas Log
Reason | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total
Design | 0 | 0 | 3 | 3
Equipment Failure | 7 | 6 | 7 | 20
Operator Error | 12 | 9 | 3 | 24
SP too close to MOP | 7 | 0 | 0 | 7
Unknown/ Not Reported | 9 | 2 | 2 | 13
Grand Total | 35 | 17 | 15 | 67
| 35 2012 OP Events | 17 2012 OP Events | 15 2012 OP Events | 67 2012 Total OP Events
[7 empty] | 35 2012 OP Events | [6 empty] | 17 2012 OP Events | 15 2012 OP Events
67 2012 Total OP Events
[7 empty] | 67 2012 Total OP Events | [5 empty] | MOP Excursions greater than 10%
15 2012 OP Events
2013 OP Events (not updated)
Reason | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total
Design | 0 | 0 | 0 | 0
Equipment Failure | 5 | 1 | 1 | 7
Operator Error | 3 | 2 | 4 | 9
SP too close to MOP | 1 | 0 | 0 | 1
Unknown/ Not Reported | 0 | 0 | 0 | 0
Grand Total | 9 | 3 | 5 | 17
| 9 2013 OP Events | 3 2013 OP Events | 5 2013 OP Events | 17 2013 Total OP Events
[7 empty] | 9 2013 OP Events | [6 empty] | 3 2013 OP Events | 5 2013 OP Events
17 2013 Total OP Events
2012 OP Events for entire year
Reason | Large Excursions | Small Excursions | Grand Total
Design | 3 | 0 | 3
Equipment Failure | 3 | 23 | 26
Operator Error | 2 | 27 | 29
SP too close to MOP | 0 | 32 | 32
Unknown/ Not Reported | 0 | 218 | 218
Grand Total | 8 | 300 | 308
| 2012 Large Excursion OP Events - 8 Events | 2012 Small Excursion OP Events - 300 Events | 2012 Total OP - 308 Events
[7 empty] | 2012 Total OP - 308 Events | [5 empty] | 2012 Large Excursion OP Events - 8 Events
2013 OP Events for entire year
Reason | Large Excursions | Small Excursions | Grand Total
Design | 0 | 1 | 1
Equipment Failure | 4 | 11 | 15
Operator Error | 6 | 8 | 14
SP too close to MOP | 0 | 1 | 1
Unknown/ Not Reported | 0 | 0 | 0
Grand Total | 10 | 21 | 31
| 2013 Large Excursion OP Events - 10 Events | 2013 Small Excursion OP Events - 21 Events | 2013 Total OP - 31 Events
[7 empty] | 2013 Total OP - 31 Events | [5 empty] | 2013 Large Excursion OP Events - 10 Events
2013 OP Events for quarter - First Quarter
Reason | Large Excursions | Small Excursions | Grand Total
Design | 0 | 0 | 0
Equipment Failure | 0 | 5 | 5
Operator Error | 5 | 2 | 7
SP too close to MOP | 0 | 1 | 1
Unknown/ Not Reported | 0 | 0 | 0
Grand Total | 5 | 8 | 13
| 2013 Large Excursion OP Events - 5 Events | 2013 Small Excursion OP Events - 8 Events | 2013 Total OP- 13 Events as of 3/31/13
2013 OP Events for quarter - Second Quarter
Reason | Large Excursions | Small Excursions | Grand Total
Design | 0 | 0 | 0
Equipment Failure | 1 | 4 | 5
Operator Error | 0 | 3 | 3
SP too close to MOP | 0 | 0 | 0
Unknown/ Not Reported | 0 | 0 | 0
Grand Total | 1 | 7 | 8
| 2013 Large Excursion OP Events - 1 Events | 2013 Small Excursion OP Events - 7 Events | 2013 Total OP- 8 Events as of 7/2/13
2013 OP Events for quarter - Third Quarter
Reason | Large Excursions | Small Excursions | Grand Total |  |  |  | 2013 Total OP- 13 Events as of 3/31/13 | [5 empty] | 2013 Large Excursion OP Events - 5 Events
Design | 0 | 1 | 1
Equipment Failure | 1 | 1 | 2
Operator Error | 1 | 1 | 2
SP too close to MOP | 0 | 0 | 0
Unknown/ Not Reported | 0 | 0 | 0
Grand Total | 2 | 3 | 5
| 2013 Large Excursion OP Events - 2 Events | 2013 Small Excursion OP Events - 3 Events | 2013 Total OP- 5 Events as of 9/30/13
2013 OP Events for quarter - Fourth Quarter
Reason | Large Excursions | Small Excursions | Grand Total
Design | 0 | 0 | 0
Equipment Failure | 1 | 1 | 2
Operator Error | 0 | 2 | 2
SP too close to MOP | 0 | 0 | 0
Unknown/ Not Reported | 0 | 0 | 0
Grand Total | 1 | 3 | 4
| 2013 Large Excursion OP Events - 1 Events | 2013 Small Excursion OP Events - 3 Events | 2013 Total OP- 4 Events as of 9/30/13
2012 OP Events - LP Distribution
Reason | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total
Design | 0 | 0 | 0 | 0
Equipment Failure | 0 | 1 | 4 | 5
Operator Error | 0 | 1 | 5 | 6
SP too close to MOP | 4 | 0 | 0 | 4
Unknown/ Not Reported | 142 | 61 | 10 | 213
Grand Total | 146 | 63 | 19 | 228
| 146 2012 LP OP Events | 63 2012 LP OP Events | 19 2012 LP OP Events | 228 2012 Total LP OP Events
[7 empty] | 146 2012 LP OP Events | [6 empty] | 63 2012 LP OP Events | 19 2012 LP OP Events
228 2012 Total LP OP Events
Design |  |  | 2
Equipment Failure | 1 | 2 | 2
2012 OP Events - HP Distribution
Reason | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total
Design | 0 | 0 | 2 | 2
Equipment Failure | 1 | 2 | 2 | 5
Operator Error | 0 | 0 | 0 | 0
SP too close to MOP | 0 | 0 | 0 | 0
Unknown/ Not Reported | 0 | 0 | 0 | 0
Grand Total | 1 | 2 | 4 | 7
| 1 2012 HP OP Events | 2 2012 HP OP Events | 4 2012 HP OP Events | 7 2012 Total HP OP Events
[7 empty] | 1 2012 HP OP Events | [6 empty] | 2 2012 HP OP Events | 4 2012 HP OP Events
7 2012 Total HP OP Events
Design |  |  | 1
Equipment Failure | 12 | 3 | 1
Operator Error | 15 | 8
Setpt too close to MOP | 28
Unknown/Not Reported | 5
2012 OP Events - Transmission
Reason | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total
Design | 0 | 0 | 1 | 1
Equipment Failure | 12 | 3 | 1 | 16
Operator Error | 15 | 8 | 0 | 23
SP too close to MOP | 28 | 0 | 0 | 28
Unknown/ Not Reported | 5 | 0 | 0 | 5
Grand Total | 60 | 11 | 2 | 73
| 60 2012 Transmission OP Events | 11 2012 Transmission OP Events | 2 2012 Transmission OP Events | 73 2012 Total Transmission OP Events
[7 empty] | 60 2012 Transmission OP Events | [6 empty] | 11 2012 Transmission OP Events | 2 2012 Transmission OP Events
73 2012 Total Transmission OP Events
SCADA vs Non-SCADA | 2012-01-01 | 2012-02-01 | 2012-03-01 | 2012-04-01 | 2012-05-01 | 2012-06-01 | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01
Non-SCADA | 2012-01-01: 2; 2012-02-01: 1; 2012-05-01: 1; 2012-09-01: 1; 2012-10-01: 1; 2012-11-01: 1; 2012-12-01: 3 | 10
SCADA | 66 | 67 | 92 | 47 | 12 | 2 | 2 | 2 | 1 | 4 |  | 3 | 298
Grand Total | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 | 308
Equipment Failure | 2012-03-01: 4
Operator Error | 2012-03-01: 4
Unknown/ Not Reported | 2012-01-01: 376; 2012-02-01: 197; 2012-03-01: 43
2011 OP Events - LP Distribution
Reason | 2012-01-01: MOP Excursions less than 2%; 2012-02-01: MOP Excursions from 2% to less than 10%; 2012-03-01: MOP Excursions greater than 10%; 2012-04-01: Grand Total
Design | 2012-01-01: 0; 2012-02-01: 0; 2012-03-01: 0; 2012-04-01: 0
Equipment Failure | 2012-01-01: 0; 2012-02-01: 0; 2012-03-01: 4; 2012-04-01: 4
Operator Error | 2012-01-01: 0; 2012-02-01: 0; 2012-03-01: 4; 2012-04-01: 4
SP too close to MOP | 2012-01-01: 0; 2012-02-01: 0; 2012-03-01: 0; 2012-04-01: 0
Unknown/ Not Reported | 2012-01-01: 376; 2012-02-01: 197; 2012-03-01: 43; 2012-04-01: 616
Grand Total | 2012-01-01: 376; 2012-02-01: 197; 2012-03-01: 51; 2012-04-01: 624
| 376 2011 LP OP Events | 197 2011 LP OP Events | 51 2011 LP OP Events | 624 2011 Total LP OP Events
| 2012-07-01: 376 2011 LP OP Events |  | 197 2011 LP OP Events | 51 2011 LP OP Events
624 2011 Total LP OP Events
2011 OP Events - HP Distribution
Reason | 2012-01-01: MOP Excursions less than 2%; 2012-02-01: MOP Excursions from 2% to less than 10%; 2012-03-01: MOP Excursions greater than 10%; 2012-04-01: Grand Total
Design | 2012-01-01: 0; 2012-02-01: 0; 2012-03-01: 1; 2012-04-01: 1
Equipment Failure | 2012-01-01: 9; 2012-02-01: 3; 2012-03-01: 1; 2012-04-01: 13
Operator Error | 2012-01-01: 5; 2012-02-01: 3; 2012-03-01: 4; 2012-04-01: 12
SP too close to MOP | 2012-01-01: 5; 2012-02-01: 0; 2012-03-01: 0; 2012-04-01: 5
Unknown/ Not Reported | 2012-01-01: 4; 2012-02-01: 0; 2012-03-01: 3; 2012-04-01: 7
Grand Total | 2012-01-01: 23; 2012-02-01: 6; 2012-03-01: 9; 2012-04-01: 38
| 23 2011 HP OP Events | 6 2011 HP OP Events | 9 2011 HP OP Events | 38 2011 Total HP OP Events
| 2012-07-01: 23 2011 HP OP Events |  | 6 2011 HP OP Events | 9 2011 HP OP Events
38 2011 Total HP OP Events
2011 OP Events - Transmission
Reason | 2012-01-01: MOP Excursions less than 2%; 2012-02-01: MOP Excursions from 2% to less than 10%; 2012-03-01: MOP Excursions greater than 10%; 2012-04-01: Grand Total
Design | 2012-01-01: 21; 2012-02-01: 3; 2012-03-01: 2; 2012-04-01: 26
Equipment Failure | 2012-01-01: 11; 2012-02-01: 6; 2012-03-01: 1; 2012-04-01: 18
Operator Error | 2012-01-01: 23; 2012-02-01: 12; 2012-03-01: 1; 2012-04-01: 36
SP too close to MOP | 2012-01-01: 0; 2012-02-01: 1; 2012-03-01: 0; 2012-04-01: 1
Unknown/ Not Reported | 2012-01-01: 23; 2012-02-01: 8; 2012-03-01: 0; 2012-04-01: 31
Grand Total | 2012-01-01: 78; 2012-02-01: 30; 2012-03-01: 4; 2012-04-01: 112
| 78 2011 Transmission OP Events | 30 2011 Transmission OP Events | 4 2011 Transmission OP Events | 112 2011 Total Transmission OP Events
| 2012-07-01: 78 2011 Transmission OP Events |  | 30 2011 Transmission OP Events | 4 2011 Transmission OP Events
112 2011 Total Transmission OP Events

## MonthlyReportDetail (hidden)
Location | Date/Time | Max Pressure Reached | MOP | % over MOP | Cause Code | Description | Preliminary Root Causes (Root Cause Evaluation not completed)
Corning-Reg Distribution | North Valley | 2014-01-07 10:32 | 66.9871 | 60 |  | Called Patrick Harding about hihi and mop alarm for Corning Reg. he's currently investigating the situation, he will call back once he finds something out NOTED HIHI, MOP ALARM FOR CORNING REG. THANK YOU spoke with Patrick Harding again, he's sending someone out to check on it now appx eta is 1 hour | • Immediately switched runs and lowered the set pressure to 55 PSIG. • Initial diagnosis appears to be failed regulator and monitor - Performed 'B' type inspection • Equipment was saturated with large amounts of pipeline liquid - so the liquids were removed. • The filters and sense lines to the pilot were also coated and were dripping upon disassembly. • More information to come as the investigation continues.
Topock Compressor Station Topock1 Plant B K Suct Press | Kern | 2014-01-10 17:44 | 699 | 660 |  | The governor on K-8 was malfunctioning (wasn’t able to speed up… only could get 220 rpms out of it) we decided to put K-7 on line and take K-8 offline (K-9 was also on line) before I could take K-8 off, K-7 came on line and pulled the suction pressure down when it automatically loaded. (K-9 valves failed to operate during shutdown, noticed high pressure on L300B suction at the time (698 psig) we isolated the units and opened the stack valve on K-8 to blowdown the pressure to 635 psig) the station was set up with AB-1, AB-3 and TW-6 closed while on line at the time... After L300B equalized we opened AB-3, AB-1 and TW-6 to equalize the plant suction pressures. We then closed the PIV valve to TW-1 and slowly opened TW-1 shutdown OP to reset at this time and have called out techs and a mech … | • Review possible relief valve installation between the suction side and Transwestern Gas in accordance to standards • Check the current status of the MAOP uprate for Topock suction piping • Further discussion on the procedures for abnormal operating conditions at Topock Compressor Station with a split suction • Perform a CAP investigation to further comprehend the root cause of the OP event
Corning-Reg Distribution | North Valley | 2014-01-13 07:52 | 89 | 60 |  | mop breach at corning reg at 0752 hrs. called t&r supervisor Patrick Harding and he stated he will be sending a tech out to corning reg Kelly; mark bailey called gdcc to advise that he is currently at corning reg and that as far as he can tell, this pipeline liquids event is identical to the issue that occurred last week. He has been going out to this station every day to celar out the liquid that's been coming through. he said the standby side of reg is fully activated, and he will be speaking with his dept to get a plan together to get this issue resolved. he will call back when more information is available and keep gdcc apprised of all updates kelly | • Repeat B inspection • and repairs on affected equipment • Leak Survey on system
9th and I St. | Eureka | 2014-01-15 05:50 | 11.3 | 10.5 |  | Description: Cause determined to be regulator and monitor set points were to close together and frequent oscillations of regulated pressure combined with high-flow conditions due to cold morning temperatures caused near-hit event. The condition location is actually the SCADA 'end of line' location 11 blocks away that did not reflect the excursion | • Immediate action was lowering regulator set-point to 8 in-WC. • Daily monitoring of chart will take place during cold weather, high gas demand conditions. Notifications were made as required. • Increase MAOP to 14 in

## Tracking2012 (hidden)
2012 OP Events - Thru Dec 26, 2012 | [7 empty] | 2011 OP Events
| Gas Log # of OP Events | Gas Log event criteria | Approach 1 # of OP Events | Approach 1 event criteria | Approach 2 # of OP Events | Approach 2 event criteria |  |  | Gas Log # of OP Events | Gas Log event criteria | Approach 1 # of OP Events | Approach 1 event criteria | Approach 2 # of OP Events | Approach 2 event criteria
HP Distribution | 7 | MAOP | 7 | MAOP | 7 | MAOP |  | HP Distr | 19 | MAOP | 38 | MAOP | 38 | MAOP
LP Distribution | 26 | some 12" HiHi, some 10.5" Hi | 13 | 12 in WC | 228 | 10.5 in WC |  | LP Distr | 6 | some 12" HiHi, some 10.5" Hi | 35 | 12 in WC | 624 | 10.5 in WC
Transmission | 34 | MOP+3, some MOP | 19 | MOP+3 | 73 | MOP |  | Trans | 51 | MOP+3, some MOP | 87 | MOP+3 | 129 | MOP
Total | 67 |  | 39 |  | 308 |  |  | Total | 76 |  | 160 |  | 791
| 33 |  |  |  | 235 |  |  |  | adjusted 3 events after review of root cause to not OP |  |  |  | 662
Over Pressure Event Frequency Metric Tracking - 2012 |  |  |  |  | Green |  | Amber |  | Red
[5 empty] | <=42 |  | >42 and <=49 |  | >49
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
Expected Path: Goal OP events | 6 | 6 | 5 | 5 | 4 | 4 | 3 | 3 | 2 | 2 | 1 | 1 |  | 42 | 42
Actual OP events - Reported | 7 | 1 | 10 | 23 | 6 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  | 67 | 67
Actual OP Events - Approach 1 | 7 | 1 | 12 | 3 | 4 | 2 | 2 | 0 | 1 | 1 | 1 | 5 |  | 39 | 39
Actual OP Events - All OP events | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  | 308 | 308
Cumulative
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Expected Path: Goal OP events | 6 | 12 | 17 | 22 | 26 | 30 | 33 | 36 | 38 | 40 | 41 | 42
Actual OP events - Reported | 7 | 8 | 18 | 41 | 47 | 49 | 51 | 53 | 55 | 60 | 61 | 67
Actual OP Events - Approach 1 | 7 | 8 | 20 | 23 | 27 | 29 | 31 | 31 | 32 | 33 | 34 | 39
Actual OP Events - All OP events | 68 | 136 | 228 | 275 | 288 | 290 | 292 | 294 | 296 | 301 | 302 | 308
Breakdown of Actual OP Events - All OP Events
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
HP Distribution | Jan: 3; Feb: 1; Sep: 1; Dec: 2 |  | 7
LP Distribution | Jan: 53; Feb: 60; Mar: 66; Apr: 37; May: 9; Dec: 3 |  | 228
Transmission | 12 | 7 | 26 | 10 | 4 | 2 | 2 | 2 | 1 | 5 | 1 | 1 |  | 73
Total | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  | 308 | 308
[8 empty] | forecast | forecast | forecast | forecast | forecast
2012 OP Events
Comments
OP Events by Month | Jul: OP Events by Quarter
Month | Distribution – MP/HP | Distribution - Low Pressure | Transmission | Grand Total | cumul total | 2013 proposed | Quarter | Distribution – MP/HP | Distribution - Low Pressure | Transmission | Grand Total | cumul total
1 | 3 | 2 | 2 | 7 | 7 | 4 | Qrtr 1 | 4 | 4 | 10 | 18 | 18
2 | 1 | 0 | 0 | 1 | 8 | 3 | Qrtr 2 | 0 | 19 | 12 | 31 | 49
3 | 0 | 2 | 8 | 10 | 18 | 3 | Qrtr 3 | 1 | 0 | 5 | 6 | 55
4 | 0 | 17 | 6 | 23 | 41 | 2 | Qrtr 4 | 2 | 3 | 7 | 12 | 67
5 | 0 | 2 | 4 | 6 | 47 | 1 | Grand Total | 7 | 26 | 34 | 67
6 | Jan: 0; Feb: 0; Mar: 2; Apr: 2; May: 49; Jun: 1
7 | Jan: 0; Feb: 0; Mar: 2; Apr: 2; May: 51; Jun: 1
8 | Jan: 0; Feb: 0; Mar: 2; Apr: 2; May: 53; Jun: 1
9 | Jan: 1; Feb: 0; Mar: 1; Apr: 2; May: 55; Jun: 1
10 | Jan: 0; Feb: 0; Mar: 5; Apr: 5; May: 60; Jun: 2
11 | Jan: 0; Feb: 0; Mar: 1; Apr: 1; May: 61; Jun: 2
12 | Jan: 2; Feb: 3; Mar: 1; Apr: 6; May: 67; Jun: 3
Grand Total | Jan: 7; Feb: 26; Mar: 34; Apr: 67; Jun: 24
Dasboard Variance Comments:
For December had 1 transmission event, 1 HP distribution event and 3 LP distribution event (more than expected). Preliminary root cause: LP distribution OP events were flooding related, both transmiission and HP distribution events were design related.
Team formed to address root causes of overpressure events. Backbone pressure reductions completed - 180 HP distribution pressure reductions completed in October and November. Distribution team lowered all LP reg pressures. Planning evaluating impact completed of proposed pressure reductions on local transmission systems and distribution systems. Planning completed evaluation of winter impacts of lowering LP regulator pressures. Initiated MOP alarm in Citect for all process gas pressure points to improve visibility of OP events. De-watering program for vaults likely to flood was instituted.
Will not return to green for the remainder of the year

## LP SubSystems (hidden)
SCADA Points LP Pressure
SCADA Point Name | SCADA Point Description | Division | LP System Name
OC1_PT0041 | Alameda Broadwy/Linc Dist Pres | East Bay | Alameda LP
OC1_PT0047 | Alameda Grand/Alameda Dist Pres | East Bay | Alameda LP
OC1_PT0048 | Alameda Grand/Pacific Dist Pres | East Bay | Alameda LP
OC2_PT0043 | Alameda Pacifc/6Th Dist Pres | East Bay | Alameda LP
OC1_PT0045 | Berkeley Fairvw/Adeln Dist Pres | East Bay | Oakland N LP
OC2_PT2109 | 34Th/Telegph Lp Pres | East Bay | Oakland N LP
OC1_PT0049 | Oakland Cooldg/Brookdl Dist Pres | East Bay | Oakland S LP
OC2_PT2105 | Foothl/Rosdl Lp Pres | East Bay | Oakland S LP
OC2_PT2108 | 19Th/E-26Th Lp Pres | East Bay | Oakland S LP
OC2_PT2111 | E-12Th/21St Lp Pres | East Bay | Oakland S LP
OC2_PT2106 | Bancrt/Havct Lp Pres | East Bay | Oakland SII LP
OC2_PT2107 | Flora/67Th Lp Pres | East Bay | Oakland SII LP
OC1_PT0031 | Oakland Center/8Th Dist Pres | East Bay | Oakland W LP
OC1_PT0046 | Richmond Penn/9Th Dist Pres | East Bay | Richmond N LP
OC2_PT0102 | Richmond 16Th/Bisl Lp Pres | East Bay | Richmond S LP
FFN_PT0033 | Fresno Fowler Lp Pres | Fresno | Fowler LP
FFN_PT0035 | Fresno Fresno-High Lp Pres | Fresno | Fresno High LP
FFN_PT0031 | Fresno Selma Lp Pres | Fresno | Selma LP
FFN_PT0041 | Fresno Tulare Alley Lp Pres | Fresno | West Side LP
K09_PT0031 | Bakersfield Beale Alley Dist Pr | Kern | Bakersfield LP
REU_PT0001 | Eureka 9Th/I Lp Pres | North Coast | Eureka LP System
STF_PT0002 | Chico Lo Press | North Valley | Chico LP (R-L03, R-L04, R-L05, R-L09, R-L12, R-L14)
SRD_PT0001 | Red-Bluff-Dist Low Press | North Valley | Red Bluff LP (R-106, R-105)
SSA_PT0101 | 19Th/C Lo Press | Sacramento | Sacramento Large LP - 10.5" WC MAOP
SSA_PT0102 | 24Th/Brdwy Lo Press | Sacramento | Sacramento Large LP - 10.5" WC MAOP
SSA_PT0103 | 38Th/H Lo Press | Sacramento | Sacramento Large LP - 10.5" WC MAOP
SSA_PT0106 | 3Rd/I Lo Press | Sacramento | Sacramento Large LP - 10.5" WC MAOP
SSA_PT0111 | 12Th/S Lo Press | Sacramento | Sacramento Large LP - 10.5" WC MAOP
SSA_PT0131 | Sacramento 14Th/52Nd Lp Pres | Sacramento | Sacramento Small LP - 10.5" WC MAOP
SWO_PT0002 | Wdlnd-Twn Lp Dist Press | Sacramento | Woodland - LP 10.5" WC MAOP
NSF_PT0018 | Amazn/Missn Lp Pres | San Francisco | Alemany 10.5"w.c.
NSF_PT0014 | Silvr/Hlyok Lp Pres | San Francisco | Bayview 10.5"w.c.
NSF_PT0012 | Tarvl/Wwona Lp Pres | San Francisco | Mount Davidson 10.5"w.c.
NSF_PT0020 | Irving/20Th Lp Pres | San Francisco | Sunset 10.5"w.c.
NSF_PT0016 | Presdio/Gry Lp Pres | San Francisco | Western Addition 10.5"w.c.
JSJ_PT0041 | Sn-Jose Gilroy Dist Pres | San Jose | MH-GILROY_Gilroy LP system DR H-98 (6th & Railroad)
JSJ_PT0044 | Sn-Jose 15Th & St John Dist Pr | San Jose | SANTA_CLARA_VALLEY_15th and St. John LP system DR F-63
JSJ_PT0039 | Sn-Jose Shortrg/30Th Dist Pres | San Jose | SANTA_CLARA_VALLEY_30th and Shortridge LP system DR F-53
JSJ_PT0037 | Sn-Jose Bird/Fuller Dist Pres | San Jose | SANTA_CLARA_VALLEY_Bird and Fuller LP system DR F-83
JSJ_PT0035 | Sn-Jose Emory/Chestnt Dist Pres | San Jose | SANTA_CLARA_VALLEY_Emory and Chestnut LP system DR F-55
JLF_PT0002 | Lfyt-Cvc Lo Press | San Jose | SANTA_CLARA_VALLEY_Park and Newhall LP system DR F-25
JSJ_PT0031 | Sn-Jose 12Th/Margaret Dist Pres | San Jose | SANTA_CLARA_VALLEY_Santa Clara and Margaret LP system DR F-77
JSJ_PT0033 | Sn-Jose Humboldt/Vine Dist Pres | San Jose | SANTA_CLARA_VALLEY_Vine and Humboldt LP system DR G-09
SMY_PT0031 | Mary-Glc Willow Alley/12Th Lp Pres | Sierra | MRY; Marysville Low Pressure
FEH_PT0003 | Elm & Hutch Lodi Lp Dist Press | Stockton | Lodi LP
FST_PT0043 | Stockton GLC Worth/Bieghle Lp Pres | Stockton | Stockton LP ST-LP-01-C (Worth & Biehle)
FST_PT0041 | Stockton GLC 5Th/Monroe Lp Pres | Stockton | Stockton LP ST-LP-02-C (5th & Monroe)
FST_PT0037 | Stockton GLC Carltn/Mtdiab Lp Pres | Stockton | Stockton LP ST-LP-03-C (Carlton & Mt Diablo)
FST_PT0039 | Stockton GLC Church/Snjose Lp Pres | Stockton | Stockton LP ST-LP-04-C (Church & San Jose)
FSN_PT0004 | Airport-Way & Sonora Lp Press | Stockton | Stockton LP ST-LP-05A-C (Airport & Sonora)
FST_PT0033 | Stockton GLC Sunset/Chrkee Lp Pres | Stockton | Stockton LP ST-LP-06-C (Sunset & Cherokee)
FST_PT0035 | Stockton GLC Harding/Huntr Lp Pres | Stockton | Stockton LP ST-LP-07-C (Harding & Hunter)
FST_PT0031 | Stockton GLC Filbert/Hardg Lp Pres | Stockton | Stockton LP ST-LP-08-C (Filbert & Harding)
FFN_PT0053 | Yosemite Madera Lp Pres | Yosemite | Madera LP
FME_PT0032 | Mrcd-V60 Yosemite Merced Lp Pres | Yosemite | Merced LP
FCT_PT0008 | Cffe-Clta G Street Pressure | Yosemite | Modesto LP MOLP-3,15, & 16
FST_PT0051 | Stockton GLC Yosemite Modesto Lp Pres | Yosemite | Modesto LP MOLP-5,7,10, & 12
F1J_PT0030 | Yosemite Oakdale Lp Press | Yosemite | Oakdale LP
FST_PT0061 | Stockton GLC Harding/Funston Lp Pres | Yosemite | Stockton LP ST-LP-05B-C (Harding & Funston)
FWA_PT0030 | West Ave Reg Yosemite Turlock LP Pres | Yosemite | Turlock LP
None |  | Fresno | Fresno Downtown LP (Modeled with F-C-S)
N9M_PT0002 | Ninth and Market Lo Press | San Francisco | 9th St and Market St 10.5"w.c.

## Regulation Sta. (hidden)
Note: Each row represents a single pressure control device. Filter by the HIS Name column to see all the equipments for an individual HIS.
Note: The source equipment shown is for normal operating conditiions, in some circumstances the pipeline flow will change.
Note: The equipment is listed by Pressure Control Device therefore in a parallel run station with Reg/Mon there will be two line items listed, one for each run.
HIS_ID | Plng Engr | Planning Model | HIS Name | HIS Description | Result | PCE | Type | Location | Area | Station Description | Additional Station information | Device Type | Valve | MOP | MAOP | District/Div | Comments
1 | MJA3 | TP_NORTH_BAY | Benica_175 | Benicia DFM | C4-V1 | PCE341 | Station | Vallejo | NGO | L-21 to Benicia DFM | Glenn Cove & Benicia Rd Reg OD 800103 V-3, 4, 5, 6; Vallejo Station OD 086452 V-33, 34, 35, 36 | Monitor | 34 | 175 | 175 | North Bay
1 | MJA3 | TP_NORTH_BAY | Benica_175 | Benicia DFM | C4-V1 | PCE340 | Station | Vallejo | NGO | L-21 to Benicia DFM | Glenn Cove & Benicia Rd Reg OD 800103 V-3, 4, 5, 6; Vallejo Station OD 086452 V-33, 34, 35, 37 | Monitor | 33 | 175 | 175 | North Bay
2 | MJA3 | TP_NORTH_BAY | Benicia_Ind_Park_175 | Benicia Industrial Park | C4-V1 | MJA3PCE800 | Reg Station | East 2nd St & Reservoir Rd, Benicia |  | V35, East 2nd St & Reservoir Rd Reg Station, Benicia | E. 2nd St & Resvr Rd OD0800104 V-3, 4, 5, 6
3 | MJA3 | TP_NORTH_BAY | Calistoga_150 | Calistoga DFM serving Calistoga & Angwin | C3-V1 | MJA3PCE801 | Reg Station | Pratt Ave & Main St, St Helena |  | R108, York Creek Reg Station, St Helena | York Creek Reg OD0800390 V-3, 4, 5, 6
4 | MJA3 | TP_NORTH_BAY | Calistoga_250 | Calistoga 250# DFM | C2-V1 | MJA3PCE802 | Reg Station | Hwy 29 & Zinfandel Ln, St Helena |  | R68, Hwy 29 & Zinfandel Ln Reg Station, St Helena | Hwy 29 & Zinfandel OD0800126, V-3, 4, 5, 6
5 | MJA3 | TP_NORTH_BAY | Cotati_150 | Cotati DFM | C4-V3 | PCE365 | Regulator Station | U.S. 101 & Old Rdwd Hwy | NGO | L-21 to Cotati DFM | Hwy 101 & Old Redwood Hwy OD0800129 V-19, 20, 21, 22; Cotati Reg OD081596 V-4, 5 | Monitor | 20 | 150 | 150 | North Coast
5 | MJA3 | TP_NORTH_BAY | Cotati_150 | Cotati DFM | C4-V3 | PCE364 | Regulator Station | U.S. 101 & Old Rdwd Hwy | NGO | L-21 to Cotati DFM | Hwy 101 & Old Redwood Hwy OD0800129 V-19, 20, 21, 22; Cotati Reg OD081596 V-4, 6 | Monitor | 19 | 150 | 150 | North Coast
5 | MJA3 | TP_NORTH_BAY | Cotati_150 | Cotati DFM | C4-V3 | MJA3PCE803 | Reg Station | West Sierra Ave & Old Redwood Hwy, Cotati |  | R375, Cotati Reg Pit, Cotati | Hwy 101 & Old Redwood Hwy OD0800129 V-19, 20, 21, 22; Cotati Reg OD081596 V-4, 7
6 | MJA3 | TP_NORTH_BAY | Fairfield_230 | Fairfield DFM to Tabor & Dover | C2-V1 | MJA3PCE804 | Reg Station | Union Ave & Ohio St, Fairfield |  | R07, Suisun-Fairfield Reg Station, Fairfield | Suisun-Fairfield Reg OD081528 V-56, 57, 58, 59
7 | MJA3 | TP_NORTH_BAY | Fulton_150 | Fulton & Grant Rd DFM to Wikiup and Healdsburg | C4-V1 | MJA3PCE807 | Reg Station | Hart Ln & Fulton Rd, Santa Rosa |  | R124, Hart Ln & Fulton Rd Reg Station, Santa Rosa | Grant School Rd Reg OD082460 V-8, 9, 10, 11 ; Fulton Reg OD0800190 V-13, 14, 15, 16
7 | MJA3 | TP_NORTH_BAY | Fulton_150 | Fulton & Grant Rd DFM to Wikiup and Healdsburg | C4-V1 | MJA3PCE808 | Reg Station | Grant School Rd & Old Redwood Highway, Healdsburg |  | R69, Grant School Rd Reg Station, Healdsburg | Grant School Rd Reg OD082460 V-8, 9, 10, 11 ; Fulton Reg OD0800190 V-13, 14, 15, 17
8 | MJA3 | TP_NORTH_BAY | Fairfield_400 | Fairfield DFM to Travis AFB and Vacaville Prison | C1-V1 | MJA3PCE806 | Reg Station | Petersen Rd, Fairfield |  | R09, Vacaville Reg Station, Fairfield | Vacaville Regulator Station OD081527 V-R1, R2, R3, R4
9 | MJA3 | TP_NORTH_BAY | Fairfield_275 | Fairfield DFM to Rancho Solano | C1-V3 | MJA3PCE805 | Reg Station | Cordelia & Chadbourne Rd, Fairfield |  | R03, Cordelia & Chadbourne Rd Reg Station, Fairfield | Cordelia & Chadbourne Reg OD0800494 V-4, 5, 8, 9
10 | MJA3 | TP_NORTH_BAY | Hiddenbrook_175 | Hiddenbrook DFM to Sky Valley | C1-V1 | MJA3PCE809 | Reg Station | Sky Valley Rd, Vallejo |  | V54, Sky Valley Reg Station, Vallejo | Sky Valley OD0800479 V-3, 4, 5, 6
11 | MJA3 | TP_NORTH_BAY | Mare_Island_100 | Mare Island DFM | C4-V1 | MJA3PCE810 | Reg Station | Pine & Woodrow Ave, Vallejo |  | V13, Pine & Woodrow Ave Reg Station, Vallejo | Pine & Woodrow Ave OD0800157 V-5, 6, 7, 8
12 | MJA3 | TP_NORTH_BAY | Marin_175 | Marin DFM | C3-V1 | PCE339 | Holder | San Rafael | NGO | L-21 to DFM 12-0402-01 | San Rafael Meter & Reg OD183804 V-6, 7, 8, 9, 15, 16, 17, 18 | Monitor | 52 | 175 | 175 | North Bay
12 | MJA3 | TP_NORTH_BAY | Marin_175 | Marin DFM | C3-V1 | PCE338 | Holder | San Rafael | NGO | L-21 to DFM 12-0401-01 | San Rafael Meter & Reg OD183804 V-6, 7, 8, 9, 15, 16, 17, 19 | Monitor | 50 | 175 | 175 | North Bay
13 | MJA3 | TP_NORTH_BAY | Marine_World_125 | Marine World DFM | C3-V2B | MJA3PCE811 | Reg Station | Hwy 80 & Coach Lane, Vallejo |  | V32, Hwy 80 & Coach Lane Reg Station, Vallejo | Hwy 80 & Coach Lane 0800102 V-1
14 | MJA3 | TP_NORTH_BAY | Napa_Valley_150 | Napa Valley 150# DFM | C3-V2B | MJA3PCE812 | Reg Station | Redwood Rd & Solano Ave, Napa |  | R51, Solano Ave Reg Station, Napa | Solano Ave Reg OD0800130 V-3, 4, 5, 6
15 | MJA3 | TP_NORTH_BAY | North_Bay_450 | North Bay 450, Napa Y to Calistoga, Marin, and Santa Rosa | C4-V1 | PCE333 | Meter Station | Napa "Y' | NGO | L-210 to L-21 | Napa Y OD385170 V-5, 11, 25.98, 60 | Monitor | 25.98 | 450 | 450 | North Bay
15 | MJA3 | TP_NORTH_BAY | North_Bay_450 | North Bay 450, Napa Y to Calistoga, Marin, and Santa Rosa | C4-V1 | PCE334 | Meter Station | Napa "Y' | NGO | L-210 to L-21 | Napa Y OD385170 V-5, 11, 25.98, 61 | Monitor | 5 | 450 | 450 | North Bay
16 | MJA3 | TP_NORTH_BAY | North_Bay_610 | North Bay 610, Santa Rosa Compressor to Willits | C2-V1 | PCE354 | Compressor Station | Santa Rosa | NGO | Discharge Pressure Control (K-1) | Santa Rosa Compressor OD082485 | PLC | N/A | 610 | 720 | North Coast
16 | MJA3 | TP_NORTH_BAY | North_Bay_610 | North Bay 610, Santa Rosa Compressor to Willits | C2-V1 | PCE355 | Compressor Station | Santa Rosa | NGO | Discharge Pressure Control (K-2) | Santa Rosa Compressor OD082486 | PLC | N/A | 610 | 720 | North Coast
17 | MJA3 | TP_NORTH_BAY | North_Bay_650 | North Bay 650, Creed to Napa "Y" and Herrmann Station | C2-V1 | PCE58 | Station | Creed | NGO | L-210 W from L400/L401 | Creed Station OD182416 V-7, 8, 10, 14, 16, 17 | Monitor | 16 | 650 | 650 | Rio Vista
17 | MJA3 | TP_NORTH_BAY | North_Bay_650 | North Bay 650, Creed to Napa "Y" and Herrmann Station | C2-V1 | PCE57 | Station | Creed | NGO | L-210 W from L400/L401 | Creed Station OD182416 V-7, 8, 10, 14, 16, 18 | Monitor | 14 | 650 | 650 | Rio Vista
18 | MJA3 | TP_NORTH_BAY | Novato_150 | Novato DFM, Novato Blvd and Diabl to Novato Blvd & Reservoir Rd | C2-V3 | MJA3PCE813 | Reg Station | Diablo Ave & S. Novato Blvd, Novato |  | RA04, Diablo Ave & S. Novato Blvd Reg Station, Novato | Diablo Ave & S. Novato Blvd OD0800128 V-5, 6, 7, 8
19 | MJA3 | TP_NORTH_BAY | Pine_St_150 | Pine St 150# DFM, Pine St Napa Meter Station to Browns Valley | C2-V3 | MJA3PCE814 | Reg Station | Pine St and Highway 29, Napa |  | R38, Pine St Reg Station, Napa | Pine St Reg OD081513 V-13, 24, E
20 | MJA3 | TP_NORTH_BAY | Schellville_150 | Schellville DFM, Schellville Reg Station to 5th St West & MacArthur | C2-V1 | MJA3PCE815 | Reg Station | Highway 121 & Fremont Rd, Sonoma |  | R543, Schellville Reg Station, Sonoma | Shellville Reg 081514 V-10, 11, 12, 13
21 | MJA3 | TP_NORTH_BAY | Sebastopol_150 | Sebastopol 150# DFM, Stone Station Reg to Graton | C4-V1 | MJA3PCE816 | Reg Station | Stone Station Rd, Sebastopol |  | R446, Stone Station Rd Reg Station, Sebastopol | Stone Reg Station OD0800563 V-4, 5, 6, 7
22 | MJA3 | TP_NORTH_BAY | Sebastopol_275 | Sebastopol 275# DFM, Madrone Station to Stone Station | C2-V1 | MJA3PCE817 | Reg Station | Stony Pt Rd & Madrone Ave, Cotati |  | R384, Madrone Ave Reg Station, w/o Cotati | Madrone Ave Reg OD082329 V-23, 24, 27, 28
23 | MJA3 | TP_NORTH_BAY | Sonoma_200 | Sonoma DFM, Monroe Station to Mountain View Reg and 5th St West & MacArthur to Oakmont | C4-V1 | PCE367 | Regulator Station | Monroe | 7 | L-21C to DFM (1304-01, 1305-01) | Monroe Reg OD081915 V-18, 19, 20, 21; 5th St West & Macarthur Reg OD0800211 V-6, 7 | Monitor | 21 | 200 | 200 | North Coast
23 | MJA3 | TP_NORTH_BAY | Sonoma_200 | Sonoma DFM, Monroe Station to Mountain View Reg and 5th St West & MacArthur to Oakmont | C4-V1 | PCE366 | Regulator Station | Monroe | 7 | L-21C to DFM (1304-01, 1305-01) | Monroe Reg OD081915 V-18, 19, 20, 21; 5th St West & Macarthur Reg OD0800211 V-6, 8 | Monitor | 20 | 200 | 200 | North Coast
23 | MJA3 | TP_NORTH_BAY | Sonoma_200 | Sonoma DFM, Monroe Station to Mountain View Reg and 5th St West & MacArthur to Oakmont | C4-V1 | MJA3PCE818 | Reg Station | Fifth St West & Macarthur, Sonoma |  | R591, Fifth St West & Macarthur Reg Station, Sonoma | Monroe Reg OD081915 V-18, 19, 20, 21; 5th St West & Macarthur Reg OD0800211 V-6, 9
24 | MJA3 | TP_NORTH_BAY | Soscol_150 | Soscol DFM, Napa Y to Soscol & Souza (R42) | C2-V1 | MJA3PCE819 | Reg Station | Kaiser Rd, Napa |  | R48, Kaiser Rd Reg Station, Napa | Napa Y OD385170 V-70, 71, 76, 79, Kaiser Rd Reg OD0800127 V-3, 4, 5, 6
24 | MJA3 | TP_NORTH_BAY | Soscol_150 | Soscol DFM, Napa Y to Soscol & Souza (R42) | C2-V1 | PCE336 | Meter Station | Napa "Y' | NGO | L-210 to Napa DFM | Napa Y OD385170 V-70, 71, 76, 79, Kaiser Rd Reg OD0800127 V-3, 4, 5, 7 | Monitor | 71 | 150 | 150 | North Bay
24 | MJA3 | TP_NORTH_BAY | Soscol_150 | Soscol DFM, Napa Y to Soscol & Souza (R42) | C2-V1 | PCE337 | Meter Station | Napa "Y" | NGO | L-210 to Napa DFM | Napa Y OD385170 V-70, 71, 76, 79, Kaiser Rd Reg OD0800127 V-3, 4, 5, 8 | Monitor | 79 | 150 | 150 | North Bay
25 | MJA3 | TP_NORTH_BAY | Trancas_250 | Trancas DFM, Napa | C2-V1 | MJA3PCE820 | Reg Station | Coffield Ave Cul de Sac, Napa |  | R41, Coffield Ave Cul de Sac Reg Station, Napa | Coffield Reg OD0800210 V-3, 4, 5, 6
26 | MJA3 | TP_NORTH_BAY | Vallejo_250 | Vallejo DFM, Herrmann Station to Napa "Y" | C2-V1 | PCE335 | Meter Station | Napa "Y' | NGO | L-210 to L-21 | Napa Y OD385170 V-9, 10; Hermann Station 082454 V-2, 9 | Monitor | 9 | 250 | 275 | North Bay
26 | MJA3 | TP_NORTH_BAY | Vallejo_250 | Vallejo DFM, Herrmann Station to Napa "Y" | C2-V1 | PCE332 | Station | Herrmann | NGO | L-210 to 16" L-21 | Napa Y OD385170 V-9, 10; Hermann Station 082454 V-2, 10 | Monitor | 2 | 250 | 375 | North Bay
27 | MJA3 | TP_VACAVILLE | Vacaville_400 | Vacaville 400 DFM supplied from Hawkins & Lewis Primary Reg Station | C2-V1 | MJA3PCE821 | Reg Station | Hawkins & Lewis Rd, Vacaville |  | R48, Hawkins & Lewis Primary Reg Station, Vacaville | Hawkins & Lewis Primary Reg Station OD0800154 V-R1, R2, R3, R4
28 | MJA3 | TP_VACAVILLE | Vacaville_450 | Vacaville 450 DFM supplied from Vaca Dixon Primary Reg Station | C1-V1 | MJA3PCE822 | Reg Station | Meridian Rd w/o I-80 @ Vaca Dixon Substation, Vacaville |  | R21, Vaca Dixon Primary Reg Station, Vacaville | Vaca Dixon Primary Reg OD0800153 V- 4, 5, 8, 9
29 | NAH1 | TP_PENINSULA | RAYCHEM DFM | DCUST 5760, EQ000032, 1M1559 to RINGB84 | C2-V3 | nah1PCE800 | Station | DCUST 5760 |  | Feeds from L101 into Raychem DFM, 175# MOP | Van Buren Dr & Ringwood Ave Station, B-84
30 | NAH1 | TP_PENINSULA | MIDDLEFIELD RINGWOOD DFM | EQ000027, SRIEXT to SREGDN | C2-V2B | nah1PCE801 | Station | Downstream of Raychem DFM |  | Feeds from Raychem DFM into Middlefield/Ringwood DFM, 120# MOP | Middlefield & Ringwood Reg Station, B-83
31 | NAH1 | TP_PENINSULA | HEALY TO MARTIN | SEGMENT OF LINE NEAR CRESSMAN THAT IS OPERATING AT 200 PSIG | C1-V1 | nah1PCE802 | Station | Near Cressman between Healy/Martin |  | Feeds Healy towards Martin at 200# set pressure | Healy Reg Station
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE171 | Regulator Station | Martin Station | CNTL | L- 132 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 12 | 145 | 145 | Milpitas
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE168 | Meter Station | Lomita Park | CNTL | L-101 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 33.68 | 145 | 275 | Milpitas
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE169 | Meter Station | Lomita Park | CNTL | L-101 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 24 | 145 | 275 | Milpitas
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE170 | Regulator Station | Martin Station | CNTL | L- 132 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 46.59 | 145 | 145 | Milpitas
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE191 | Regulator Station | Sullivan Avenue | CNTL | L-109 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 2 | 145 | 150 | Milpitas
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE192 | Regulator Station | Sullivan Avenue | CNTL | L-109 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 13 | 145 | 150 | Milpitas
33 | NAH1 | TP_PENINSULA | L109 L132 HMB | Milpitas to Sullivan; Milpitas to Healy; control point is Sullivan inlet. CWD model currently operates at 285# at Milpitas. For CWD analysis changed Milpitas supply to 280#. For APD changed regulation at Milpitas and Sierra Vista to 280#. APD is control | C4-V1 | PCE183 | Terminal | Milpitas | CNTL | L-109 | Milpitas Terminal L132, L109 | Monitor | 39 | 300 | 375 | Milpitas
33 | NAH1 | TP_PENINSULA | L109 L132 HMB | Milpitas to Sullivan; Milpitas to Healy; control point is Sullivan inlet. CWD model currently operates at 285# at Milpitas. For CWD analysis changed Milpitas supply to 280#. For APD changed regulation at Milpitas and Sierra Vista to 280#. APD is control | C4-V1 | nah1PCE816 | Station | L132 |  | Feeds into L132 at Milpitas | Milpitas Terminal L132, L110
33 | NAH1 | TP_PENINSULA | L109 L132 HMB | Milpitas to Sullivan; Milpitas to Healy; control point is Sullivan inlet. CWD model currently operates at 285# at Milpitas. For CWD analysis changed Milpitas supply to 280#. For APD changed regulation at Milpitas and Sierra Vista to 280#. APD is control | C4-V1 | PCE182 | Terminal | Milpitas | CNTL | L-109 | Milpitas Terminal L132, L111 | Monitor | 37 | 300 | 375 | Milpitas
35 | NAH1 | TP_PENINSULA | L101 | Milpitas to Lomita | C4-V1 | nah1PCE817 | Station | L101 |  | Feeds into L101 at Milpitas | Milpitas Terminal L101
36 | NAH1 | TP_PENINSULA | FOSTER CITY DFM | 0214-01 aka Poinsettia DFM | C2-V2B | nah1PCE803 | Station | Route 0214-01 |  | Feeds Foster City DFM 170# MOP | Pointsettia Ave. Reg Station, A-74
37 | NAH1 | TP_PENINSULA | EL MONTE DFM | Fed at Sierra Vista into recently uprated 201 MOP system | C2-V3 | nah1PCE804 | Station | At Sierra Vista |  | Feeds El Monte DFM 201# MOP | Sierra Vista Ave Reg Station, B-28
38 | NAH1 | TP_PENINSULA | TODO EL MUNDO DFM | 0207-01 | C3-V3 | nah1PCE805 | Station | Route 0207-01 |  | Feeds Todo El Mundo DFM 125# MOP | Woodside and L109 Reg Station, C-10
39 | NAH1 | TP_PENINSULA | RALSTON POLHEMUS DFM | 0208-02 Ralston 0209-01 Polhemus both fed from common reg station, with Ralston endpoint as design control | C4-V3 | nah1PCE811 | Station | Routes 0208-02, 0209-01 |  | Feeds Ralston Polhemus DFM 150# MOP | Ralston Ave. Reg Station, B-03
40 | NAH1 | TP_PENINSULA | PACIFICA DFM | 0213-02, floats off L109 to San Pedro Reg at MP 0.91; Beyond 0.91 the MOP is 90# | C4-V3 | nah1PCE806 | Station | Route 0213-02 |  | Feeds Pacifica DFM 90# MOP | San Pedro Valley Reg Station, C-50
41 | NAH1 | TP_PENINSULA | NORTH FIRST ST DFM | 0806-01 San Jose | C4-V2B | nah1PCE807 | Station | Route 0806-01 |  | Feeds N 1st Street DFM 200# MOP | N. First St & Tasman Dr Reg Station, E-05
42 | NAH1 | TP_PENINSULA | GRANT STEVENS CREEK LAWRENCE DFM | 8805-03,04,23 Grant; 8807-01 Lawrence; 8806-01 Stevens Creek; Fed from 2 regs Lawrence and Whisman | C4-V2B | nah1PCE809 | Station | Routes 8805-03,04,23 Grant; 8807-01 Lawrence; 8806-01 Stevens Creek; Fed from Whisman reg |  | Feeds Grant Stevens Creek Lawrence DFM 180# MOP - Whisman | Whisman & Middlefield Reg Station, B-34 ; Lawrence & Lakehaven Dr. Reg Station, C-20
42 | NAH1 | TP_PENINSULA | GRANT STEVENS CREEK LAWRENCE DFM | 8805-03,04,23 Grant; 8807-01 Lawrence; 8806-01 Stevens Creek; Fed from 2 regs Lawrence and Whisman | C4-V2B | nah1PCE808 | Station | Routes 8805-03,04,23 Grant; 8807-01 Lawrence; 8806-01 Stevens Creek; Fed from Lawrence reg |  | Feeds Grant Stevens Creek Lawrence DFM 180# MOP - Lawrence | Whisman & Middlefield Reg Station, B-34 ; Lawrence & Lakehaven Dr. Reg Station, C-21
43 | NAH1 | TP_PENINSULA | LAFAYETTE DFM | 0804-03, Santa Clara | C4-V2B | nah1PCE810 | Station | Route 0804-03, Santa Clara |  | Feeds Lafayette DFM 180# MOP | Lafayette & Hogan Reg Station, E-07
44 | JTRc | TP_PENINSULA | SUNNYVALE DFM | aka Britton Ave, GCUST 5813 | C1-V3 | nah1PCE812 | Station | GCUST 5813 |  | Feeds Sunnyvale, Britton Ave DFM 400# MOP | Reg Station C-18
45 | NAH1 | TP_PENINSULA | ALPINE DFM | 0204-01 | C4-V3 | nah1PCE813 | Station | Route 0204-01 |  | Feeds Alpine DFM 170# MOP | Alpine Rd & Piers Ln Reg Station, C-37
46 | NAH1 | TP_PENINSULA | WALSH DFM | 0205-01 | C4-V3 | nah1PCE814 | Station | Route 0205-01 |  | Feeds Walsh Rd DFM 230# MOP | Walsh Rd Reg Station, C-21
47 | NAH1 | TP_PENINSULA | HACIENDAS DFM | 0206-01 | C4-V3 | nah1PCE815 | Station | Route 0206-01 |  | Feeds Haciendas Drive DFM 110# MOP | Woodside Rd Reg Station, C-13
48 | BHH2 | TP_CENTRAL_COAST | L306_839 | L306 - 20" transmission from Kettleman to Estrella River PLS. The Town of Avenal has small DFM's off L306 but these DFM's were modeled at 630 PSIG. | C1-V1 | PCE209 | Compressor Station | Kettleman | SGO | High Discharge Press. Shutdown | Kettleman to Milpitas Lines 100, 190 & 300 382704 Sht 1 | PLC | N/A | 839 | 840 | Kettleman
48 | BHH2 | TP_CENTRAL_COAST | L306_839 | L306 - 20" transmission from Kettleman to Estrella River PLS. The Town of Avenal has small DFM's off L306 but these DFM's were modeled at 630 PSIG. | C1-V1 | PCE208 | Compressor Station | Kettleman | SGO | Discharge Pressure Control | Kettleman to Milpitas Lines 100, 190 & 300 382704 Sht 2 | PLC | N/A | 839 | 840 | Kettleman
49 | BHH2 | TP_CENTRAL_COAST | L306_636 | L306 - 20" transmission from Estralla PLS to Morro Bay Power Plant 275 PSIG primary. SoCal gas company has a tap for emergency supply to their customers. | C1-V1 | PCE225 | Pressure Limiting Station | Estrella River | SGO | L-306 | Estrella River PLS 089659 | Monitor | 4 | 636 | 650 | Kettleman
49 | BHH2 | TP_CENTRAL_COAST | L306_636 | L306 - 20" transmission from Estralla PLS to Morro Bay Power Plant 275 PSIG primary. SoCal gas company has a tap for emergency supply to their customers. | C1-V1 | PCE226 | Pressure Limiting Station | Estrella River | SGO | L-306 to L-306 | Estrella River PLS 089660 | Monitor | 8 | 636 | 650 | Kettleman
50 | BHH2 | TP_CENTRAL_COAST | L306_275 | L306 - Primary to Morro Bay Power Plant. Short piping to the plant from the primary. Min Flow is 450 MSCF, Maximum flow is 7,000 MSCF | C1-V1 | BHH2PCE800 | Regulator Station | Morro Bay PP Pri Reg Station |  | GCUST5912_102_306_70.0200 - 082657 | Morro Bay PP Pri Reg Sta 083657
51 | BHH2 | TP_CENTRAL_COAST | L310_840 | L310 - Tres Pinos to Metz. This line feeds Calpine Cogen and Calpines peaker unit. The feed comes from Tres Pinos off L300A and B. The maximum inlet pressures over the years has been no more than 750 PSIG from L300. Loads 1500 MMCF + 300 MMCF | C1-V1 | BHH2PCE801 | Regulator Station | Tres Pinos Station |  | Tres Pinos Station - 089179 | Tres Pinos Station 089179
52 | BHH2 | TP_CENTRAL_COAST | L301A_396 | Line 301A - Old MOP 396 PSIG, CROP 394 PSIG (2011). This line is exclusive to Moss PP units 6&7. Max capacity of this line is 7,000 mcfh. Units 6&7 peak at 13,800 mcfh and the additional load will come from L301G. This line is currently operating at 3 | C1-V1 | PCE204 | Meter Station | Hollister | CNTL | L-301A from L-300A | Hollister Meter Station 282255 | Monitor | 35 | 315 | 396 | Hollister
52 | BHH2 | TP_CENTRAL_COAST | L301A_396 | Line 301A - Old MOP 396 PSIG, CROP 394 PSIG (2011). This line is exclusive to Moss PP units 6&7. Max capacity of this line is 7,000 mcfh. Units 6&7 peak at 13,800 mcfh and the additional load will come from L301G. This line is currently operating at 3 | C1-V1 | PCE207 | Meter Station | Hollister | CNTL | L-301A from L-300A | Hollister Meter Station 282256 | Monitor | 28 | 315 | 396 | Hollister
53 | BHH2 | TP_CENTRAL_COAST | CARMEL_125 | Carmel DFM - 125 PSIG MOP. This system comes off the Monterey system tied to L301B. Aguaito cuts the pressure into Carmel at 125 PSIG. | C4-V1 | BHH2PCE802 | Regulator Station | Aguajito Road Reg Station |  | Aguajito Road Reg Station - 086445 | Aguajito Road Reg Sta 086445
54 | BHH2 | TP_CENTRAL_COAST | KING_CITY_130 | King City 130 DFM has 2 feeds. The primary is from King City (off L187) and the secondary is off L310 (Metz). Both regulators are set around 125 PSIG | C2-V1 | PCE427 | Regulator Station | Metz Road | SGO | L-310 to KC DFM (1st stage) | King City Primary Regulator Station 0800096, and Metz Road Station 183721 | Monitor | 10 | 320 | 320 | Central Coast
54 | BHH2 | TP_CENTRAL_COAST | KING_CITY_130 | King City 130 DFM has 2 feeds. The primary is from King City (off L187) and the secondary is off L310 (Metz). Both regulators are set around 125 PSIG | C2-V1 | PCE429 | Regulator Station | Metz Road | SGO | L-310 to KC DFM (2nd stage) | King City Primary Regulator Station 0800096, and Metz Road Station 183722 | Monitor | 21 | 130 | 130 | Central Coast
54 | BHH2 | TP_CENTRAL_COAST | KING_CITY_130 | King City 130 DFM has 2 feeds. The primary is from King City (off L187) and the secondary is off L310 (Metz). Both regulators are set around 125 PSIG | C2-V1 | PCE426 | Primary Regulator Station | King City | SGO | L-187 to King City DFM | King City Primary Regulator Station 0800096, and Metz Road Station 183723 | Monitor | 3 | 130 | 130 | Central Coast
54 | BHH2 | TP_CENTRAL_COAST | KING_CITY_130 | King City 130 DFM has 2 feeds. The primary is from King City (off L187) and the secondary is off L310 (Metz). Both regulators are set around 125 PSIG | C2-V1 | PCE428 | Regulator Station | Metz Road | SGO | L-310 to KC DFM (1st stage) | King City Primary Regulator Station 0800096, and Metz Road Station 183724 | Monitor | 11 | 320 | 320 | Central Coast
55 | BHH2 | TP_CENTRAL_COAST | L301BCEF_408 | L301BCEF - 408 MOP CROP 344 MOP regulators set at 324 PSIG at Dolan. This system feeds primarily the Ford Ord, Monterey and Carmel areas. Secondary feed is to Harkins which feeds L187, but is now secondary to L187 and L103 is the primary | C1-V3 | PCE203 | Meter Station | Dolan Road | CNTL | L-301B from L-301G | Dolan Road Meter Sta 083812 | Monitor | 20 | 408 | 408 | Hollister
55 | BHH2 | TP_CENTRAL_COAST | L301BCEF_408 | L301BCEF - 408 MOP CROP 344 MOP regulators set at 324 PSIG at Dolan. This system feeds primarily the Ford Ord, Monterey and Carmel areas. Secondary feed is to Harkins which feeds L187, but is now secondary to L187 and L103 is the primary | C1-V3 | PCE202 | Meter Station | Dolan Road | CNTL | L-301B from L-301G | Dolan Road Meter Sta 083813 | Monitor | 19 | 408 | 408 | Hollister
56 | BHH2 | TP_CENTRAL_COAST | L103_350 | L103 - 350 MOP system. Bolsa set at 330 PSIG to California Street Regulator station | C2-V1 | PCE201 | Meter Station | Bolsa | CNTL | L-301 A&G to L-103 | Bolsa Meter Station 089655 | Monitor | 8 | 350 | 350 | Hollister
56 | BHH2 | TP_CENTRAL_COAST | L103_350 | L103 - 350 MOP system. Bolsa set at 330 PSIG to California Street Regulator station | C2-V1 | PCE200 | Meter Station | Bolsa | CNTL | L-301 A&G to L-103 | Bolsa Meter Station 089656 | Monitor | 7 | 350 | 350 | Hollister
57 | BHH2 | TP_CENTRAL_COAST | L301G_500 | L301G - 500 MOP is the main transmission line that feeds the Central Coast area. This line directly feeds Moss power plant units 1&2 and extra capacity for units 6&7. There is a back feed regulator set at the end of L301G at 260 PSIG to allow pressure t | C2-V3 | PCE206 | Meter Station | Hollister | CNTL | L-301G from L-300A | Hollister Meter Station 282255 | Monitor | 27 | 500 | 500 | Hollister
57 | BHH2 | TP_CENTRAL_COAST | L301G_500 | L301G - 500 MOP is the main transmission line that feeds the Central Coast area. This line directly feeds Moss power plant units 1&2 and extra capacity for units 6&7. There is a back feed regulator set at the end of L301G at 260 PSIG to allow pressure t | C2-V3 | PCE205 | Meter Station | Hollister | CNTL | L-301G from L-300A | Hollister Meter Station 282256 | Monitor | 26 | 500 | 500 | Hollister
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | C1-V1 | PCE430 | Primary Regulator Station | Moss Landing PP | SGO | Power Plant | Moss LandingPower Plant Primary Reg Sta 083811 | Monitor | 1 | 135 | 275 | Central Coast
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | C1-V1 | PCE431 | Primary Regulator Station | Moss Landing PP | SGO | Power Plant | Moss LandingPower Plant Primary Reg Sta 083811 | Monitor | 2 | 135 | 275 | Central Coast
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | C1-V1 | PCE432 | Primary Regulator Station | Moss Landing PP | SGO | Power Plant | Moss LandingPower Plant Primary Reg Sta 083811 | Monitor | 4 | 135 | 275 | Central Coast
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | C1-V1 | PCE433 | Primary Regulator Station | Moss Landing PP | SGO | Power Plant | Moss LandingPower Plant Primary Reg Sta 083811 | Monitor | 5 | 135 | 275 | Central Coast
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | C1-V1 | PCE434 | Primary Regulator Station | Moss Landing PP | SGO | Power Plant | Moss LandingPower Plant Primary Reg Sta 083811 | Monitor | M | 135 | 275 | Central Coast
59 | BHH2 | TP_CENTRAL_COAST | L103_L187_313 | L103-L187 Transmission main from California Reg Station (off L103) to Harkins Road (off L301C) to San Ardo. Primary feed used to be from L301C but had to be shifted to L103 due to the CROP | C2-V3 | PCE424 | Primary Regulator Station | Harkins Rd. | SGO | L-301C to L-187 | Dolan Road Meter Sta 083812, California Street Reg Station 089570 and Harkins Rd Regulator Sta 082856 | Monitor | 7 | 313 | 313 | Central Coast
59 | BHH2 | TP_CENTRAL_COAST | L103_L187_313 | L103-L187 Transmission main from California Reg Station (off L103) to Harkins Road (off L301C) to San Ardo. Primary feed used to be from L301C but had to be shifted to L103 due to the CROP | C2-V3 | PCE425 | Regulator Station | Harkins Rd. | SGO | L-301C to L-187 | Dolan Road Meter Sta 083812, California Street Reg Station 089570 and Harkins Rd Regulator Sta 082857 | Monitor | 6 | 313 | 313 | Central Coast
59 | BHH2 | TP_CENTRAL_COAST | L103_L187_313 | L103-L187 Transmission main from California Reg Station (off L103) to Harkins Road (off L301C) to San Ardo. Primary feed used to be from L301C but had to be shifted to L103 due to the CROP | C2-V3 | PCE423 | Regulator Station | California St. | SGO | L-103 to L-103 | Dolan Road Meter Sta 083812, California Street Reg Station 089570 and Harkins Rd Regulator Sta 082858 | Monitor | 2 | 313 | 313 | Central Coast
60 | BHH2 | TP_CENTRAL_COAST | MTY1_2_313 | 1813, 1815 Monterey - 313 MOP system. Two stations feed the Fort Ord, Monterey area. 1st & 8th and Davis - Reservation | C2-V1 | BHH2PCE804 | Regulator Station | Davis - Reservation Roads Reg Stat |  | Davis Reservation Reg Station - 089572 | 8th St and 1st Ave Regulator Station 087211 and Davis-Reservation Roads Regulator Station 089572
60 | BHH2 | TP_CENTRAL_COAST | MTY1_2_313 | 1813, 1815 Monterey - 313 MOP system. Two stations feed the Fort Ord, Monterey area. 1st & 8th and Davis - Reservation | C2-V1 | BHH2PCE803 | Regulator Station | 8th St and 1st Ave Reg Station |  | 8th street & 1st Ave - 08721 | 9th St and 1st Ave Regulator Station 087211 and Davis-Reservation Roads Regulator Station 089572
61 | BHH2 | TP_CENTRAL_COAST | L181A_DFM1_303 | 1816 - 303 PSIG system from San Jaun to Blain Street (inlet to Felton DFM) | C4-V3 | PCE438 | Regulator Station | San Juan Rd. | SGO | L-181A to L-181A | San Juan Road Reg Station 0800062, Front St Regulator Station 0800097, Watsonville Crosstie Reg Sta 0800407 and Rob Roy Junction Pressure Limiting Sta 087212 | Monitor | 17 | 242 | 303 | Central Coast
61 | BHH2 | TP_CENTRAL_COAST | L181A_DFM1_303 | 1816 - 303 PSIG system from San Jaun to Blain Street (inlet to Felton DFM) | C4-V3 | PCE436 | Pressure Limiting Station | Rob Roy Junction | SGO | DMF -2 to DFM -1 | San Juan Road Reg Station 0800062, Front St Regulator Station 0800097, Watsonville Crosstie Reg Sta 0800407 and Rob Roy Junction Pressure Limiting Sta 087213 | Rob Roy Junction Pressure Limiting Sta 087212 and the Santa Cruz Underground Holder 080393 | PCE435, PCE436 | Monitor | 15 | 303 | 303 | Central Coast
61 | BHH2 | TP_CENTRAL_COAST | L181A_DFM1_303 | 1816 - 303 PSIG system from San Jaun to Blain Street (inlet to Felton DFM) | C4-V3 | PCE435 | Pressure Limiting Station | Rob Roy Junction | SGO | DFM -2 to DFM -1 | San Juan Road Reg Station 0800062, Front St Regulator Station 0800097, Watsonville Crosstie Reg Sta 0800407 and Rob Roy Junction Pressure Limiting Sta 087214 | Cole Road Reg Sta 089666 and San Juan 0800062 | BHH2PCE808, BHH2PCE809 | Monitor | 14 | 303 | 303 | Central Coast
61 | BHH2 | TP_CENTRAL_COAST | L181A_DFM1_303 | 1816 - 303 PSIG system from San Jaun to Blain Street (inlet to Felton DFM) | C4-V3 | PCE437 | Regulator Station | San Juan Rd. | SGO | L-181A to L-181A | San Juan Road Reg Station 0800062, Front St Regulator Station 0800097, Watsonville Crosstie Reg Sta 0800407 and Rob Roy Junction Pressure Limiting Sta 087215 | Santa Cruz Underground Holder 080393 | PCE439, PCE440 | Monitor | 12 | 242 | 303 | Central Coast
62 | BHH2 | TP_CENTRAL_COAST | DFM1_2_3_303 | 1816 and 1818 DFM (Felton and Davenport DFM's, Santa Cruz holder). Systems past Rob Roy | C4-V1 | PCE436 | Pressure Limiting Station | Rob Roy Junction | SGO | DMF -2 to DFM -1 | Rob Roy Junction Pressure Limiting Sta 087212 and the Santa Cruz Underground Holder 080392 | Monitor | 15 | 303 | 303 | Central Coast
62 | BHH2 | TP_CENTRAL_COAST | DFM1_2_3_303 | 1816 and 1818 DFM (Felton and Davenport DFM's, Santa Cruz holder). Systems past Rob Roy | C4-V1 | PCE435 | Pressure Limiting Station | Rob Roy Junction | SGO | DFM -2 to DFM -1 | Rob Roy Junction Pressure Limiting Sta 087212 and the Santa Cruz Underground Holder 080392 | Monitor | 14 | 303 | 303 | Central Coast
63 | BHH2 | TP_CENTRAL_COAST | L181B_DFM2_400 | 1817 - 400 MOP system starting at Cole Road Regulator Station and endind at Rob Roy. Cole is the primary feed, and San Juan is the secondary feed | C4-V1 | BHH2PCE808 | Regulator Station | Cole Road Regulator Station |  | Cole Road Regulator Station - 089666 | Cole Road Reg Sta 089666 and San Juan 0800061
63 | BHH2 | TP_CENTRAL_COAST | L181B_DFM2_400 | 1817 - 400 MOP system starting at Cole Road Regulator Station and endind at Rob Roy. Cole is the primary feed, and San Juan is the secondary feed | C4-V1 | BHH2PCE809 | Regulator Station | San Juan Regulator Station |  | San Juan Regulator Station - 0800062 | Cole Road Reg Sta 089666 and San Juan 0800061
64 | BHH2 | TP_CENTRAL_COAST | SANTA_CRUZ_HOLDER | The underground holder is used during winter months to make up capacity to serve the Felton area. It is manually filled each time it is used during a cold event. There is no permanent connection to the transmission system that could over pressure it. | C4-V1 | PCE440 | Underground Holder | Santa Cruz | SGO | Holder Relief | Santa Cruz Underground Holder 080393 | Relief | C | 618 | 618 | Central Coast
64 | BHH2 | TP_CENTRAL_COAST | SANTA_CRUZ_HOLDER | The underground holder is used during winter months to make up capacity to serve the Felton area. It is manually filled each time it is used during a cold event. There is no permanent connection to the transmission system that could over pressure it. | C4-V1 | PCE439 | Underground Holder | Santa Cruz | SGO | Holder Relief | Santa Cruz Underground Holder 080393 | Relief | B | 618 | 618 | Central Coast
65 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Tap | L138A, L138B | C1-V1 | RLP7PCE811 | Regulator Station | Oper. Drw - 081818 |  | Helm tap L138 | Helm Tap Sta. Op Dia. 081818
66 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Fresno Belt Main | System d/s of Tarpey, Chestnut/Clay and FGLC | C4-V1 | RLP7PCE800 | Regulator Station | Oper. Drw - 080421 |  | Tarpey Reg Station | Tarpey Reg Sta. Op Dia. 080421
66 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Fresno Belt Main | System d/s of Tarpey, Chestnut/Clay and FGLC | C4-V1 | PCE449 | Gas Load Center | Fresno | SGO | Header to Belt Main | Oper. Drw - 382885 | Monitor | 19 | 163 | 163 | Fresno
66 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Fresno Belt Main | System d/s of Tarpey, Chestnut/Clay and FGLC | C4-V1 | PCE443 | Regulator Station | Chestnut & Clay | SGO | L-138 to Belt Main | Oper. Drw - 082423 | Monitor | 10 | 163 | 163 | Fresno
67 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L108 Tap | Vernalis Tap to Vernalis Field Valve Lot | C1-V1 | PCE154 | Meter Station | Vernalis | CNTL | L-108 | Oper. Drw - 089654 | Monitor | 6 | 720 | 720 | Tracy
68 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L108 Vernalis Valve Lot | Vernalis Field Valve Lot to Ripon Reg Station | C2-V1 | RLP7PCE809 | Regulator Station | Oper. Drw - 082994 |  | Vernalis Mixing Sta. L112 to L108 | Op Dia. 082994
69 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L215 | Oak Flat to West Ave Reg. | C1-V1 | RLP7PCE808 | Regulator Station | Oper. Drw - 082544 |  | Oak Flat Rd. Mt. Sta. L215 | Op Dia. 082544
70 | RLP7 | TP_SAN_JOAQUIN_VALLEY | 7224-19 | Stanislaus DFM | C4-V2B | RLP7PCE806 | Regulator Station | Oper. Drw - 0800480 |  | Oregan and Santa Anna | Op Dia. 0800480
71 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Oakdale | Oakdale, Escalon, Riverbank | C2-V1 | PCE465 | Regulator Station | Coffee and Claratina | SGO | 408 System to 180 System | Coffee & Claratina Reg Sta Op Dia. 082435 | Monitor | 26 | 180 | 180 | Yosemite
72 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Turlock-Modesto DFM | 260 psig system. Serves Modesto, Ceres, Turlock. | C2-V3 | PCE464 | Regulator Station | Coffee and Claratina | SGO | 408 System to 260 System | Coffee & Claratina Reg Sta Op Dia. 082435 | Monitor | 29 | 260 | 260 | Yosemite
72 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Turlock-Modesto DFM | 260 psig system. Serves Modesto, Ceres, Turlock. | C2-V3 | PCE463 | Regulator Station | Coffee and Claratina | SGO | 408 System to 260 System | Coffee & Claratina Reg Sta Op Dia. 082435 | Monitor | 28 | 260 | 260 | Yosemite
72 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Turlock-Modesto DFM | 260 psig system. Serves Modesto, Ceres, Turlock. | C2-V3 | RLP7PCE817 | Regulator Station | Oper. Drw - 082545 |  | West Ave. Reg. Sta | Op Dia. 082545
72 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Turlock-Modesto DFM | 260 psig system. Serves Modesto, Ceres, Turlock. | C2-V3 | RLP7PCE816 | Regulator Station | Oper. Drw - 0800499 |  | Morgan Ave. and Morgan Rd. | Op Dia. 0800499
73 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Modesto | 408 psig system. | C4-V1 | RLP7PCE802 | Regulator Station | Oper. Drw - 086444 |  | Ripon Modesto Mt. Sta. | Op Dia. 0800719
74 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118N | Bradbury to Merced (V-60.45) | C4-V1 | PCE450 | Junction | Fresno | SGO | L- 118 from L-111S | Oper. Drw - 081524 | Monitor | 4 | 400 | 400 | Fresno
74 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118N | Bradbury to Merced (V-60.45) | C4-V1 | RLP7PCE804 | Regulator Station | Oper. Drw - 081543 |  | Herndon Junction L134 to L118 | Op Dia. 081543
74 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118N | Bradbury to Merced (V-60.45) | C4-V1 | RLP7PCE803 | Regulator Station | Oper. Drw - 082548 |  | Bradbury Rd. Sta. L118 | Op Dia. 082548
75 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Eight Mile Road DFM | Eight Mile Road DFM fed from L108. | C1-V3 | RLP7PCE822 | Regulator Station | Oper. Drw - 0802402 |  | Eight Mile Rd. PLS L108 | Op Dia. 0802402
76 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L148 | McMullin Ranch to Morgan/Whitmore | C4-V1 | RLP7PCE801 | Regulator Station | Oper. Drw - 081792 |  | McMullin Sta.L108 to L148 | Op Dia. 081792
77 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Hammertown | Hammertown and Tom 'O' Shanter | C1-V3 | RLP7PCE823 | Regulator Station | Oper. Drw - 9892403 |  | West Lane and Hammertown Rd. L108 | Op Dia. 0802403
79 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Zephyr Road DFM | Fed from L108 1606 at Carpenter Rd | C1-V3 | RLP7PCE821 | Regulator Station | Oper. Drw - 089442 |  | Carpenter Rd. Sta. | Op Dia. 0800484
80 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Alpine DFM | 1621-01, DREG 4939. Fed from L108. | C4-V3 | RLP7PCE805 | Regulator Station | Oper. Drw - 0800489 |  | Stadium and San Rafael Reg. Sta. L108 | Op Dia. 0800489
81 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Manteca DFM | 1602-01. MP 0.7 - MP 2.66 | C3-V3 | RLP7PCE807 | Regulator Station | Oper. Drw - 081534 |  | Manteca Reg. Sta. | Op Dia. 081534
83 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Stockton L108 | Ripon-Modesto Meter Station to Eight Mile Road. | C4-V1 | RLP7PCE825 | Regulator Station | Oper. Drw - 086444 |  | Ripon Modesto Mt. Sta. L108 | Op Dia. 086444
84 | RLP7 | OTHER | Patterson DFM | Served from L-2. | C2-V3 | PCE149 | Station | Patterson | CNTL | Patterson from L-2 | Oper. Drw - 085517 | Monitor | 14 | 250 | 395 | Tracy
85 | RLP7 | OTHER | Los Banos DFM | Served from L-2. | C2-V1 | RLP7PCE810 | Regulator Station | Oper. Drw - 183301 |  | Los Banos Sta. L2 | Op Dia.183301
86 | RLP7 | OTHER | L-331 | Crosstied to L-2 and L-401 | C1-V1 | PCE104 | Station | Bayview Road | CNTL | L-331 from L-401 | Oper. Drw - 087998 | Monitor | 12 | 890 | 890 | Tracy | Removed
86 | RLP7 | OTHER | L-331 | Crosstied to L-2 and L-401 | C1-V1 | PCE105 | Station | Bayview Road | CNTL | L-331 from L-401 | Oper. Drw - 087999 | Monitor | 16 | 890 | 890 | Tracy | Removed
87 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Jct/Elkhorn | Downstream of Helm Jct and Elkhorn. 650 psig system. | C2-V1 | PCE446 | Station | Elkhorn | SGO | L- 138 | Oper. Drw - 085548 | Monitor | 3 | 650 | 650 | Fresno
87 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Jct/Elkhorn | Downstream of Helm Jct and Elkhorn. 650 psig system. | C2-V1 | PCE447 | Station | Elkhorn | SGO | L- 138 | Oper. Drw - 085549 | Monitor | 4 | 650 | 650 | Fresno
87 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Jct/Elkhorn | Downstream of Helm Jct and Elkhorn. 650 psig system. | C2-V1 | PCE451 | Meter & Regulator Station | Helm Junction | SGO | L-111 N from L-138A | Oper. Drw - 081541 | Monitor | 9 | 650 | 650 | Fresno
87 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Jct/Elkhorn | Downstream of Helm Jct and Elkhorn. 650 psig system. | C2-V1 | PCE452 | Meter & Regulator Station | Helm Junction | SGO | L-111 N from L-138A | Oper. Drw - 081541 | Monitor | 10 | 650 | 650 | Fresno
88 | RLP7 | TP_SAN_JOAQUIN_VALLEY | FGLC | FGLC to FJCT | C2-V1 | PCE448 | Gas Load Center | Fresno | SGO | L-138 to L-118 & L-111 | Oper. Drw - 382885 | Monitor | 107 | 400 | 400 | Fresno
88 | RLP7 | TP_SAN_JOAQUIN_VALLEY | FGLC | FGLC to FJCT | C2-V1 | PCE450 | Junction | Fresno | SGO | L- 118 from L-111S | Oper. Drw - 081542 | Monitor | 4 | 400 | 400 | Fresno
89 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118 | FJCT to V-60.45 (Merced). | C4-V2B | PCE450 | Junction | Fresno | SGO | L- 118 from L-111S | Oper. Drw - 0815402 | Monitor | 4 | 400 | 400 | Fresno
91 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Selma | 1209-02. Feed to Selma. | C2-V3 | RLP7PCE815 | Regulator Station | Oper. Drw - |  | Selma DFM Sta. off L138 Leonard N/O South DR J57 | Oper. Drw -
92 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L307/134 | Spreckels to Herndon Jct | C2-V1 | PCE235 | Meter Station | Spreckels Sugar | SGO | L-307 from L-2 | Oper. Drw - 085533 | Monitor | 13 | 500 | 500 | L300-N
92 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L307/134 | Spreckels to Herndon Jct | C2-V1 | PCE234 | Meter Station | Spreckels Sugar | SGO | L-307 from L-2 | Oper. Drw - 085533 | Monitor | 9 | 500 | 500 | L300-N
93 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Kerman | Kerman DFM serves Kerman and Biola | C2-V3 | RLP7PCE820 | Regulator Station | Oper. Drw - 0800141 |  | Kerman Reg. Sta L134 | Oper. Drw -
94 | RLP7 | TP_TRACY | Tracy | Serves City of Tracy. | C1-V1 | PCE152 | Station | Tracy | CNTL | L-162 from L-2 | Oper. Drw - 385181 | Monitor | 91 | 365 | 720 | Tracy
94 | RLP7 | TP_TRACY | Tracy | Serves City of Tracy. | C1-V1 | PCE138 | Station | MacArthur Road | CNTL | Tracy from L-2 | Oper. Drw - 081666 | Monitor | 11 | 365 | 365 | Tracy
95 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Baker Commodities | Transmission along Madera Ave that feeds Foster Farms and Baker Commodities. | C1-V2B | RLP7PCE819 | Regulator Station | Oper. Drw - |  | Baker Commodities Reg. Sta. L111A mp 8.83
96 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Herndon & Hayes | Fed from Cattern and Weber. | C1-V3 | RLP7PCE824 | Regulator Station | Oper. Drw - |  | Cattem and Weber DR 45 L118A mp 10.5
97 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Kamm Ave Feeder | Served from L111 and feed Con Agra Foods and Helm Sulfur. | C1-V2B | RLP7PCE818 | Regulator Station | Oper. Drw - |  | Kamm Ave. DFM Sta L111 Serving Brita Tomato DR K05
98 | RLP7 | OTHER | L-186 | Serves Dos Palos from L-2. | C2-V3 | RLP7PCE826 | Regulator Station | Oper. Drw - 085509 |  | Dos Palos Sta. L2 | Op Dia. 085509
99 | RLP7 | OTHER | Nees Ave DFM | Serves Olam West (DeFrancisco) from L-2. | C1-V2B | PCE467 | Regulator Station | De Francisco | SGO | De Francisco from L-2 | Oper. Drw - 089657 | Monitor | 3 | 620 | 620 | Yosemite
100 | RLP7 | OTHER | Newman-Gustine | Looped DFM to serve Newman and Gustine. | C2-V3 | PCE134 | Station | Gustine | CNTL | Gustine from L-2 | Oper. Drw - 085529 | Monitor | 11 | 150 | 150 | Tracy
100 | RLP7 | OTHER | Newman-Gustine | Looped DFM to serve Newman and Gustine. | C2-V3 | PCE142 | Station | Newman | CNTL | Newman from L-2 | Oper. Drw - 183202 | Monitor | 11 | 150 | 150 | Tracy
101 | c5s1 | TP_SAN_JOSE | L100 | L100 from Milpitas Terminal to PLS7 | C4-V1 | c5s1PCE800 | Terminal | Milpitas Terminal & L100, San Jose |  | Milpitas Terminal L100 Feed | Milpitas Terminal
102 | c5s1 | TP_SAN_JOSE | Dixon Landing DFM | DFM from L131 at Dixon Landing & 880 to Dixon Landing & Milpitas Blvd. | C2-V1 | c5s1PCE801 | Reg Station | Dixon Landing DFM & L131, San Jose |  | Dixon Landing Reg Station E-15 | Dixon Landing & Hwy 880 Regulator Station
103 | c5s1 | TP_SAN_JOSE | Barber DFM | DFM from Milpitas Terminal to Lundy & Murphy Station (F17) and Abbott-Milpitas Alvisio Road (E11). | C2-V3 | PCE180 | Terminal | Milpitas | CNTL | SJ DFM | Milpitas Terminal (SJDFM) | Monitor | 33 | 160 | 200 | Milpitas
104 | c5s1 | TP_SAN_JOSE | Mabury DFM | DFM from Mabury Station at Mabury Rd & Pine Hollow (F06) to Autumn & Julian Reg Station (F47). | C2-V1 | c5s1PCE802 | Reg Station | Mabury DFM & L100, San Jose |  | Mabury Reg Station F-06 | Mabury Road Regulator Station
105 | c5s1 | TP_SAN_JOSE | Tully DFM | DFM from Tully Station (F78) to Roberts & Fisher Station (D24). | C4-V1 | PCE460 | Station | Tully | SGO | Tully DFM from L-100 | Tully Regulator Station | Monitor | 4 | 200 | 200 | San Jose
106 | c5s1 | TP_SAN_JOSE | Fontanoso DFM | DFM from Fontanoso Reg Station (G77) to Cottle & Poughkeepsie Reg Station (G49). | C1-V1 | c5s1PCE803 | Reg Station | Fontanoso DFM & L300A, San Jose |  | Fontanoso Reg Station G-77 | Fontanoso Road Regulator Station
107 | c5s1 | TP_SAN_JOSE | Blossom Hill DFM | DFM from Cottle & Poughkeepsie Reg Station (G49) to endpoints of Cottle & Santa Teresa Reg Station (G73) and Rajkovich & Almaden Expressway Reg Station (G79). | C3-V1 | c5s1PCE804 | Reg Station | Blossom Hill DFM & Fontanoso DFM, San Jose |  | Cottle & Poughkeepsie Reg Station G-49 | Cottle & Poughkeepsie Road Regulator Station
108 | c5s1 | TP_GILROY | Emado DFM | DFM from Emado Reg Station (H15) to Emado & Hwy 101 Reg Station (H23). | C3-V3 | c5s1PCE805 | Reg Station | Emado DFM & L300A, San Jose |  | Emado Reg Station H-15 | Emado Ave Regulator Station
109 | c5s1 | TP_GILROY | Puppo DFM | DFM from Hwy 101 & Scheller Ave Reg Station (H18) to Monterey Hwy & Puppo R/W Reg Station (H16). | C1-V3 | c5s1PCE806 | Reg Station | Puppo DFM & L300A, San Jose |  | Hwy 101 & Scheller Reg Station H-18 | Hwy 101 and Scheller Ave Regulator Station
110 | c5s1 | TP_GILROY | Cochrane DFM | DFM from Peet & Cochrane Reg Station (H01) to N/S Cochrane, w/o Hwy 101 Reg Station (H03). | C2-V3 | c5s1PCE807 | Reg Station | Cochrane DFM & L300A, Morgan Hill |  | Peet & Cochrane Road Reg Station H-01 | Peet & Cochrane Regulator Station
111 | c5s1 | TP_GILROY | Diana DFM | DFM from Diana Reg Station(H06) east to Diana & L300A Reg Station (H05) and west to Diana e/o Railroad Reg Station (H09). | C2-V2B | c5s1PCE808 | Reg Station | Diana DFM & L300A, Morgan Hill |  | L300A & Diana Reg Station H-06 | Diana Ave Regulator Station
112 | c5s1 | TP_GILROY | Church DFM | DFM from Church Ave Reg Station (H46) to Church & Old 101 Hwy (H33). | C1-V1 | c5s1PCE809 | Reg Station | Church DFM & L300A, San Martin |  | Church Ave Reg Station H-46 | Church Ave Regulator Station
113 | c5s1 | TP_GILROY | Roop DFM | DFM from Roop Road Reg Station (H95) to Roop Road & New Reg Station (H96). | C3-V3 | c5s1PCE810 | Reg Station | Roop Road DFM & L300A, Gilroy |  | Roop Road Reg Station H-95 | Roop Road Regulator Station
114 | c5s1 | TP_GILROY | Bloomfield DFM | DFM from Bloomfield Reg Station (H73) to Kelton Dr & First Reg Station. DFM includes Calpine/Gilroy Power Plant. | C2-V1 | c5s1PCE811 | Reg Station | Bloomfield DFM & L300A, Gilroy |  | Bloomfield Reg Station H-73 | Bloomfield Regulator Station
115 | ZTR1 | TP_REDDING | L402_REDDING_600 | L402 from Redding/ Calaveras Tap (L400) to Lehigh Cement and associated DFM's | C2-V1 | PCE374 | Tap | Redding Calaveras | NGO | Calaveras Cement from L-400/401 | Redding Calaveras Tap OD083694 V-8, 9, 10, 11 | Monitor | 8 | 600 | 600 | North Valley
115 | ZTR1 | TP_REDDING | L402_REDDING_600 | L402 from Redding/ Calaveras Tap (L400) to Lehigh Cement and associated DFM's | C2-V1 | PCE375 | Tap | Redding Calaveras | NGO | Calaveras Cement from L-400/401 | Redding Calaveras Tap OD083694 V-8, 9, 10, 11 | Monitor | 10 | 600 | 600 | North Valley
115 | ZTR1 | TP_REDDING | L402_REDDING_600 | L402 from Redding/ Calaveras Tap (L400) to Lehigh Cement and associated DFM's | C2-V1 | PCE40 | Tap | Redding Calaveras | NGO | L-400 | Redding Calaveras Tap OD083694 V-8, 9, 10, 11 | Relief(QO) | H | 865 | 911 | Willows
116 | ZTR1 | TP_HUMBOLDT | 1309_ALTON_100 | 100 psig DFM served from L177A via the Alton Primary that serves Rio Dell and Scotia | C4-V1 | ZTR1PCE801 | Reg Station | Alton Primary, Humboldt County |  | NCR 67 | Alton Primary OD082931 V-14, 15, 16, 17
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE361 | Meter & Regulator Station | Tompkins Hill | NGO | L-177 from 4" & 6" L-125 | Gerber Compressor OD284543 V-21, 22 | Monitor | 71 | 350 | 425 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE357 | Meter & Regulator Station | Tompkins Hill | NGO | L-177(Ryan Slough) from L-177 (Cummings Crk) | Gerber Compressor OD284543 V-21, 22 | Monitor | 8 | 350 | 425 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE360 | Meter & Regulator Station | Tompkins Hill | NGO | L-177 from 4" & 6" L-125 | Gerber Compressor OD284543 V-21, 22 | Monitor | 70 | 350 | 425 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE348 | Pressure Limiting Station | Cummings Creek | NGO | L-177(Ryan Slough) from L-177 (Gerber) | Gerber Compressor OD284543 V-21, 22 | Monitor | 8 | 430 | 430 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE345 | Regulator Station | Arcata | NGO | L-137B to L-137D | Gerber Compressor OD284543 V-21, 22 | Monitor | 27 | 250 | 350 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE346 | Regulator Station | Arcata | NGO | L-137B to L-137D | Gerber Compressor OD284543 V-21, 22 | Monitor | 30 | 250 | 350 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE356 | Meter & Regulator Station | Tompkins Hill | NGO | L-177(Ryan Slough) from L-177 (Cummings Crk) | Gerber Compressor OD284543 V-21, 22 | Monitor | 7 | 350 | 425 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE347 | Pressure Limiting Station | Cummings Creek | NGO | L-177(Ryan Slough) from L-177 (Gerber) | Gerber Compressor OD284543 V-21, 22 | Monitor | 7 | 430 | 430 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE38 | Compressor Station | Gerber | NGO | L-177 from L-400/L-401 | Gerber Compressor OD284543 V-21, 22 | Monitor | 21 | 610 | 819 | Willows
118 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_430 | L177A Cummins Creek to Tompkins Hill | C4-V1 | PCE347 | Pressure Limiting Station | Cummings Creek | NGO | L-177(Ryan Slough) from L-177 (Gerber) | Gerber Compressor OD284543 V-21, 22 | Monitor | 7 | 430 | 430 | North Coast
118 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_430 | L177A Cummins Creek to Tompkins Hill | C4-V1 | PCE348 | Pressure Limiting Station | Cummings Creek | NGO | L-177(Ryan Slough) from L-177 (Gerber) | Gerber Compressor OD284543 V-21, 22 | Monitor | 8 | 430 | 430 | North Coast
119 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_350 | L177A from Tompkins Hill to Ryan Slough: L126A, L126B, L189, L137B | C4-V1 | PCE356 | Meter & Regulator Station | Tompkins Hill | NGO | L-177(Ryan Slough) from L-177 (Cummings Crk) | Gerber Compressor OD284543 V-21, 22 | Monitor | 7 | 350 | 425 | North Coast
119 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_350 | L177A from Tompkins Hill to Ryan Slough: L126A, L126B, L189, L137B | C4-V1 | PCE357 | Meter & Regulator Station | Tompkins Hill | NGO | L-177(Ryan Slough) from L-177 (Cummings Crk) | Gerber Compressor OD284543 V-21, 22 | Monitor | 8 | 350 | 425 | North Coast
119 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_350 | L177A from Tompkins Hill to Ryan Slough: L126A, L126B, L189, L137B | C4-V1 | PCE360 | Meter & Regulator Station | Tompkins Hill | NGO | L-177 from 4" & 6" L-125 | Gerber Compressor OD284543 V-21, 22 | Monitor | 70 | 350 | 425 | North Coast
119 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_350 | L177A from Tompkins Hill to Ryan Slough: L126A, L126B, L189, L137B | C4-V1 | PCE361 | Meter & Regulator Station | Tompkins Hill | NGO | L-177 from 4" & 6" L-125 | Gerber Compressor OD284543 V-21, 22 | Monitor | 71 | 350 | 425 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE362 | Station | Union Street (Eureka) | NGO | Dist. Regulator Station | Cummins Creek OD082474 V-2, 4, 7, 8 | Monitor | 25 | 50 | 50 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE349 | Regulator Station | Elk River Road | NGO | L-177 to L-126C | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 14 | 167 | 167 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE350 | Regulator Station | Elk River Road | NGO | L-177 to L-126C | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 15 | 167 | 167 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE351 | Regulator Station | Ryan Slough | NGO | L-177 to L-137A & L-137C | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 13 | 167 | 167 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE352 | Regulator Station | Ryan Slough | NGO | L-177 to L-137A & L-137C | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 15 | 167 | 167 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE363 | Station | Union Street (Eureka) | NGO | Lines 126 to Line 126 | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 24 | 167 | 167 | North Coast
123 | ZTR1 | TP_HUMBOLDT | L137D_GIUNTOLI_250 | 10" Line from Arcata Reg to Giuntoli | C2-V1 | PCE346 | Regulator Station | Arcata | NGO | L-137B to L-137D | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 30 | 250 | 350 | North Coast
123 | ZTR1 | TP_HUMBOLDT | L137D_GIUNTOLI_250 | 10" Line from Arcata Reg to Giuntoli | C2-V1 | PCE345 | Regulator Station | Arcata | NGO | L-137B to L-137D | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 27 | 250 | 350 | North Coast
124 | ZTR1 | TP_HUMBOLDT | 1310/1311_LOLETA_170 | 2 DFM's fed fro Tompkins Hill serving Loleta and Fernbridge | C2-V1 | PCE359 | Meter & Regulator Station | Tompkins Hill | NGO | Distribution Lines from Mixed Gas | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 62 | 170 | 170 | North Coast
124 | ZTR1 | TP_HUMBOLDT | 1310/1311_LOLETA_170 | 2 DFM's fed fro Tompkins Hill serving Loleta and Fernbridge | C2-V1 | PCE358 | Meter & Regulator Station | Tompkins Hill | NGO | Distribution Lines from Mixed Gas | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 61 | 170 | 170 | North Coast
126 | ZTR1 | TP_HUMBOLDT | 1001_REDBLUFF_470 | Rawson Road DFM serving Red Bluff West, Pactiv, and Neo Power | C2-V1 | ZTR1PCE800 | Reg Station | Rawson Road, Red Bluff |  | R102 | Tompkins Hill OD183697 V-50, 51, 66, 78
127 | ZTR1 | TP_CHICO | 1027_OROVILLE_110 | Oroville 110# DFM | C3-V1 | ZTR1PCE802 | Reg Station | Lincoln & Oro Dam |  | ORB-11 | Tompkins Hill OD183697 V-50, 51, 66, 78
127 | ZTR1 | TP_CHICO | 1027_OROVILLE_110 | Oroville 110# DFM | C3-V1 | ZTR1PCE803 | Reg Station | 5th & Pomona |  | ORB-51 | Arcata Reg OD082630 V-26, 27, 30, 31
128 | ZTR1 | TP_CHICO | 1027_OROVILLE_235 | Oroville 235# DFM | C4-V1 | PCE378 | Meter Station | Richvale "Y" | NGO | Oroville DFM from L-50 (N) | Arcata Reg OD082630 V-26, 27, 30, 31 | Monitor | 28 | 235 | 235 | North Valley
128 | ZTR1 | TP_CHICO | 1027_OROVILLE_235 | Oroville 235# DFM | C4-V1 | PCE377 | Meter Station | Richvale "Y" | NGO | Oroville DFM from L-50 (S) | Arcata Reg OD082630 V-26, 27, 30, 31 | Monitor | 24 | 235 | 235 | North Valley
129 | ZTR1 | TP_CHICO | 1004_ORLAND_490 | Orland 490# DFM from Primary to Secondary | C1-V1 | ZTR1PCE804 | Reg Station | Orland Primary at L177 (6th & Wyo) |  | R-001 | Arcata Reg OD082630 V-26, 27, 30, 31
130 | ZTR1 | TP_CHICO | 1004_ORLAND_170 | Orland 170# DFM from Secondary to Tertiary | C1-V1 | ZTR1PCE805 | Reg Station | Orland Secondary |  | R-002 | Tompkins Hill OD183697 V-60, 61, 62, 63
131 | ZTR1 | TP_CHICO | L209/128_WILLOWS_479 | Manville - Willows - Ordbend 479# Line | C1-V2B | PCE42 | Meter & Regulator Station | Johns Manville | NGO | L-209 from L-400 | Tompkins Hill OD183697 V-60, 61, 62, 63 | Monitor | 6 | 479 | 720 | Willows
131 | ZTR1 | TP_CHICO | L209/128_WILLOWS_479 | Manville - Willows - Ordbend 479# Line | C1-V2B | PCE41 | Meter & Regulator Station | Johns Manville | NGO | L-209 from L-400 | Tompkins Hill OD183697 V-60, 61, 62, 63 | Monitor | 3 | 479 | 720 | Willows
132 | ZTR1 | TP_CHICO | 1022_ARTOIS_200 | DFM serving Artois from Jacinto (L128) 200# | C1-V2B | PCE373 | Regulator Station | Jacinto | NGO | L-128 to Artois DFM | Tompkins Hill OD183697 V-60, 61, 62, 63 | Monitor | 29 | 200 | 200 | North Valley
132 | ZTR1 | TP_CHICO | 1022_ARTOIS_200 | DFM serving Artois from Jacinto (L128) 200# | C1-V2B | PCE372 | Regulator Station | Jacinto | NGO | L-128 to Artois DFM | Tompkins Hill OD183697 V-60, 61, 62, 63 | Monitor | 25 | 200 | 200 | North Valley
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE369 | Regulator Station | Grape Way | NGO | L-177 to L-177 | Tompkins Hill OD183697 V-60, 61, 62, 63 | Monitor | 9 | 469 | 469 | North Valley
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | ZTR1PCE808 | Reg Station | Butte Station, Chico |  | Butte 177 | Red Bluff & Diamond National Primary OD082621 V-4, 5, 6, 7
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE49 | Regulator & Odor Station | Fell | NGO | L-169 to L-136 | Red Bluff & Diamond National Primary OD082621 V-4, 5, 6, 8 | Monitor | 21 | 550 | 550 | Meridian
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | ZTR1PCE807 | Reg Station | Neal Road, Paradise |  | P-001
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE376 | Meter Station | Richvale "Y" | NGO | L-50 (S) from L-50 (N) | Richvaley Y OD081499 | Monitor | 38 | 250 | 250 | North Valley
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE368 | Regulator Station | Grape Way | NGO | Line 177 to Line 177 | Grape Way OD086447 V-4, 5, 8, 9 | Monitor | 4 | 469 | 469 | North Valley
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE50 | Regulator & Odor Station | Fell | NGO | L-169 to L-136 | Fell Reg & Oderizer OD082551 V-21, 22, 24, 25 | Monitor | 22 | 550 | 550 | Meridian
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE39 | Compressor Station | Gerber | NGO | L-177 from L-400/L-401 | Gerber Compressor OD284543 V-27, 28; Fell Reg & Oderizer OD082551 V-21, 22, 24, 25; Grape Way OD086447 V-4, 5, 8, 9; Butte Station OD284095 V-8, 9, 10, 11, 16, 17, 18, 19; Richvaley Y OD081499 V-28, 30, 32 | Monitor | 28 | 610 | 819 | Willows
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE378 | Meter Station | Richvale "Y" | NGO | Oroville DFM from L-50 (N) | Richvaley Y OD081499 | Monitor | 28 | 235 | 235 | North Valley
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE377 | Meter Station | Richvale "Y" | NGO | Oroville DFM from L-50 (S) | Richvaley Y OD081499 | Monitor | 24 | 235 | 235 | North Valley
135 | ZTR1 | TP_CHICO | L50_CHICO_400 | L50 from Butte Station to Richvale Y, including L50B to Paradise | C4-V1 | ZTR1PCE808 | Reg Station | Butte Station, Chico |  | Butte 177 | Butte Station OD 284095 V-8, 9, 10, 11
135 | ZTR1 | TP_CHICO | L50_CHICO_400 | L50 from Butte Station to Richvale Y, including L50B to Paradise | C4-V1 | ZTR1PCE807 | Reg Station | Neal Road, Paradise |  | P-001 | Butte Station OD 284095 V-8, 9, 10, 11
138 | ZTR1 | TP_CHICO | 1019_HAM-CITY_250 | DFM serving Prune Dryer south of Hamilton City | C2-V3 | ZTR1PCE813 | Reg Station | Hamilton City |  | R-004 | Hamilton City Regulator OD082877 V-56, 57, 60, 61
139 | ZTR1 | TP_REDDING | 1042_MCARTHUR_525 | DFM fed from L400, serving Fall River and McArthur | C1-V3 | ZTR1PCE814 | Reg Station | Red Mtn Rd Glenburn |  | R75 | Red Mt. Rd. Glenburn
140 | ZTR1 | TP_CHICO | 1009_MILLS-ORCHARD_200 | DFM fed from L177A MP9.88 to Mills Orchard and Sunsweet Dryers | C1-V3 | ZTR1PCE815 | Reg Station | Mills Orchard Primary |  | R-008 | Mills Orchard Primary OD0800189 V-2, 4, 5, 7
148 | HxFe | TP_KERN | HXFEPS704 | Pioneer_DFM | C1-V1 | HXFEPCE800 | DFM | Bakersfield |  | Bakersfield reg station feeding the Pioneer_DFM | Bakersfield Reg Sta
152 | TCQ2 | TP_EBAY | DFM_2404_85 | 85 psig DFM near Enterprise in Newark - Salt Dryers | C3-V3 | tcq2PCE801 | DFM | Timber and Central, Newark |  | Timber Reg Station; RF39 | Timber Reg Station; RF39
153 | TCQ2 | TP_EBAY | DFM_3010_100 | Wilbur DFM | C2-V3 | tcq2PCE814 | DFM | Wilbur Ave DFM RS |  | Wilbur Ave DFM RS | Wilbur Reg Station
154 | TCQ2 | TP_EBAY | SP3_System_600 | Stanpac 3 System from Antioch to Los Medanos | C2-V1 | PCE74 | Terminal | Antioch | CNTL | L-191 from L-400 | Antioch Terminal - Control Valves | Monitor | 93 | 600 | 600 | Los Medanos
154 | TCQ2 | TP_EBAY | SP3_System_600 | Stanpac 3 System from Antioch to Los Medanos | C2-V1 | PCE75 | Terminal | Antioch | CNTL | L-191 from L-400 | Antioch Terminal - Control Valves | Monitor | 95 | 600 | 600 | Los Medanos
154 | TCQ2 | TP_EBAY | SP3_System_600 | Stanpac 3 System from Antioch to Los Medanos | C2-V1 | PCE73 | Terminal | Antioch | CNTL | L-191 from L-400 | Antioch Terminal - Control Valves | Monitor | 92 | 600 | 600 | Los Medanos
155 | TCQ2 | TP_EBAY | Line_105_250 | 250 psig Line 105 from Irvington to Enrico Station | C2-V1 | PCE163 | Station | Irvington | CNTL | L- 105N from Mixer | Irvington Station | Monitor | 5 | 250 | 250 | Milpitas
156 | TCQ2 | TP_EBAY | Line_105B_397 | 397 psig Line 105B Herrmann to San Pablo | C2-V1 | PCE332 | Station | Herrmann | NGO | L-210 to 16" L-21 | Hermann Station - Control Valves | Monitor | 2 | 250 | 375 | North Bay
157 | TCQ2 | TP_EBAY | DFM 3004 | Port Costa Feeder from Stanpac 3 | C1-V2B | PCE324 | Regulator Station | Port Costa | NGO | Port Costa Mtr Sta from SP3 | Port Costa Reg Station | Monitor | 6 | 315 | 338 | East Bay-N
157 | TCQ2 | TP_EBAY | DFM 3004 | Port Costa Feeder from Stanpac 3 | C1-V2B | PCE323 | Regulator Station | Port Costa | NGO | Port Costa Mtr Sta from SP3 | Port Costa Reg Station | Monitor | 5 | 315 | 338 | East Bay-N
158 | TCQ2 | TP_EBAY | Line_105_150 | 150 psig Oakland System | C2-V1 | PCE325 | Station | San Pablo | NGO | L-105A from L-105B | Fairway Station, Enrico Station, East Bay PLS (All Control Valves) | Monitor | 64 | 150 | 198 | East Bay-N
158 | TCQ2 | TP_EBAY | Line_105_150 | 150 psig Oakland System | C2-V1 | PCE326 | Pressure Limiting Station | Oakland | NGO | L-153 to L-105 N | Fairway Station, Enrico Station, East Bay PLS (All Control Valves) | Monitor | 22 | 135 | 198 | East Bay-S
158 | TCQ2 | TP_EBAY | Line_105_150 | 150 psig Oakland System | C2-V1 | PCE327 | Station | Fairway Ave. Crossover | NGO | L-105N from L-153 | Fairway Station, Enrico Station, East Bay PLS (All Control Valves) | Monitor | 12 | 135 | 198 | Mission
158 | TCQ2 | TP_EBAY | Line_105_150 | 150 psig Oakland System | C2-V1 | tcq2PCE800 | LT | Grant Road, San Lorenzo |  | Enrico Station | Fairway Station, Enrico Station, East Bay PLS (All Control Valves)
159 | TCQ2 | TP_EBAY | DFM_0141-01_110 | C&H Sugar DFM | C1-V3 | PCE319 | Station | Crockett | NGO | C&H Sugar Tap From L-105B/21H | Crockett Station | Monitor | 3 | 110 | 110 | East Bay-N
159 | TCQ2 | TP_EBAY | DFM_0141-01_110 | C&H Sugar DFM | C1-V3 | PCE320 | Station | Crockett | NGO | C&H Sugar Tap From L-105B/21H | Crockett Station | Monitor | 4 | 110 | 110 | East Bay-N
160 | TCQ2 | TP_EBAY | Line_153_336 | 336 psig Line 153 from Irvington to Marina Station | C1-V1 | PCE166 | Station | Irvington | CNTL | Mixer from L- 107 | Irvington Station | Monitor | 66 | 476 | 477 | Milpitas
160 | TCQ2 | TP_EBAY | Line_153_336 | 336 psig Line 153 from Irvington to Marina Station | C1-V1 | PCE165 | Station | Irvington | CNTL | Mixer from L- 131 | Irvington Station | Monitor | 50 | 476 | 595 | Milpitas
160 | TCQ2 | TP_EBAY | Line_153_336 | 336 psig Line 153 from Irvington to Marina Station | C1-V1 | PCE163 | Station | Irvington | CNTL | L- 105N from Mixer | Irvington Station | Monitor | 5 | 250 | 250 | Milpitas
160 | TCQ2 | TP_EBAY | Line_153_336 | 336 psig Line 153 from Irvington to Marina Station | C1-V1 | PCE167 | Station | Irvington | CNTL | Mixer from L- 303 | Irvington Station | Monitor | 71 | 476 | 477 | Milpitas
161 | TCQ2 | TP_EBAY | Line_153_246 | 246 psig Line 153 from Marina Station to the Oakland PLS | C2-V1 | PCE328 | Station | Marina Blvd | NGO | L-153 Oakland from L-153 Irvington | Marina Station | Monitor | V18.00 | 246 | 246 | Mission
162 | TCQ2 | TP_EBAY | Line 191-1_268 | Line 191-1 from C Street to Plaza station (pipe continues to Reliez station) | C3-V1 | tcq2PCE806 | LT | C Street Station in Martinez off of SP3 |  | C Street Station | C Street Station, Martinez
163 | TCQ2 | TP_EBAY | DFM_2402_01 | 150 psig Castro Valley DFM | C3-V1 | tcq2PCE804 | DFM | A and Yolo Street, Diagram 0800545 |  | A Street Reg Station, RH-05 | C Street Station
164 | TCQ2 | TP_EBAY | DFM_2403_125 | 125 psig Niles DFM from Decoto to Mowry | C4-V1 | tcq2PCE802 | DFM | Decoto and Niles, Fremont |  | Niles Reg Station, RF38 | Niles Reg Station, RF38
165 | TCQ2 | TP_EBAY | DFM_3001-01_170 | Moraga DFM 3001-01 | C4-V1 | PCE315 | Regulator Station | Reliez Station Road | NGO | 16" L-191 to Moraga DFM/12" L-191 | Reliez Station | Monitor | 32 | 170 | 170 | Diablo/Con.
165 | TCQ2 | TP_EBAY | DFM_3001-01_170 | Moraga DFM 3001-01 | C4-V1 | PCE316 | Regulator Station | Reliez Station Road | NGO | 16" L-191 to Moraga DFM/12" L-191 | Reliez Station | Monitor | 33 | 170 | 170 | Diablo/Con.
166 | TCQ2 | TP_EBAY | DFM_3002_170 | Glorietta DFM | C4-V1 | PCE313 | Regulator Station | Reliez Station Road | NGO | 16" L-191 to 12" L-191 | Reliez Station | Monitor | 28 |  |  | Diablo/Con.
166 | TCQ2 | TP_EBAY | DFM_3002_170 | Glorietta DFM | C4-V1 | PCE314 | Regulator Station | Reliez Station Road | NGO | 16" L-191 to 12" L-192 | Reliez Station | Monitor | 29 |  |  | Diablo/Con.
167 | TCQ2 | TP_EBAY | DFM_3006/3008_170 | Concord DFM | C4-V1 | PCE310 | Meter Station | Concord | NGO | Concord from SP3 | Vine Hill Station, Concord Meter Station | Monitor | 9 | 170 | 170 | Diablo/Con.
167 | TCQ2 | TP_EBAY | DFM_3006/3008_170 | Concord DFM | C4-V1 | PCE309 | Meter Station | Concord | NGO | Concord from SP3 | Vine Hill Station, Concord Meter Station | Monitor | 8 | 170 | 170 | Diablo/Con.
167 | TCQ2 | TP_EBAY | DFM_3006/3008_170 | Concord DFM | C4-V1 | PCE317 | Meter Station | Vine Hill | NGO | Concord/PH from SP3 | Vine Hill Station, Concord Meter Station | Monitor | 10 | 170 | 170 | Diablo/Con.
167 | TCQ2 | TP_EBAY | DFM_3006/3008_170 | Concord DFM | C4-V1 | PCE318 | Meter Station | Vine Hill | NGO | Concord/PH from SP3 | Vine Hill Station, Concord Meter Station | Monitor | 11 | 170 | 170 | Diablo/Con.
168 | TCQ2 | TP_EBAY | DFM_3004-01_338 | Foster Wheeler Cogen DFM | C2-V2B | PCE312 | Meter & Regulator Station | Foster-Wheeler | NGO | FW Cogen from L-3 | Foster Wheeler Meter Station off of SP3 | Monitor | 6 | 320 | 600 | Diablo/Con.
168 | TCQ2 | TP_EBAY | DFM_3004-01_338 | Foster Wheeler Cogen DFM | C2-V2B | PCE311 | Meter & Regulator Station | Foster-Wheeler | NGO | FW Cogen from L-3 | Foster Wheeler Meter Station off of SP4 | Monitor | 5 | 320 | 600 | Diablo/Con.
169 | TCQ2 | TP_EBAY | DFM_3010-01_338 | Antioch Vierra DFM - Can be tied to Line 191_338 psig system | C2-V3 | tcq2PCE809 | DFM | Vierra Sation on Line 191 |  | Vierra Station | Antioch/Vierra Reg station
170 | TCQ2 | TP_EBAY | DFM_3012_172 | Dow Chemical and USS DFM | C2-V1 | tcq2PCE815 | DFM | Dow Chemical Feeder RA11 |  | Dow Chemical Feeder | Pittsburg Town Station
171 | TCQ2 | TP_EBAY | DFM_3014-01_338 | Nichols DFM Tapped off of SP3 | C1-V3 | tcq2PCE810 | DFM | Nichols DFM |  | Nichols DFM | Nichols Reg Station
172 | TCQ2 | TP_EBAY | DFM_3019_275 | Rhodia_DFM | C2-V3 | tcq2PCE816 | DFM | Smith Street at MP 8.48 on Line 153 |  | Rhodia DFM RS | Shell Reg Station DIRC29
173 | TCQ2 | TP_EBAY | Line SP3_405 | Stanpac 3 from Los Medanos PLS to Franklin Canyon PLS | C2-V1 | PCE90 | Pressure Limiting Station | Los Medanos | CNTL | SP3 | Los Medanos PLS - Control Valves | Monitor | 705 | 405 | 468 | Los Medanos
173 | TCQ2 | TP_EBAY | Line SP3_405 | Stanpac 3 from Los Medanos PLS to Franklin Canyon PLS | C2-V1 | PCE91 | Pressure Limiting Station | Los Medanos | CNTL | SP3 | Los Medanos PLS - Control Valves | Monitor | 706 | 405 | 468 | Los Medanos
174 | TCQ2 | TP_EBAY | Line SP3_380 | 380 psig Stanpac 3 from Franklin Canyon to San Pablo Station | C2-V1 | PCE322 | Station | Franklin Canyon | NGO | SP3 | Franklin Canyon PLS | Monitor | 10 | 380 | 380 | East Bay-N
174 | TCQ2 | TP_EBAY | Line SP3_380 | 380 psig Stanpac 3 from Franklin Canyon to San Pablo Station | C2-V1 | PCE321 | Station | Franklin Canyon | NGO | SP3 | Franklin Canyon PLS | Monitor | 8 | 380 | 380 | East Bay-N
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | C4-V1 | PCE94 | Meter Station | SP3-Line 191 | CNTL | SP-3 to L-191 | Antioch Terminal and SP3/191 Crosstie (control valves) | Monitor | 11 | 338 | 338 | Los Medanos
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | C4-V1 | PCE84 | Terminal | Antioch | CNTL | SP5 from Antioch Header | Antioch Terminal and SP3/191 Crosstie (control valves) | Monitor | 158 | 338 | 390 | Los Medanos
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | C4-V1 | PCE95 | Meter Station | SP3-Line 191 | CNTL | SP-3 to L-191 | Antioch Terminal and SP3/191 Crosstie (control valves) | Monitor | 12 | 338 | 338 | Los Medanos
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | C4-V1 | PCE96 | Meter Station | SP3-Line 191 | CNTL | SP-3 to L-191 | Antioch Terminal and SP3/191 Crosstie (control valves) | Monitor | 20 | 338 | 338 | Los Medanos
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | C4-V1 | PCE81 | Terminal | Antioch | CNTL | SP5 from Antioch Header | Antioch Terminal and SP3/191 Crosstie (control valves) | Monitor | 175 | 338 | 390 | Los Medanos
176 | TCQ2 | TP_EBAY | DFM_2408-01 | Stanley DFM in Pleasanton | C2-V1 | PCE330 | Meter & Regulator Station | Santa Rita Road | NGO | L-131 to Pleasanton DFM | Isabel Staiton/ Santa Rita Station | Monitor | 4 | 160 | 160 | Mission
176 | TCQ2 | TP_EBAY | DFM_2408-01 | Stanley DFM in Pleasanton | C2-V1 | PCE329 | Meter & Regulator Station | Santa Rita Road | NGO | L-131 to Pleasanton DFM | Bay Area Loop - Control Valves | Monitor | 3 | 160 | 160 | Mission
178 | TCQ2 | TP_EBAY | DFM_2805-05_215 | San Ramon DFM | C2-V1 | tcq2PCE808 | DFM | Isabel Station at Line 131 |  | Isabel Station | Altimrano/Arnold reg station
179 | TCQ2 | TP_EBAY | DFM_2403_240 | 240 psig Isabel DFM 2403-02 and 2403-01 | C1-V2B | tcq2PCE803 | DFM | Smith Street at MP 8.48 on Line 153 |  | Smith Reg Station, RF-41 | Smith Reg Station, RF-41
180 | TCQ2 | TP_EBAY | DFM 0107.02 | 160 psig Coral/Tunis DFM (near Oakland Airport) | C2-V2B | tcq2PCE805 | DFM | Coral and Tunis, San Leandro, Diagram 082483 |  | Coral and Tunis Reg Station EBA-09 | Coral and Tunis Regulator Station
181 | TCQ2 | TP_EBAY | DFM_CCPP | Contra Costa Power Plant DFM | C2-V3 | PCE82 | Terminal | Antioch | CNTL | CCPP from Antioch Header | Antioch Terminal valves 155, 156, 157, 173 | Monitor | 155 | 195 | 195 | Los Medanos
181 | TCQ2 | TP_EBAY | DFM_CCPP | Contra Costa Power Plant DFM | C2-V3 | PCE83 | Terminal | Antioch | CNTL | CCPP from Antioch Header | Antioch Terminal valves 155, 156, 157, 174 | Monitor | 156 | 195 | 195 | Los Medanos
182 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C2-V2B | DRJ4PCE820 | Underground Holder | Oper. Drw - 382860.g06 |  | North Sacramento | Franklin Canyon PLS
182 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C2-V2B | PCE404 | Regulator Station | Lincoln Junction | NGO | L-124 to L-123 | Franklin Canyon PLS | Monitor | 16 | 500 | 500 | Sierra
183 | MUMY | TP_SACRAMENTO_VALLEY | 0605_GALT_395 | Galt Primary Reg Sta (PCE) and Thornton Reg Sta (PCE) to the town of Galt at the inlet to DR R_SCSTA_B07. | C1-V1 | DRJ4PCE803 | Regulator Station | Oper. Drw - 0800439.G06 |  | Thornton | Antioch Terminal and SP3/191 Crosstie (control valves)
184 | MUMY | TP_SACRAMENTO_VALLEY | 0606_ELK_GROVE_150 | Elk Grove Emergency Backfeed Sta (PCE) to the inlet to DR R_SRSTA-B17. This looks to be a backup feed to distribution system, not LT | C2-V1 | DRJ4PCE804 | Regulator Station | Oper. Drw - 089653.g06 |  | Elk Grove - Clarksburg | Antioch Terminal and SP3/191 Crosstie (control valves)
185 | MUMY | TP_SACRAMENTO_VALLEY | 0609_FLORIN_150 | Florin Rd & Munson Way Reg Sta (PCE) to DFM 0609. | C4-V1 | DRJ4PCE808 | Regulator Station | Oper. Drw - 0800152.g06 |  | Florin Rd & Munson Way | Isabel Staiton/ Santa Rita Station
186 | MUMY | TP_SACRAMENTO_VALLEY | 0611_MATHER_240 | 20th Av & Martin Luther King Jr Blvd Reg Sta (PCE) to Blue Ravine Reg Station in Folsom - Mather DFM system serving south Sacramento and Rancho Cordova. The Pmin Design Shown is in Folsom at DR R_SCSTA-51 which receives backfeed support from the Folsom D | C2-V1 | DRJ4PCE809 | Meter & Regulator Station | Oper. Drw - 0800151.g06 |  | 20th Ave & Martin Luther King Jr Blvd | Isabel Staiton/ Santa Rita Station
187 | MUMY | TP_SACRAMENTO_VALLEY | 0613_SAC_FLOATER_260 | Sacramento Gas Load Center (PCE) to North Sacramento Holder and North Sacramento 180 psig DFM. Provides the lead supply to the DFM to a secondary backup supply off of L119B/C. The North Sacramento Holder is operated during winter season morning peak hou | C4-V3 | PCE393 | Gas Load Center | Sacramento | NGO | L-116 to North Sac. DFM | Isabel Staiton/ Santa Rita Station | Monitor | 16 | 260 | 260 | Sacramento
187 | MUMY | TP_SACRAMENTO_VALLEY | 0613_SAC_FLOATER_260 | Sacramento Gas Load Center (PCE) to North Sacramento Holder and North Sacramento 180 psig DFM. Provides the lead supply to the DFM to a secondary backup supply off of L119B/C. The North Sacramento Holder is operated during winter season morning peak hou | C4-V3 | PCE394 | Gas Load Center | Sacramento | NGO | L-116 to North Sac. DFM | Isabel Staiton/ Santa Rita Station | Monitor | 20 | 260 | 260 | Sacramento
188 | MUMY | TP_SACRAMENTO_VALLEY | 0615_SAC_METRO_425 | El Centro Rd & Hwy 80 Reg Sta (PCE) to the Sacramento Metropolitan Airport. | C1-V1 | DRJ4PCE801 | Regulator Station | Oper. Drw - 0800492.g06 |  | El Centro Rd & Hwy 80 | Isabel Staiton/ Santa Rita Station
189 | MUMY | TP_SACRAMENTO_VALLEY | 0617_KIRBY_150 | Roseville Rd Reg Sta (PCE) to the inlet to DR R_SCSTA-A37. | C4-V3 | PCE389 | Regulator Station | Roseville Road | NGO | 12" L-119 to Sacto DFM | Bay Area Loop - Control Valves | Monitor | 66 | 150 | 150 | Sacramento
190 | MUMY | TP_SACRAMENTO_VALLEY | 0618_ANTELOPE_WALERGA_175 | Antelope Meter Sta (PCE) to Antelope at the inlet to DR . | C4-V3 | PCE381 | Meter Station | Antelope | NGO | L-123 to Roseville DFM | Bay Area Loop - Control Valves | Monitor | 25 | 180 | 180 | Sacramento
190 | MUMY | TP_SACRAMENTO_VALLEY | 0618_ANTELOPE_WALERGA_175 | Antelope Meter Sta (PCE) to Antelope at the inlet to DR . | C4-V3 | PCE382 | Meter Station | Antelope | NGO | L-123 to Roseville DFM | Smith Reg Station, RF-41 | Monitor | 27 | 180 | 180 | Sacramento
191 | ANY3 | TP_SACRAMENTO_VALLEY | 0619_SOUTH_RIVER_150 | 0619-01: 150# (South River) Included in distribution model: ESDZONE_SA_WEST_SAC_H_W1112_APD_452_(MOP_MINUS_20_STUDY) | C2-V3 | DRJ4PCE810 | Regulator Station | Oper. Drw - 0800230.g06 |  | S River Rd | Coral and Tunis Regulator Station
192 | ANY3 | TP_SACRAMENTO_VALLEY | 0621_ARMFIELD_190 | 0621-01: 190# (Teichert Modeled) Included in distribution model: ESDZONE_SA_WOODLAND_HL_W1112_CFD_452_(w_Teichert)_(MOP_MINUS_20_STUDY) | C2-V3 | DRJ4PCE811 | Regulator Station | Oper. Drw - 081798.g06 |  | Woodland | Antioch Terminal valves 155, 156, 157, 173
193 | ANY3 | TP_SACRAMENTO_VALLEY | 0627_UCDAVIS_175 | 0627-01: 175# Davis Meter and Reg Sta (PCE) to UC Davis Campus at the inlet to DR R_SCDA-001. (AFTER 1st & A St MWC 47 job) Included in distribution model: ESDZONE_SA_DAVIS_H_W1112_CWD_452_(MOP_MINUS_20_STUDY)_1st_&_A_St_Upgrade) | C2-V3 | PCE384 | Meter & Regulator Station | Davis | NGO | L-116 to Davis DFM |  | Monitor | 89 | 175 | 175 | Sacramento
193 | ANY3 | TP_SACRAMENTO_VALLEY | 0627_UCDAVIS_175 | 0627-01: 175# Davis Meter and Reg Sta (PCE) to UC Davis Campus at the inlet to DR R_SCDA-001. (AFTER 1st & A St MWC 47 job) Included in distribution model: ESDZONE_SA_DAVIS_H_W1112_CWD_452_(MOP_MINUS_20_STUDY)_1st_&_A_St_Upgrade) | C2-V3 | PCE385 | Meter & Regulator Station | Davis | NGO | L-116 to Davis DFM |  | Monitor | 90 | 175 | 175 | Sacramento
194 | LRS3 | TP_SACRAMENTO_VALLEY | 0630_COLUSA_MERIDIAN_240 | Lurline Rd Sta (PCE) to closed MAOP sdeparation valve V-5. Serves the town of Colusa and Sunsweet Driers. The Pmin Design shown is in Colusa at the inlet to DR R_SCC008 (55 psig Distr system). Lurline DFM Included in distribution model: 07-J07colusaAS | C2-V2B | DRJ4PCE812 | Regulator Station | Oper. Drw - 0800125.g06 |  | Lurline Road
195 | LRS3 | TP_SACRAMENTO_VALLEY | 0630_COLUSA_MERIDIAN_430 | Marysville Buttes Sta (PCE) to closed MAOP separation valve V-5. Colusa DFM Included in distribution model: 07-J07colusaASD_UTM_Qrc+20%+Noncore_452_MOP_MINUS_20_STUDY.MDB | C2-V2B | DRJ4PCE813 | Regulator Station | Oper. Drw - 081498.g06 |  | Marysville-Buttes
196 | LRS3 | TP_SACRAMENTO_VALLEY | 0632_WILLIAMS_180 | Williams Primary (PCE) to the town of Williams DR R_FM_SCWL04. Williams DFM Included in distribution model: 11-J11WILLIAMSCFD_UTM_45_MOP_MINUS_20_STUDY | C4-V3 | DRJ4PCE815 | Regulator Station | Oper. Drw - 082870.g06 |  | Williams Town
197 | MUMY | TP_SACRAMENTO_VALLEY | 0635_WALNUT_GROWER_210 | West Beehive Bend Reg Sta (PCE) | V3 | DRJ4PCE824 | Meter & Odorizer Station | Oper. Drw - 183096.g06 |  | West Beehive Bend(DREG)
198 | LRS3 | TP_SACRAMENTO_VALLEY | 124C-1_BEALE_AFB_395 | Camp Far West Meter Sta (PCE) to Beale Air Force Base. Beale DFM Included in distribution model: ESDZONE_08-J08wheatbelAPD_UTM_45_MOP_MINUS_20_STUDY | C1-V3 | PCE403 | Meter Station | Camp Far West | NGO | L-124 to l-124 |  | Monitor | 11 | 395 | 400 | Sierra
198 | LRS3 | TP_SACRAMENTO_VALLEY | 124C-1_BEALE_AFB_395 | Camp Far West Meter Sta (PCE) to Beale Air Force Base. Beale DFM Included in distribution model: ESDZONE_08-J08wheatbelAPD_UTM_45_MOP_MINUS_20_STUDY | C1-V3 | PCE402 | Meter Station | Camp Far West | NGO | L-124 to l-124 |  | Monitor | 7 | 395 | 400 | Sierra
199 | LRS3 | TP_SACRAMENTO_VALLEY | 1502_DIST10_120 | Magnolia Rd Sta (PCE) to DFM 1502. District 10 DFM north of Magnolia Rd Reg Station Included in distribution model: 10-J10mryASD_UTM_45_MOP_MINUS_20_STUDY | C4-V2B | DRJ4PCE817 | Regulator Station | Oper. Drw - 0800099.g06 |  | Hwy 70 & Magnolia Rd
200 | LRS3 | TP_SACRAMENTO_VALLEY | 1504_NICOLAUS_274 | Lincoln Jct (PCE) to the town of Lincoln DR R_SRSTA-602 and R_SRSTA-603. Lincoln DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C1-V1 | PCE406 | Regulator Station | Lincoln Junction | NGO | L-124 to Lincoln DFM |  | Monitor | 22 | 274 | 274 | Sierra
200 | LRS3 | TP_SACRAMENTO_VALLEY | 1504_NICOLAUS_274 | Lincoln Jct (PCE) to the town of Lincoln DR R_SRSTA-602 and R_SRSTA-603. Lincoln DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C1-V1 | PCE405 | Regulator Station | Lincoln Junction | NGO | L-124 to Lincoln DFM |  | Monitor | 21 | 274 | 274 | Sierra
201 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L124B_1502_400 | Yuba City Holder (PCE) to Lincoln Jct - 400 psig system serving Marysville and subsystem 1504_NICOLAUS_274. The Pmin Design shown is in Lincoln at the inlet to Lincoln Jct. | C4-V1 | DRJ4PCE806 | Underground Holder | Oper. Drw - 284091.g06 |  | Yuba City
202 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L151_250 | Gridley Jct (PCE) to Richvale Y and Yuba City Holder (PCE). Yuba City Holder is normally set as a secondary supply and not flowing into L050A. A CROP in place on L151, which is part of the subsystem, requires operating the subsystem in two HIS - Gridley | C1-V1 | PCE370 | Station | Gridley Junction | NGO | L-167 to L-50 |  | Monitor | 13 | 250 | 250 | North Valley
202 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L151_250 | Gridley Jct (PCE) to Richvale Y and Yuba City Holder (PCE). Yuba City Holder is normally set as a secondary supply and not flowing into L050A. A CROP in place on L151, which is part of the subsystem, requires operating the subsystem in two HIS - Gridley | C1-V1 | PCE371 | Station | Gridley Junction | NGO | L-167 to L-50 |  | Monitor | 17 | 250 | 250 | North Valley
202 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L151_250 | Gridley Jct (PCE) to Richvale Y and Yuba City Holder (PCE). Yuba City Holder is normally set as a secondary supply and not flowing into L050A. A CROP in place on L151, which is part of the subsystem, requires operating the subsystem in two HIS - Gridley | C1-V1 | PCE376 | Meter Station | Richvale "Y" | NGO | L-50 (S) from L-50 (N) |  | Monitor | 38 | 250 | 250 | North Valley
203 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVN_412 | Las Vinas Sta (PCE) to BTU MLV 66.14. Serves South Sacramento. The Pmin Design shown is in South Sacramento at the inlet to DR R_SCSTA-B39 and DR R_SCSTA-B37. | C2-V1 | PCE61 | Station | Las Vinas | NGO | L-108S from L-196A/B |  | Monitor | 75 | 400 | 412 | Rio Vista
203 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVN_412 | Las Vinas Sta (PCE) to BTU MLV 66.14. Serves South Sacramento. The Pmin Design shown is in South Sacramento at the inlet to DR R_SCSTA-B39 and DR R_SCSTA-B37. | C2-V1 | PCE62 | Station | Las Vinas | NGO | L-108S from L-196A/B |  | Monitor | 76 | 400 | 412 | Rio Vista
204 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVS_412 | Las Vinas Sta (PCE) to 8-mile Rd PLS (PCE). Supplies Turner Rd Sta and NCPA-Lodi. The Pmin Design shown is at Armstrong Rd at the inlet to DR R_LOHP77. | C2-V1 | PCE61 | Station | Las Vinas | NGO | L-108S from L-196A/B |  | Monitor | 75 | 400 | 412 | Rio Vista
204 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVS_412 | Las Vinas Sta (PCE) to 8-mile Rd PLS (PCE). Supplies Turner Rd Sta and NCPA-Lodi. The Pmin Design shown is at Armstrong Rd at the inlet to DR R_LOHP77. | C2-V1 | PCE62 | Station | Las Vinas | NGO | L-108S from L-196A/B |  | Monitor | 76 | 400 | 412 | Rio Vista
205 | MUMY | TP_SACRAMENTO_VALLEY | L108_SGLC_412 | Sacramento Gas Load Center (PCE) to closed BTU Separation valve V-66.14. Supplies South Sacramento area and subsystem 0611_MATHER_240. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609- | C1-V1 | PCE397 | Gas Load Center | Sacramento | NGO | L-172 to L-108 |  | Monitor | 7 | 412 | 412 | Sacramento
205 | MUMY | TP_SACRAMENTO_VALLEY | L108_SGLC_412 | Sacramento Gas Load Center (PCE) to closed BTU Separation valve V-66.14. Supplies South Sacramento area and subsystem 0611_MATHER_240. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609- | C1-V1 | PCE395 | Gas Load Center | Sacramento | NGO | L-172 to L-108 |  | Monitor | 3 | 412 | 412 | Sacramento
205 | MUMY | TP_SACRAMENTO_VALLEY | L108_SGLC_412 | Sacramento Gas Load Center (PCE) to closed BTU Separation valve V-66.14. Supplies South Sacramento area and subsystem 0611_MATHER_240. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609- | C1-V1 | PCE396 | Gas Load Center | Sacramento | NGO | L-172 to L-108 |  | Monitor | 5 | 412 | 412 | Sacramento
206 | MUMY | TP_SACRAMENTO_VALLEY | L116_L119A_720 | Swingel Jct (PCE) to Sacramento Gas Load Center and North Sacramento Holder. Supplies North Natomas area, North Sacramento and subsystems L119B_L119C_0617_FOLSOM_500, 0613_SAC_FLOATER_260, L119D_0614_NSAC_180, and 0615_SAC_METRO_425. The Pmin Design show | C1-V1 | PCE398 | Meter & Regulator Station | Swingle Junction | NGO | L-172 to L-116/119 |  | Monitor | 21 | 533 | 720 | Sacramento
206 | MUMY | TP_SACRAMENTO_VALLEY | L116_L119A_720 | Swingel Jct (PCE) to Sacramento Gas Load Center and North Sacramento Holder. Supplies North Natomas area, North Sacramento and subsystems L119B_L119C_0617_FOLSOM_500, 0613_SAC_FLOATER_260, L119D_0614_NSAC_180, and 0615_SAC_METRO_425. The Pmin Design show | C1-V1 | PCE399 | Meter & Regulator Station | Swingle Junction | NGO | L-172 to L-116/119 |  | Monitor | 29 | 533 | 720 | Sacramento
207 | BHH2 | TP_SACRAMENTO_VALLEY | L119D_0614_NSAC_180 | North Sacramento Holder Sta (PCE) to DFM 0614. The North Sacramento Underground Holder storage is manually operated during winter season mornning hours to take over supplying the DFM at 180 psig. | C4-V3 | PCE409 | Underground Holder | North Sacramento | NGO | Sacto Load Center to Sacto DFM |  | Monitor | 167 | 180 | 180 | Sierra
207 | BHH2 | TP_SACRAMENTO_VALLEY | L119D_0614_NSAC_180 | North Sacramento Holder Sta (PCE) to DFM 0614. The North Sacramento Underground Holder storage is manually operated during winter season mornning hours to take over supplying the DFM at 180 psig. | C4-V3 | PCE408 | Underground Holder | North Sacramento | NGO | Sacto Load Center to Sacto DFM |  | Monitor | 137 | 180 | 180 | Sierra
207 | BHH2 | TP_SACRAMENTO_VALLEY | L119D_0614_NSAC_180 | North Sacramento Holder Sta (PCE) to DFM 0614. The North Sacramento Underground Holder storage is manually operated during winter season mornning hours to take over supplying the DFM at 180 psig. | C4-V3 | PCE407 | Underground Holder | North Sacramento | NGO | Sacto Load Center to Sacto DFM |  | Monitor | 93 | 180 | 180 | Sierra
208 | MUMY | TP_SACRAMENTO_VALLEY | L121_485 | Marysville Buttes Sta (PCE) to Yuba City Holder Sta (PCE). Yuba City Holder Sta provides backup supply into L121 at 420 psig when the Yuba City Cogen comes on-line to maintain an elevated delivery service pressure of 375 psig at the meter. | C2-V3 | DRJ4PCE814 | Meter & Regulator Station | Oper. Drw - 081498.g06 |  | Marysville-Buttes
209 | MUMY | TP_SACRAMENTO_VALLEY | L123_L173_500, L119B_L119C_0617_FOLSOM_500 | Lincoln Junction (PCE) to North Sacramento Underground Holder (PCE) 500 psig system serving Auburn and El Dorado Hills. These two subsystems have the same MAOP and operate as a single system under Design Day conditions across L123 Open BTU MLV 3.42 at Ba | C4-V1 | DRJ4PCE820 | Underground Holder | Oper. Drw - 382860.g06 |  | North Sacramento
209 | MUMY | TP_SACRAMENTO_VALLEY | L123_L173_500, L119B_L119C_0617_FOLSOM_500 | Lincoln Junction (PCE) to North Sacramento Underground Holder (PCE) 500 psig system serving Auburn and El Dorado Hills. These two subsystems have the same MAOP and operate as a single system under Design Day conditions across L123 Open BTU MLV 3.42 at Ba | C4-V1 | PCE404 | Regulator Station | Lincoln Junction | NGO | L-124 to L-123 |  | Monitor | 16 | 500 | 500 | Sierra
210 | MUMY | TP_SACRAMENTO_VALLEY | L124A_L202_1511_600 | Yuba City Holder (PCE) to Lincoln Jct - 600 psig system serving Grass Valley and subsystem L123_L173_500. The Pmin design shown is in Grass Valley at DR R_SRSTA-112. | C4-V1 | PCE413 | Underground Holder | Yuba City | NGO | L-167 to L-124 |  | Monitor | 53 | 600 | 600 | Sierra
211 | MUMY | TP_SACRAMENTO_VALLEY | L150_0626_0600_125 | Pleasant Creek Line 159 Reg Sta (PCE) to Davis at the inlet to DR R_SCSTA-D13. | C4-V3 | PCE379 | Regulator Station | Pleasant Creek Line 159 | NGO | L-159 to L-159 |  | Monitor | 5 | 125 | 750 | Sacramento
211 | MUMY | TP_SACRAMENTO_VALLEY | L150_0626_0600_125 | Pleasant Creek Line 159 Reg Sta (PCE) to Davis at the inlet to DR R_SCSTA-D13. | C4-V3 | PCE380 | Regulator Station | Pleasant Creek Line 159 | NGO | L-159 to L-160 |  | Monitor | 9 | 125 | 750 | Sacramento
212 | MUMY | TP_SACRAMENTO_VALLEY | L172A_500 | Swingle Jct (PCE) to Sacramento Gas Load Center. Supplies West Sacramento and subsystem L108_SGLC_412. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609-02. | C2-V1 | PCE401 | Meter & Regulator Station | Swingle Junction | NGO | L-172 to L-116/172 |  | Monitor | 53 | 500 | 520 | Sacramento
212 | MUMY | TP_SACRAMENTO_VALLEY | L172A_500 | Swingle Jct (PCE) to Sacramento Gas Load Center. Supplies West Sacramento and subsystem L108_SGLC_412. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609-02. | C2-V1 | PCE400 | Meter & Regulator Station | Swingle Junction | NGO | L-172 to L-116/172 |  | Monitor | 52 | 500 | 520 | Sacramento
213 | MUMY | TP_SACRAMENTO_VALLEY | L172A_N_L169_L167_800 | Hershey Jct North (PCE) to Fell Station and Yuba City Holder. Receives withdrawal gas from Wild Goose Storage Field (PCE) and local California Production in the Willows Field area. The Pmin Design shown is in Grass Valley at the inlet to DR R_SRSTA-112 | C4-V1 | PCE51 | Junction | Hershey | NGO | L-172 from L-302 |  | Monitor | 2 | 800 | 800 | Willows
213 | MUMY | TP_SACRAMENTO_VALLEY | L172A_N_L169_L167_800 | Hershey Jct North (PCE) to Fell Station and Yuba City Holder. Receives withdrawal gas from Wild Goose Storage Field (PCE) and local California Production in the Willows Field area. The Pmin Design shown is in Grass Valley at the inlet to DR R_SRSTA-112 | C4-V1 | PCE54 | Storage Interconnect | Wild Goose Gridley | NGO | Storage metering run |  | Monitor | 6 | 800 | 800 | Willows
214 | MUMY | TP_SACRAMENTO_VALLEY | L172A_S_800 | Hershey Jct (PCE) and Yolo Jct (PCE) to L172-220 Xtie and Swingle Jct. The Pmin Design shown is in Davis at the inlet to Swingle Jct. | C4-V1 | PCE52 | Junction | Hershey | NGO | L-172 from L-302 |  | Monitor | 3 | 800 | 800 | Willows
214 | MUMY | TP_SACRAMENTO_VALLEY | L172A_S_800 | Hershey Jct (PCE) and Yolo Jct (PCE) to L172-220 Xtie and Swingle Jct. The Pmin Design shown is in Davis at the inlet to Swingle Jct. | C4-V1 | PCE44 | Pressure Limiting Station | Yolo Station | NGO | L-172 from L-406 |  | Monitor | 5 | 800 | 800 | Willows
214 | MUMY | TP_SACRAMENTO_VALLEY | L172A_S_800 | Hershey Jct (PCE) and Yolo Jct (PCE) to L172-220 Xtie and Swingle Jct. The Pmin Design shown is in Davis at the inlet to Swingle Jct. | C4-V1 | PCE45 | Pressure Limiting Station | Yolo Station | NGO | L-172 from L-406 |  | Monitor | 11 | 800 | 800 | Willows
214 | MUMY | TP_SACRAMENTO_VALLEY | L172A_S_800 | Hershey Jct (PCE) and Yolo Jct (PCE) to L172-220 Xtie and Swingle Jct. The Pmin Design shown is in Davis at the inlet to Swingle Jct. | C4-V1 | PCE43 | Pressure Limiting Station | Yolo Station | NGO | L-172 from L-406 |  | Monitor | 2 | 800 | 800 | Willows
215 | MUMY | TP_SACRAMENTO_VALLEY | L195_L196_L200_L210B_800 | Creed Sta (PCE) to Las Vinas Sta. The Pmin Design shown is in South Sacramento at the inlet to DR R_SCSTA-B37 and DR R_SCSTA-B05. | C2-V1 | PCE56 | Station | Creed | NGO | L-210 E from L400/L401 |  | Monitor | 11 | 686 | 800 | Rio Vista
216 | MUMY | TP_SACRAMENTO_VALLEY | L197_1614_TURNER_300 | Las Vinas Sta (PCE) and Turner Rd Sta (PCE) to Lodi, Ione and Valley Springs. The Pmin Design shown is in Ione at the inlet to DR R_LOHP24 and in Sutter at the inlet to DR MARHP-01. General Mills has a Pmin requirement for an elevated delivery service pr | C2-V2A | PCE61 | Station | Las Vinas | NGO | L-108S from L-196A/B |  | Monitor | 75 | 400 | 412 | Rio Vista
216 | MUMY | TP_SACRAMENTO_VALLEY | L197_1614_TURNER_300 | Las Vinas Sta (PCE) and Turner Rd Sta (PCE) to Lodi, Ione and Valley Springs. The Pmin Design shown is in Ione at the inlet to DR R_LOHP24 and in Sutter at the inlet to DR MARHP-01. General Mills has a Pmin requirement for an elevated delivery service pr | C2-V2A | PCE64 | Station | Las Vinas | NGO | L-197A/B from L-108S |  | Monitor | 96 | 300 | 300 | Rio Vista
216 | MUMY | TP_SACRAMENTO_VALLEY | L197_1614_TURNER_300 | Las Vinas Sta (PCE) and Turner Rd Sta (PCE) to Lodi, Ione and Valley Springs. The Pmin Design shown is in Ione at the inlet to DR R_LOHP24 and in Sutter at the inlet to DR MARHP-01. General Mills has a Pmin requirement for an elevated delivery service pr | C2-V2A | DRJ4PCE800 | Regulator Station | Oper. Drw - 081929.g06 |  | Turner Rd
217 | MUMY | TP_SACRAMENTO_VALLEY | L220_500 | Lines 172 & 220 Crosstie (PCE) to Davis Meter and Reg Sta | C1-V1 | PCE387 | Crosstie | Line 172/220 | NGO | L-172 to L-221 |  | Monitor | 6 | 500 | 500 | Sacramento
217 | MUMY | TP_SACRAMENTO_VALLEY | L220_500 | Lines 172 & 220 Crosstie (PCE) to Davis Meter and Reg Sta | C1-V1 | PCE386 | Crosstie | Line 172/220 | NGO | L-172 to L-220 |  | Monitor | 5 | 500 | 500 | Sacramento
218 | LRS3 | TP_SACRAMENTO_VALLEY | South Sutter Co Reg Sta (PCE) to DR R_FM_B-85. South Sutter DFM Included in distribution model: 09-J09YUBACITYaSd_UTM_45_MOP_MINUS_20_STUDY | South Sutter DFM | C4-V2B | DRJ4PCE816 | Regulator Station | Oper. Drw - 087571.g06 |  | So Sutter Co
219 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | District 10 DFM between L-50 tap & Magnolia Rd (no source Reg) Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C2-V2B | PCE404 | Regulator Station | Lincoln Junction | NGO | L-124 to L-123 |  | Monitor | 16 | 500 | 500 | Sierra
219 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | District 10 DFM between L-50 tap & Magnolia Rd (no source Reg) Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C2-V2B | DRJ4PCE820 | Underground Holder | Oper. Drw - 382860.g06 |  | North Sacramento
220 | ANY3 | TP_SACRAMENTO_VALLEY | 0600_DIXON_158 | Dixon Reg Sta (PCE) to Dixon at the inlet to DR R_FM_R-22. 0600-05: 158# Included in distribution model:ESDZONE_SA_DIXON_H_W1112_APD_452_(MOP_MINUS_20_STUDY) | C2-V1 | DRJ4PCE805 | Regulator Station | Oper. Drw - 081529.g06 |  | Dixon
221 | LRS3 | TP_SACRAMENTO_VALLEY | 0634_COLUSA_GLENN_DRIER_600 | Maxwell Primary Reg Sta (PCE) to Maxwell and Comet Rice Drier. Included in distribution model: -BASE_08-J07maxwellAPD_UTM_452_MOP_MINUS_STUDY.MDB | C1-V2B | DRJ4PCE823 | Regulator Station | Oper. Drw - 0800496.g06 |  | Maxwell Primary
222 | LRS3 | TP_SACRAMENTO_VALLEY | 0643_ARBUCKLE_150 | Arbuckle DFM Included in distribution model: BASE-07-J07ArbuckleAPD_UTM_452_MOP_MINUS_20_STUDY.MDB | C4-V1 | PCE48 | Station | Arbuckle | NGO | Arbuckle DFM from Intermediate |  | Relief | H | 150 | 150 | Meridian
222 | LRS3 | TP_SACRAMENTO_VALLEY | 0643_ARBUCKLE_150 | Arbuckle DFM Included in distribution model: BASE-07-J07ArbuckleAPD_UTM_452_MOP_MINUS_20_STUDY.MDB | C4-V1 | PCE47 | Station | Arbuckle | NGO | Arbuckle DFM from Intermediate |  | Relief | F | 150 | 150 | Meridian
223 | LRS3 | TP_SACRAMENTO_VALLEY | 1514_TOWNSHIP_150 | North Township DFM Included in distribution model: 09-J09YUBACITYaSd_UTM_45_MOP_MINUS_20_STUDY | C2-V3 | DRJ4PCE818 | Regulator Station | Oper. Drw - 0800098.g06 |  | Almendra & Township Rds
224 | ANY3 | TP_SACRAMENTO_VALLEY | L116_L150_200 | L-150/L-116: 200# Davis Meter and Reg Sta (PCE) to Davis at the inlet to DR R_SCSTA-D08. -included in distribution model: ESDZONE_SA_DAVIS_H_W1112_APD_452_(MOP_MINUS_20_STUDY)_1st_&_A_St_Upgrade) | C2-V3 | PCE383 | Meter & Regulator Station | Davis | NGO | L-150 to L-116 |  | Monitor | 105 | 200 | 500 | Sacramento
225 | ANY3 | TP_SACRAMENTO_VALLEY | L158_L220_500 | D. Q. Scott Reg Sta (PCE) to Clark Pacific Concrete Plant. L-158/L-220 (Woodland?) Included in distribution model: ESDZONE_SA_WOODLAND_HL_W1112_APD_452_(w_Teichert)_(MOP_MINUS_20_STUDY) | C1-V1 | DRJ4PCE821 | Regulator Station | Oper. Drw - 087220.g06 |  | D.q. Scott

## MOP -20 Results (hidden)
HIS_ID | Plng Engr | Planning Model | HIS Name | HIS Description | Regulator Station Name | Est. Footage (Miles) | Pipeline Section(s) | Pressure Control Equipment | Validation Status | MOP (psig) | MOP Remarks | NOP (psig) | NOP as Modeled | Pmin Design (psig) | CWD110%Res Pmin (psig) | APD110%Res Pmin (psig) | Analysis Results | New CWD110%Res Pmin (psig) | New APD110%Res Pmin (psig) | Investment Description | Investment Cost ($) | Analysis Notes | Result | PSEP PR Pipe EXIST? | Cust. Impacts | MOP | P min | CDW Pmin | APD P min | CWD ΔP ² | APD ΔP ²
1 | MJA3 | TP_NORTH_BAY | Benica_175 | Benicia DFM | Glenn Cove & Benicia Rd Reg OD 800103 V-3, 4, 5, 6; Vallejo Station OD 086452 V-33, 34, 35, 36 | 7.5 | MJA3PS700 | PCE340, PCE341 | V1-Meets Plng Guide validation criteria | 175 | PCE340,PCE341 valve numbers to do match V-3 and V-4 on operating diagram 0800103 | 170 | 165 | 90 | 140 | 117 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 122 | 96 | Rebuild V18 at Southhampton Rd & Highway 80 in Benicia | $500,000 | No noncore customers | C4-V1 | Y |  | 175 | 90 | 140 | 117 | 48.9456 | 75.1876
2 | MJA3 | TP_NORTH_BAY | Benicia_Ind_Park_175 | Benicia Industrial Park | E. 2nd St & Resvr Rd OD0800104 V-3, 4, 5, 6 | 1.9 | MJA3PS701 | MJA3PCE800 | V1-Meets Plng Guide validation criteria | 175 |  | 168 | 165 | 90 | 149 | 161 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 134 | 147 | Rebuild V38 at Industrial Way & E Channel Rd in Benicia Industrial Park | $500,000 | This analysis includes 100% stage 2 curtailment of Valero Refining (C428) | C4-V1 | Y |  | 175 | 90 | 149 | 161 | 37.3984 | 20.8835
3 | MJA3 | TP_NORTH_BAY | Calistoga_150 | Calistoga DFM serving Calistoga & Angwin | York Creek Reg OD0800390 V-3, 4, 5, 6 | 11.2 | MJA3PS702 | MJA3PCE801 | V1-Meets Plng Guide validation criteria | 150 |  | 146 | 144 | 90 | 117 | 102 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 98 | 80 | Parallel 3,200' 6" with 8" on Highway 29, north of Angwin tap | $2,061,000 | This analysis includes 100% stage 2 curtailment of Pacific Union College (4433 & C406) and St Helena Hospital (C405) | C3-V1 | Y | Y | 150 | 90 | 117 | 102 | 61.1875 | 84
4 | MJA3 | TP_NORTH_BAY | Calistoga_250 | Calistoga 250# DFM | Hwy 29 & Zinfandel OD0800126, V-3, 4, 5, 6 | 4 | PS623, MJA3PS721 | MJA3PCE802 | V1-Meets Plng Guide validation criteria | 250 |  | 246 | 243 | 158 | 230 | 226 | C2-NOP can be lowered to MOP-20 now | 212 | 208 | N/A | N/A | This analysis includes 100% stage 2 curtailments of three customers from the Calistoga_150 subsystem | C2-V1 | Y | Y | 250 | 158 | 230 | 226 | 25.5754 | 30.4348
5 | MJA3 | TP_NORTH_BAY | Cotati_150 | Cotati DFM | Hwy 101 & Old Redwood Hwy OD0800129 V-19, 20, 21, 22; Cotati Reg OD081596 V-4, 5 | 9.5 | PS626, MJA3PS703 | PCE364, PCE365, MJA3PCE803 | V3-Insufficient P data to complete validation | 150 |  | 147 | 145 | 90 | 137 | 131 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 117 | 110 | Rebuild R477 at Penngrove Pitt in Penngrove | $500,000 | This analysis includes 100% stage 2 curtailment of Sonoma State University (C519). Do not lower pressure until pressure data is available to validate model! | C4-V3 | Y |  | 150 | 90 | 137 | 131 | 25.9097 | 37.0764
6 | MJA3 | TP_NORTH_BAY | Fairfield_230 | Fairfield DFM to Tabor & Dover | Suisun-Fairfield Reg OD081528 V-56, 57, 58, 59 | 2.8 | MJA3PS704 | MJA3PCE804 | V1-Meets Plng Guide validation criteria | 230 |  | 220 | 220 | 90 | 184 | 153 | C2-NOP can be lowered to MOP-20 now | 173 | 139 | N/A | N/A | This analysis includes 100% stage 2 curtailment of City of Fairfield Cogen (9178) and County of Solano (9190) | C2-V1 |  | Y | 230 | 90 | 184 | 153 | 42.5089 | 65.8281
7 | MJA3 | TP_NORTH_BAY | Fulton_150 | Fulton & Grant Rd DFM to Wikiup and Healdsburg | Grant School Rd Reg OD082460 V-8, 9, 10, 11 ; Fulton Reg OD0800190 V-13, 14, 15, 16 | 11.6 | MJA3PS705 | MJA3PCE807, MJA3PCE808 | V1-Meets Plng Guide validation criteria | 150 |  | 147 | 143 | 90 | 126 | 110 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 107 | 87 | Parallel 1,130' 3" with 6" on River Rd, east of Fulton Rd, rebuild R108 and R122 at Windsor Rd & Airport Blvd in Santa Rosa | $1,756,900 | This analysis includes 100% stage 2 curtailment of The Airport Club (4581) and Syar Industries(C508 & C509) | C4-V1 |  |  | 150 | 90 | 126 | 110 | 46 | 72.2222
8 | MJA3 | TP_NORTH_BAY | Fairfield_400 | Fairfield DFM to Travis AFB and Vacaville Prison | Vacaville Regulator Station OD081527 V-R1, R2, R3, R4 | 8 | PS609, MJA3PS722 | MJA3PCE806 | V1-Meets Plng Guide validation criteria | 400 |  | 380 | 377 | 90 | 371 | 374 | C1-Existing NOP offset is 20 psi or more | 371 | 374 | N/A | N/A | This analysis includes 100% stage 2 curtailment of Ball Corporation (9177), Calif State Prison (9183), Travis AFB (F134), and American National (F159) | C1-V1 |  |  | 400 | 90 | 371 | 374 | 14.7196 | 13.2482
9 | MJA3 | TP_NORTH_BAY | Fairfield_275 | Fairfield DFM to Rancho Solano | Cordelia & Chadbourne Reg OD0800494 V-4, 5, 8, 9 | 5 | MJA3PS706 | MJA3PCE805 | V3-Insufficient P data to complete validation | 275 |  | 240 | 237 | 90 | 216 | 205 | C1-Existing NOP offset is 20 psi or more | 233 | 222 | N/A | N/A | This analysis includes 100% stage 2 curtailment of 4 customers (9189, 9193, F160, F288). Do not lower pressure until pressure data is available to validate model! | C1-V3 |  |  | 275 | 90 | 216 | 205 | 42.9011 | 49.7593
10 | MJA3 | TP_NORTH_BAY | Hiddenbrook_175 | Hiddenbrook DFM to Sky Valley | Sky Valley OD0800479 V-3, 4, 5, 6 | 2.7 | MJA3PS707 | MJA3PCE809 | V1-Meets Plng Guide validation criteria | 175 |  | 145 | 140 | 90 | 133 | 128 | C1-Existing NOP offset is 20 psi or more | 133 | 128 | N/A | N/A | No noncore customers | C1-V1 |  |  | 175 | 90 | 133 | 128 | 57.4295 | 63.2231
11 | MJA3 | TP_NORTH_BAY | Mare_Island_100 | Mare Island DFM | Pine & Woodrow Ave OD0800157 V-5, 6, 7, 8 | 3.6 | MJA3PS708 | MJA3PCE810 | V1-Meets Plng Guide validation criteria | 100 |  | 95 | 92 | 90 | 89 | 88 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 104 | 72 | Install 3.5 miles 8" DFM to float off Vallejo 250# DFM. Rebuild of 6 reg stations | $9,202,200 | Installation of new main ($7,252,200) will allow for floating off L21H and removal of reg station at Pine & Woodrow. Also includes rebuilds of 6 reg stations ($1,950,000) | C4-V1 | Y |  | 100 | 90 | 89 | 88 | 109.4211 | 118.7368
12 | MJA3 | TP_NORTH_BAY | Marin_175 | Marin DFM | San Rafael Meter & Reg OD183804 V-6, 7, 8, 9, 15, 16, 17, 18 | 20.4 | PS625, MJA3PS709 | PCE338, PCE339 | V1-Meets Plng Guide validation criteria | 175 |  | 168 | 168 | 90 | 148 | 134 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 131 | 115 | Rebuild A39 at Meadowsweet & Conow in Corte Madera. Utilization at 84% for MOP-10 | $500,000 | This analysis includes 100% stage 2 curtailment of 5 customers including San Quentin Prison (4120, C104, C105, C110, C114) | C3-V1 | Y | Y | 175 | 90 | 148 | 134 | 38.717 | 56.2442
13 | MJA3 | TP_NORTH_BAY | Marine_World_125 | Marine World DFM | Hwy 80 & Coach Lane 0800102 V-1 | 0.4 | MJA3PS710 | MJA3PCE811 | V2B-Incomplete validation - results suspect | 125 | Questionable whether MOP is 125 or 250#. Requested PLE to research 3/28/12 | 125 | 125 | 90 | 124 | 124 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 104 | 103 | Rebuild V47 at Coach Ln & Fairgrounds Dr in Vallejo. Utilization at 75% for MOP-10 | $500,000 | No noncore customers. Do not lower pressure until pressure data is available to validate model! | C3-V2B |  |  | 125 | 90 | 124 | 124 | 3.309 | 3.309
14 | MJA3 | TP_NORTH_BAY | Napa_Valley_150 | Napa Valley 150# DFM | Solano Ave Reg OD0800130 V-3, 4, 5, 6 | 10.9 | MJA3PS711 | MJA3PCE812 | V2B-Incomplete validation - results suspect | 150 |  | 148 | 145 | 90 | 139 | 139 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 121 | 121 | RebuildL31 at West Park & Solano in Napa for MOP-20. Utilization at 89% for MOP-10 | $500,000 | This analysis includes 100% stage 2 curtailment of the Veterans Home (C412). Do not lower pressure until pressure data is available to validate model! | C3-V2B | Y |  | 150 | 90 | 139 | 139 | 22.0764 | 22.0764
15 | MJA3 | TP_NORTH_BAY | North_Bay_450 | North Bay 450, Napa Y to Calistoga, Marin, and Santa Rosa | Napa Y OD385170 V-5, 11, 25.98, 60 | 154.5 | PS4, PS5, PS6, PS7, PS8, PS9, PS11, PS12, PS621, PS622, PS624, PS627, PS628, MJA3PS712 | PCE333, PCE334 | V1-Meets Plng Guide validation criteria | 450 | Set point remotely controlled by SF operators | 445 | 445 | 160 | 269 | 199 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 244 | 156 | Rebuild R130 at Piner Rd in Santa Rosa and R597 at Temelec in Sonoma for MOP-20. | $1,000,000 | This analysis includes 100% stage 2 curtailment of 9 customers (4432, C111, 4566, 4578, 4579, 4580, C514, C534, C558) & 22 customers from d/s subsystems | C4-V1 | Y |  | 450 | 160 | 269 | 199 | 73.5664 | 92.0854
16 | MJA3 | TP_NORTH_BAY | North_Bay_610 | North Bay 610, Santa Rosa Compressor to Willits | Santa Rosa Compressor OD082485 | 86.8 | PS10, MJA3PS723 | PCE354, PCE355 | V1-Meets Plng Guide validation criteria | 610 | Current MOP limited to 610 until potential of long seam threats are eliminated. Should be resolved after latest L21E Hopland to Ukiah pig run results are reviewed | 600 | 600 | 160 | 269 | 199 | C2-NOP can be lowered to MOP-20 now | 244 | 156 | N/A | N/A | This analysis includes 100% stage 2 curtailment of 3 customers (4576, C305, and 4571) | C2-V1 | Y | Y | 610 | 160 | 269 | 199 | 86.5048 | 95.9593
17 | MJA3 | TP_NORTH_BAY | North_Bay_650 | North Bay 650, Creed to Napa "Y" and Herrmann Station | Creed Station OD182416 V-7, 8, 10, 14, 16, 17 | 74.2 | PS233, PS234, PS236, PS237, PS238, PS603, PS604, PS605, MJA3PS724 | PCE57, PCE58 | V1-Meets Plng Guide validation criteria | 650 | Set point remotely controlled by SF operators | 645 | 645 | 430 | 453 | 454 | C2-NOP can be lowered to MOP-20 now | 431 | 421 | N/A | N/A | Curtailment of Crocket Cogen and 3 major refineries (Valero, Chevron, Conoco-Philips). This analysis includes 100% stage 2 curtailment of 8 customers (C413, C427, 9169, 9171, 9173, 9174, 9179, 9180), 56 customers from d/s subsystems & 3 customers across | C2-V1 | Y | Y | 650 | 430 | 453 | 454 | 91.4524 | 91.0707
18 | MJA3 | TP_NORTH_BAY | Novato_150 | Novato DFM, Novato Blvd and Diabl to Novato Blvd & Reservoir Rd | Diablo Ave & S. Novato Blvd OD0800128 V-5, 6, 7, 8 | 1.2 | MJA3PS713 | MJA3PCE813 | V3-Insufficient P data to complete validation | 150 |  | 144 | 144 | 90 | 137 | 131 | C2-NOP can be lowered to MOP-20 now | 122 | 116 | N/A | N/A | No noncore customers. Do not lower pressure until pressure data is available to validate model! | C2-V3 |  |  | 150 | 90 | 137 | 131 | 25.9097 | 37.0764
19 | MJA3 | TP_NORTH_BAY | Pine_St_150 | Pine St 150# DFM, Pine St Napa Meter Station to Browns Valley | Pine St Reg OD081513 V-13, 24, E | 1.5 | MJA3PS714 | MJA3PCE814 | V3-Insufficient P data to complete validation | 150 |  | 149 | 147 | 90 | 145 | 143 | C2-NOP can be lowered to MOP-20 now | 125 | 123 | N/A | N/A | No noncore customers. Do not lower pressure until pressure data is available to validate model! | C2-V3 | Y |  | 150 | 90 | 145 | 143 | 10.2431 | 14.2431
20 | MJA3 | TP_NORTH_BAY | Schellville_150 | Schellville DFM, Schellville Reg Station to 5th St West & MacArthur | Shellville Reg 081514 V-10, 11, 12, 13 | 3.9 | MJA3PS715 | MJA3PCE815 | V1-Meets Plng Guide validation criteria | 150 |  | 147 | 145 | 90 | 134 | 125 | C2-NOP can be lowered to MOP-20 now | 115 | 106 | N/A | N/A | No noncore customers | C2-V1 |  |  | 150 | 90 | 134 | 125 | 31.5556 | 47.7431
21 | MJA3 | TP_NORTH_BAY | Sebastopol_150 | Sebastopol 150# DFM, Stone Station Reg to Graton | Stone Reg Station OD0800563 V-4, 5, 6, 7 | 9.9 | MJA3PS716 | MJA3PCE816 | V1-Meets Plng Guide validation criteria | 150 |  | 146 | 146 | 90 | 129 | 117 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 111 | 97 | Rebuild R387 at Graton and R405 at Occidental/Peachland in Sebastopol for MOP-20. | $1,000,000 | No noncore customers | C4-V1 | Y |  | 150 | 90 | 129 | 117 | 40.6875 | 61.1875
22 | MJA3 | TP_NORTH_BAY | Sebastopol_275 | Sebastopol 275# DFM, Madrone Station to Stone Station | Madrone Ave Reg OD082329 V-23, 24, 27, 28 | 5.2 | MJA3PS717 | MJA3PCE817 | V1-Meets Plng Guide validation criteria | 275 |  | 270 | 265 | 160 | 248 | 236 | C2-NOP can be lowered to MOP-20 now | 232 | 213 | N/A | N/A | This analysis includes 100% stage 2 curtailment of City of Sebastopol (C552) | C2-V1 | Y |  | 275 | 160 | 248 | 236 | 28.2279 | 39.8381
23 | MJA3 | TP_NORTH_BAY | Sonoma_200 | Sonoma DFM, Monroe Station to Mountain View Reg and 5th St West & MacArthur to Oakmont | Monroe Reg OD081915 V-18, 19, 20, 21; 5th St West & Macarthur Reg OD0800211 V-6, 7 | 37.9 | PS629 | PCE366, PCE367, MJA3PCE818 | V1-Meets Plng Guide validation criteria | 200 |  | 196 | 196 | 90 | 160 | 136 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 140 | 113 | Rebuild R330 at Bennett Valley in Santa Rosa, R639 at Academy Ln in Sonoma, R672 at Sunnyside Ave in Sonoma, and R729 at Oakmont in Santa Rosa for MOP-20. | $2,000,000 | This analysis includes 100% stage 2 curtailment of 9 customers including Memorial Hospital & Santa Rosa Jr College (4585, 4586, C512, C516, C521, C527, C528, C530, C550) | C4-V1 |  |  | 200 | 90 | 160 | 136 | 45.1411 | 67.4107
24 | MJA3 | TP_NORTH_BAY | Soscol_150 | Soscol DFM, Napa Y to Soscol & Souza (R42) | Napa Y OD385170 V-70, 71, 76, 79, Kaiser Rd Reg OD0800127 V-3, 4, 5, 6 | 7.3 | MJA3PS718 | PCE336,PCE337,MJA3PCE819 | V1-Meets Plng Guide validation criteria | 150 |  | 145 | 144 | 90 | 117 | 121 | C2-NOP can be lowered to MOP-20 now | 96 | 101 | N/A | N/A | This analysis includes 100% stage 2 curtailment of Napa State Hospital (C409 & C 418), Napa Jr College (C117), and Syar Industies (C414) | C2-V1 | Y | Y | 150 | 90 | 117 | 121 | 61.1875 | 54.5764
25 | MJA3 | TP_NORTH_BAY | Trancas_250 | Trancas DFM, Napa | Coffield Reg OD0800210 V-3, 4, 5, 6 | 6.1 | MJA3PS719 | MJA3PCE820 | V1-Meets Plng Guide validation criteria | 250 |  | 247 | 240 | 90 | 202 | 172 | C2-NOP can be lowered to MOP-20 now | 181 | 148 | N/A | N/A | This analysis includes 100% stage 2 curtailment of Queen of the Valley Hospital (C419) | C2-V1 |  |  | 250 | 90 | 202 | 172 | 39.8824 | 60.5074
26 | MJA3 | TP_NORTH_BAY | Vallejo_250 | Vallejo DFM, Herrmann Station to Napa "Y" | Napa Y OD385170 V-9, 10; Hermann Station 082454 V-2, 9 | 13.1 | PS15, PS16, PS17, MJA3PS720 | PCE332,PCE335 | V1-Meets Plng Guide validation criteria | 250 |  | 235 | 233 | 90 | 226 | 221 | C2-NOP can be lowered to MOP-20 now | 223 | 218 | N/A | N/A | This analysis includes 100% stage 2 curtailments of four customers from the Mare_Island_100 subsystem (4430, 4437, C116, C426) | C2-V1 |  |  | 250 | 90 | 226 | 221 | 21 | 25.1085
27 | MJA3 | TP_VACAVILLE | Vacaville_400 | Vacaville 400 DFM supplied from Hawkins & Lewis Primary Reg Station | Hawkins & Lewis Primary Reg Station OD0800154 V-R1, R2, R3, R4 | 13.5 | PS600, PS602, PS607, MJA3PS725 | MJA3PCE821 | V1-Meets Plng Guide validation criteria | 400 |  | 390 | 390 | 90 | 233 | 142 | C2-NOP can be lowered to MOP-20 now | 216 | 113 | N/A | N/A | This analysis includes 100% stage 2 curtailments of four customers (9343, 9342, F130, F131). Consideration should be given towards replacing 1000' of 3/2" to low pressure point that is very sensitive to load and has a 120# pressure drop | C2-V1 | Y | Y | 400 | 90 | 233 | 142 | 69.5925 | 92.0579
28 | MJA3 | TP_VACAVILLE | Vacaville_450 | Vacaville 450 DFM supplied from Vaca Dixon Primary Reg Station | Vaca Dixon Primary Reg OD0800153 V- 4, 5, 8, 9 | 3.7 | PS598,MJA3PS726 | MJA3PCE822 | V1-Meets Plng Guide validation criteria | 450 |  | 370 | 370 | 90 | 300 | 288 | C1-Existing NOP offset is 20 psi or more | 300 | 288 | N/A | N/A | This analysis includes 100% stage 2 curtailments of four customers (9361, 9360, 9362, F164) | C1-V1 | Y |  | 450 | 90 | 300 | 288 | 57.8704 | 61.5
29 | NAH1 | TP_PENINSULA | RAYCHEM DFM | DCUST 5760, EQ000032, 1M1559 to RINGB84 | Van Buren Dr & Ringwood Ave Station, B-84 | 1.18 | PS372 | nah1PCE800 | V3-Insufficient P data to complete validation | 175 | From 089868, feeds into 120 psig Middlefield Ringwood DFM | 170 | 170 | 120 | 154.3 | 140.4 | C2-NOP can be lowered to MOP-20 now | 137.5 | 122.1 |  |  | SRI is elevated pressure customer which may be affected. CWD is lower than APD pressure at node RAYCHEM, but above design minimum listed above, which is inlet to downstream Middlefield/Ringwood feeder. Needs further validation before pressure lowering c | C2-V3 |  |  | 175 | 120 | 154.3 | 140.4 | 42.0124 | 67.2594
30 | NAH1 | TP_PENINSULA | MIDDLEFIELD RINGWOOD DFM | EQ000027, SRIEXT to SREGDN | Middlefield & Ringwood Reg Station, B-83 | 2.01 | PS353, PS361 | nah1PCE801 | V2B-Incomplete validation - results suspect | 120 | From 086868 | 120 | 120 | 90 | 116.6 | 112.2 | C2-NOP can be lowered to MOP-20 now | 96 | 90.7 |  |  | Small DFM with loading which should be confirmed and results validated | C2-V2B |  |  | 120 | 90 | 116.6 | 112.2 | 12.7689 | 28.7486
31 | NAH1 | TP_PENINSULA | HEALY TO MARTIN | SEGMENT OF LINE NEAR CRESSMAN THAT IS OPERATING AT 200 PSIG | Healy Reg Station | 6.62 | nah1PS700 | nah1PCE802 | V1-Meets Plng Guide validation criteria | 300 | 086868, currently operating at 200 psig and modeled as such for all scenarios | 200 | 200 | 155 | 140.2 | 110 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 |  |  | 300 | 155 | 140.2 | 110 | 106.6221 | 118.075
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | Sullivan Station, C-97; Martin Station, Lomita Park Station | 28.87 | PS56, PS116, PS34 | PCE168, PCE169, PCE170, PCE171, PCE191, PCE192 | V1-Meets Plng Guide validation criteria | 145 | From 086868 | 141 | 141 | 90 | 133.2 | 95.3 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 117.9 | 84.4 | Uprate/replace as needed to bring Sullivan to Lomita to 275#; add regulation at SFGLC and run segment between Martin and SFGLC at 145#. Replacement of pipeline downstream of Sullivan totals 1 mile direct replacement, 2 miles of lined pipe replacement. | $20,165,120 | Resulting Pmins above in (17) and (18) are the results at 17th/Missouri without uprate/replacement. Included as FYI | C4-V1 | Y |  | 145 | 90 | 133.2 | 95.3 | 25.3985 | 92.4016
33 | NAH1 | TP_PENINSULA | L109 L132 HMB | Milpitas to Sullivan; Milpitas to Healy; control point is Sullivan inlet. CWD model currently operates at 285# at Milpitas. For CWD analysis changed Milpitas supply to 280#. For APD changed regulation at Milpitas and Sierra Vista to 280#. APD is control | Milpitas Terminal L132, L109 | 100.15 | PS115, PS55, PS349 | nah1PCE816, PCE182, PCE183 | V1-Meets Plng Guide validation criteria | 300 | From 086868 | 285 | 285 | 130 | 139.9 | 104.2 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 130.7 | 94.4 | Install Regulation from L147 (L101) into L132/L109 at Edgewood per plans currently in place; completion planned for 10/31/12 per Richard Geraghty. Estimated at $700k per Richard G. San Bruno Ave x-tie estimated at $3MM per Scott Fannin (2500' total L132 | $3,700,000 | Resulting Pmins above in (17) and (18) are the results without uprate/replacement. Included as FYI These Pmins are for Milpitas L101 at 345#, but Pmin with Milpitas L101 at 350# is also deficient. Pipeline Section PS55 also includes the 6.67 mile secti | C4-V1 | Y |  | 300 | 130 | 139.9 | 104.2 | 96.3447 | 108.2659
34 | NAH1 | TP_PENINSULA | ZANKER | Zanker Rd DFM, San Jose, 0829-01 | Zanker Rd Reg Station, E-03 | 0.72 | PS459 | nah1PS701 | V3-Insufficient P data to complete validation | 170 | From 086868 | 170 | 170 | 90 | 164.5 | 170 | C2-NOP can be lowered to MOP-20 now | 143.8 | 150 |  |  | Service' to customer. Needs validation before pressure lowering can occur. | C2-V3 |  |  | 170 | 90 | 164.5 | 170 | 8.845 | 0
35 | NAH1 | TP_PENINSULA | L101 | Milpitas to Lomita | Milpitas Terminal L101 | 33.68 | PS32, PS33 | nah1PCE817 | V1-Meets Plng Guide validation criteria | 365 | Verified with PLE Scott Fannin | 350 | 350 | 130 | 198 | 131.6 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 198.5 | 123.5 | Likely operational modifications will allow for reduction to 345#. Modifications include backing off pressure support from L147 to L132/L109 at Edgewood, backing off pressure support from L132A into L132/L109 at Sierra Vista, Closing MLV 10.32 during win | TBD | For purposes of this analysis, Edgewood was installed at is feeding into L132/L109 at 285#. Edgewood cost captured on L132 L109 HMB HIS. Possible 'uprate to 397#' of L101 acceleration of hydrotests on spurs | C4-V1 | Y |  | 365 | 130 | 198 | 131.6 | 80.8261 | 99.6402
36 | NAH1 | TP_PENINSULA | FOSTER CITY DFM | 0214-01 aka Poinsettia DFM | Pointsettia Ave. Reg Station, A-74 | 1.69 | PS360 | nah1PCE803 | V2B-Incomplete validation - results suspect | 170 | From 086868 | 170 | 170 | 90 | 165.5 | 130.2 | C2-NOP can be lowered to MOP-20 now | 144.9 | 123.1 |  |  | DFM loading should be validated further before pressure dropped | C2-V2B |  |  | 170 | 90 | 165.5 | 130.2 | 7.2584 | 57.4421
37 | NAH1 | TP_PENINSULA | EL MONTE DFM | Fed at Sierra Vista into recently uprated 201 MOP system | Sierra Vista Ave Reg Station, B-28 | 4.08 | PS401 | nah1PCE804 | V3-Insufficient P data to complete validation | 201 | From 086868 | 192 | 192 | 90 | 153 | 116 | C2-NOP can be lowered to MOP-20 now | 139.2 | 98.1 |  |  | DFM loading should be validated further before pressure dropped | C2-V3 |  |  | 201 | 90 | 153 | 116 | 52.6052 | 83.4185
38 | NAH1 | TP_PENINSULA | TODO EL MUNDO DFM | 0207-01 | Woodside and L109 Reg Station, C-10 | 1.17 | PS357 | nah1PCE805 | V3-Insufficient P data to complete validation | 125 | From 086868 | 120 | 120 | 90 | 113.4 | 104 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 97.5 | 86.7 | ~3500 8" downstream segment replaced with 12" is possibility. More research needed on constraining segment more lead to more appropriate investment | $2,765,000 | 10 psig lowering yields 98.3 psig. Further validation needed. | C3-V3 |  |  | 125 | 90 | 113.4 | 104 | 36.75 | 63.907
39 | NAH1 | TP_PENINSULA | RALSTON POLHEMUS DFM | 0208-02 Ralston 0209-01 Polhemus both fed from common reg station, with Ralston endpoint as design control | Ralston Ave. Reg Station, B-03 | 3.28 | PS358, PS359 | nah1PCE811 | V3-Insufficient P data to complete validation | 150 | From 086868, based on uprate of 2010 | 147 | 147 | 90 | 109.2 | 15 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 101.7 | TBD - Per JTRc uprate planned for 2012. Planned pressure increase is to 222# MOP for 11/1/12 completion with $500k cost per Scott Fannin. Also added $80k for reg station rebuild as model shows deficiency. Should be confirmed with Scott F. | $580,000 | Further work with Distribution is required to verify loading. Uprate currently planned for 222# per Scott Fannin. 202# NOP. Once complete, this should be adequate to allow for 20# setpoint lowering. | C4-V3 |  |  | 150 | 90 | 109.2 | 15 | 73.44 | 154.6875
40 | NAH1 | TP_PENINSULA | PACIFICA DFM | 0213-02, floats off L109 to San Pedro Reg at MP 0.91; Beyond 0.91 the MOP is 90# | San Pedro Valley Reg Station, C-50 | 4.25 | PS366 | nah1PCE806 | V3-Insufficient P data to complete validation | 90 | From 086868 | 86 | 86 | 65 | 77.9 | 65.8 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 145.8 | Replacement of all pipe d/s of San Pedro and eliminate San Pedro Valley Reg Station 17817 ft of 8". Float off L109/L132 | $14,075,430 | Did not change setpoints in the -20 models as no reason to do so on a 90 psig MOP | C4-V3 | Y |  | 90 | 65 | 77.9 | 65.8 | 52.4281 | 97.2996
41 | NAH1 | TP_PENINSULA | NORTH FIRST ST DFM | 0806-01 San Jose | N. First St & Tasman Dr Reg Station, E-05 | 3.01 | PS442 | nah1PCE807 | V2B-Incomplete validation - results suspect | 200 | From 086868 | 190 | 190 | 90 | 160.5 | 140.2 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Conservative investment would be full replacement of 15,840' with 8" | $12,513,600 | Per JTRc can not trust model results as likely under-loaded and currently constrained. As such, we cannot lower by 20# without further analysis on distribution system modeling | C4-V2B |  |  | 200 | 90 | 160.5 | 140.2 | 44.6387 | 63.7742
42 | NAH1 | TP_PENINSULA | GRANT STEVENS CREEK LAWRENCE DFM | 8805-03,04,23 Grant; 8807-01 Lawrence; 8806-01 Stevens Creek; Fed from 2 regs Lawrence and Whisman | Whisman & Middlefield Reg Station, B-34 ; Lawrence & Lakehaven Dr. Reg Station, C-20 | 26.95 | PS400, PS402 | nah1PCE808, nah1PCE809 | V2B-Incomplete validation - results suspect | 180 | From 086868 | 175 | 175 | 90 | 135.5 | 86.7 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Uprate of Lawrence DFM to ?? Psig and PLS installation near Stevens Creek | TBD | Per JTRc can not trust model results as likely under-loaded and currently constrained. As such, we cannot lower by 20# without further analysis on distribution system modeling | C4-V2B |  |  | 180 | 90 | 135.5 | 86.7 | 57.7767 | 102.3996
43 | NAH1 | TP_PENINSULA | LAFAYETTE DFM | 0804-03, Santa Clara | Lafayette & Hogan Reg Station, E-07 | 6.39 | PS439 | nah1PCE810 | V2B-Incomplete validation - results suspect | 180 | From 086868 | 175 | 175 | 90 | 115.1 | 147.9 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Large portions are parallel main with newer pipe (1967, 1973) parelleling older pipe (1949). Possibility of abandonment of 1949 pipeline and uprate of newer pipe. Pipe downstream of these parellel sections is 1957, 1962, 1980 era. | TBD | Per JTRc can not trust model results as likely under-loaded and currently constrained. As such, we cannot lower by 20# without further analysis using distribution system modeling. This DFM is CWD controlled vs APD. Possible uprate due to newer pipeline | C4-V2B | Y |  | 180 | 90 | 115.1 | 147.9 | 78.8148 | 43.3152
44 | JTRc | TP_PENINSULA | SUNNYVALE DFM | aka Britton Ave, GCUST 5813 | Reg Station C-18 | 1.37 | PS406 | nah1PCE812 | V3-Insufficient P data to complete validation | 400 | From 086868 | 225 | 225 | 90 | 224.9 | 225 | C1-Existing NOP offset is 20 psi or more |  |  | TBD - see notes | TBD | Minimal load exists on this DFM on the Peninsula LTS model. Valid analysis not possible | C1-V3 |  |  | 400 | 90 | 224.9 | 225 | 72.0342 | 72.0046
45 | NAH1 | TP_PENINSULA | ALPINE DFM | 0204-01 | Alpine Rd & Piers Ln Reg Station, C-37 | 1.62 | PS354 | nah1PCE813 | V3-Insufficient P data to complete validation | 170 | From 086868 | 170 | 170 | 90 | 170 | 170 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | TBD | TBD | Minimal load exists on this DFM on the Peninsula LTS model. No determination can be made. | C4-V3 |  |  | 170 | 90 | 170 | 170 | 0 | 0
46 | NAH1 | TP_PENINSULA | WALSH DFM | 0205-01 | Walsh Rd Reg Station, C-21 | 1.04 | PS355 | nah1PCE814 | V3-Insufficient P data to complete validation | 230 | 130# MOP listed on 086868, but should be 230# per SWL8. Modeled as 225# in Peninsula LTS. Discuss with JTRc SWL8 | 225 | 225 | 90 | 176.5 | 74.1 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 113 | Possible parallel 1/2 mile with 8" downstream of current 4"/6"parellel section' | $2,085,600 | 130# MOP listed on 086868. Modeled as 225# in Peninsula LTS. SWL8 confirmed this should be listed as 230# MOP | C4-V3 | Y |  | 230 | 90 | 176.5 | 74.1 | 48.5441 | 105.8241
47 | NAH1 | TP_PENINSULA | HACIENDAS DFM | 0206-01 | Woodside Rd Reg Station, C-13 | 0.7 | PS356 | nah1PCE815 | V3-Insufficient P data to complete validation | 110 | From 086868 | 110 | 110 | 90 | 110 | 110 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | TBD | TBD | Minimal load exists on this DFM. Needs Distribution model analysis and further validation for determination to be made. | C4-V3 |  |  | 110 | 90 | 110 | 110 | 0 | 0
48 | BHH2 | TP_CENTRAL_COAST | L306_839 | L306 - 20" transmission from Kettleman to Estrella River PLS. The Town of Avenal has small DFM's off L306 but these DFM's were modeled at 630 PSIG. | Kettleman to Milpitas Lines 100, 190 & 300 382704 Sht 1 | 43.44 | PS288, BHH2PS700, BHH2PS701, BHH2PS702 | PCE208, PCE209 | V1-Meets Plng Guide validation criteria | 840 | L306 has not operated with an inlet of 750 PSIG for years. Morro Bay Power Plant is a peaker and has a total capacity of 7,000 MCFH | 700 | 630 | 500 | 528 | 523 | C1-Existing NOP offset is 20 psi or more | 528 | 523 | No investments needed to reduce the pressure at L300 (Kettlemen) |  | Morro Bay is a peaker plant and has a total capacity of 7,000 MCFH, which is a lot less than the line was originally designed. | C1-V1 | Y |  | 840 | 500 | 528 | 523 | 93.6822 | 94.8356
49 | BHH2 | TP_CENTRAL_COAST | L306_636 | L306 - 20" transmission from Estralla PLS to Morro Bay Power Plant 275 PSIG primary. SoCal gas company has a tap for emergency supply to their customers. | Estrella River PLS 089659 | 29.72 | PS289 | PCE225, PCE226 | V1-Meets Plng Guide validation criteria | 636 |  | 550 | 500 | 250 | 439 | 437 | C1-Existing NOP offset is 20 psi or more | 439 | 437 | No investments needed to lower the MOP due to Morro Bay Power plants is a peaker and load is 7,000 MCFH |  | This power plant can run on either CWD or APD | C1-V1 | Y |  | 636 | 250 | 439 | 437 | 61.9232 | 62.4355
50 | BHH2 | TP_CENTRAL_COAST | L306_275 | L306 - Primary to Morro Bay Power Plant. Short piping to the plant from the primary. Min Flow is 450 MSCF, Maximum flow is 7,000 MSCF | Morro Bay PP Pri Reg Sta 083657 | 0.42 | BHH2PS704 | BHH2PCE800 | V1-Meets Plng Guide validation criteria | 275 | The power plant requires 100 PSIG with a low alarm at 90 PSIG | 150 | 100 | 90 | 99 | 99 | C1-Existing NOP offset is 20 psi or more | 99 | 99 | No investment needed because of Morro Bay Power Plant is a peaker and loads are 7,000 MCFH |  | This power plant can run on either a CWD or APD. | C1-V1 |  |  | 275 | 90 | 99 | 99 | 97.4809 | 97.4809
51 | BHH2 | TP_CENTRAL_COAST | L310_840 | L310 - Tres Pinos to Metz. This line feeds Calpine Cogen and Calpines peaker unit. The feed comes from Tres Pinos off L300A and B. The maximum inlet pressures over the years has been no more than 750 PSIG from L300. Loads 1500 MMCF + 300 MMCF | Tres Pinos Station 089179 | 37.57 | PS293 | BHH2PCE801 | V1-Meets Plng Guide validation criteria | 840 | Newer line installed to serve Calpine Cogen (old BAF) and the new peaker plant | 750 | 750 | 360 | 528 | 732 | C1-Existing NOP offset is 20 psi or more | 528 | 732 | No investments needed for this line. |  | Calpine and Calpine peaker are U/S of Metz and need to have a minimum of 360 PSIG | C1-V1 | Y |  | 840 | 360 | 528 | 732 | 74.1 | 29.475
52 | BHH2 | TP_CENTRAL_COAST | L301A_396 | Line 301A - Old MOP 396 PSIG, CROP 394 PSIG (2011). This line is exclusive to Moss PP units 6&7. Max capacity of this line is 7,000 mcfh. Units 6&7 peak at 13,800 mcfh and the additional load will come from L301G. This line is currently operating at 3 | Hollister Meter Station 282255 | 25.2 | PS270 | PCE204, PCE207 | V1-Meets Plng Guide validation criteria | 394 | CROP 394 8/3/11. Regulators currently set at 374 PSIG. | 374 | 374 | 150 | 177 | 177 | C1-Existing NOP offset is 20 psi or more | 177 | 177 | No investment needed |  | Line is currently lowered MOP - 20. Moss power plant will be able to use 7,000 MMCF off this line during a CWD, APD because it does not effect Monterey and Santa Cruz | C1-V1 | Y |  | 394 | 150 | 177 | 177 | 93.3485 | 93.3485
53 | BHH2 | TP_CENTRAL_COAST | CARMEL_125 | Carmel DFM - 125 PSIG MOP. This system comes off the Monterey system tied to L301B. Aguaito cuts the pressure into Carmel at 125 PSIG. | Aguajito Road Reg Sta 086445 | 2.5 | PS416 | BHH2PCE802 | V1-Meets Plng Guide validation criteria | 125 |  | 118 | 105 | 90 | 97 | 70 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 99 | 90 | Replace the 13,200' 8" with 10" transmission main tested to 313 PSIG. Highly Congested $790/ft includes 70k move around charge. Distribution needs 3 stations rebuilt at $300k each | $11,398,000 | Highly sensitive and political area | C4-V1 | Y |  | 125 | 90 | 97 | 70 | 82.6047 | 142.5249
54 | BHH2 | TP_CENTRAL_COAST | KING_CITY_130 | King City 130 DFM has 2 feeds. The primary is from King City (off L187) and the secondary is off L310 (Metz). Both regulators are set around 125 PSIG | King City Primary Regulator Station 0800096, and Metz Road Station 183721 | 3.9 | PS427 | PCE426, PCE427, PCE428, PCE429 | V1-Meets Plng Guide validation criteria | 130 | 2 Regulator stations feed this DFM, and with both systems, the DFM has adequate capacity | 125 | 125 | 90 | 122 | 121 | C2-NOP can be lowered to MOP-20 now | 109 | 108 | No investments needed since this DFM has 2 feeds going into it |  | The long term investment of this DFM is to uprate it to 313 MOP and have only one regulator station at Metz | C2-V1 |  |  | 130 | 90 | 122 | 121 | 22.9091 | 25.6705
55 | BHH2 | TP_CENTRAL_COAST | L301BCEF_408 | L301BCEF - 408 MOP CROP 344 MOP regulators set at 324 PSIG at Dolan. This system feeds primarily the Ford Ord, Monterey and Carmel areas. Secondary feed is to Harkins which feeds L187, but is now secondary to L187 and L103 is the primary | Dolan Road Meter Sta 083812 | 32.63 | PS271, PS272, PS274, PS275, PS411, PS417 | PCE202, PCE203 | V3-Insufficient P data to complete validation | 408 | ASSUME CROP IS CLEARED where CROP reduction on L301B has caused this line to be reduced 20% until a 300' section of main can be hydro tested in 2012. | 388 | 388 | 300 | 318 | 306 | C1-Existing NOP offset is 20 psi or more | 323 | 309 |  |  | PS411, PS417 does not have any pressure recorders and one will be installed to collect data this winter | C1-V3 | Y |  | 408 | 300 | 318 | 306 | 85.452 | 95.2448
56 | BHH2 | TP_CENTRAL_COAST | L103_350 | L103 - 350 MOP system. Bolsa set at 330 PSIG to California Street Regulator station | Bolsa Meter Station 089655 | 26.4 | PS35, PS423, PS424, PS426, PS430 | PCE200, PCE201 | V1-Meets Plng Guide validation criteria | 350 | MOP lowered to 330 PSIG for analysis. California street is the control point and needs 250 at California. L103 is the primary, and Harkins is the secondary going into L187 | 347 | 330 | 250 | 257 | 249 | C2-NOP can be lowered to MOP-20 now | 257 | 249 | No Investments needed. Pmin at San Ardo is 114 PSIG CWD, and 170 PSIG APD. Pmin required at San Ardo is 110 PSIG. |  | L103 is the primary feed, with Harkins as the secondary, due to the CROP reduction on L301B | C2-V1 | Y | Y | 350 | 250 | 257 | 249 | 94.085 | 100.8317
57 | BHH2 | TP_CENTRAL_COAST | L301G_500 | L301G - 500 MOP is the main transmission line that feeds the Central Coast area. This line directly feeds Moss power plant units 1&2 and extra capacity for units 6&7. There is a back feed regulator set at the end of L301G at 260 PSIG to allow pressure t | Hollister Meter Station 282255 | 39.5 | PS276, PS412, PS418, PS434 | PCE205, PCE206 | V3-Insufficient P data to complete validation | 500 | Modeled at 480 PSIG. Old regulators set at 490-495 PSIG from Hollister and L300A&B | 490 | 480 | 260 | 353 | 473 | C2-NOP can be lowered to MOP-20 now | 353 | 473 | PS412 there was a ERX installed in March of 2012, but data was not collected in the winter of 2011-12. Need to wait until 2013 to validate the DFM. |  | Assuming adequate pressure (480 PSIG +) from L300A and B at Hollister. Control valves regulate pressure coming into L301A and G. | C2-V3 | Y |  | 500 | 260 | 353 | 473 | 68.7451 | 14.403
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | Moss LandingPower Plant Primary Reg Sta 083811 | 0.9 | PS436 | PCE430, PCE431, PCE432, PCE433, PCE434 | V1-Meets Plng Guide validation criteria | 275 | Moss units 6&7 primary regulator station. Regulators set at 125 PSIG with secondary regulators at 120 PSIG from L301G. | 125 | 125 | 110 | 117 | 120 | C1-Existing NOP offset is 20 psi or more | 117 | 120 | No investments needed since this primary is off L301A which is almost exclusive to Moss units 6&7 |  | During a APD, Moss will be able to use 7,000 off L301A since this line does not feed into Monterey and Santa Cruz. | C1-V1 |  |  | 275 | 110 | 117 | 120 | 97.4986 | 96.3794
59 | BHH2 | TP_CENTRAL_COAST | L103_L187_313 | L103-L187 Transmission main from California Reg Station (off L103) to Harkins Road (off L301C) to San Ardo. Primary feed used to be from L301C but had to be shifted to L103 due to the CROP | Dolan Road Meter Sta 083812, California Street Reg Station 089570 and Harkins Rd Regulator Sta 082856 | 69.89 | PS36, PS192, PS193, PS425, PS437, PS431, PS432, PS433 | PCE423, PCE424, PCE425 | V3-Insufficient P data to complete validation | 313 | Because of the CROP reduction on L301B the primary feed to San Ardo will be switched from L301C to L103 (california reg station) | 307 | 293 | 110 | 114 | 170 | C2-NOP can be lowered to MOP-20 now | 114 | 170 | PS425, DCUST2139, DREG4259, PS437 do not have pressure recorders and will be installed this winter to collect data. |  | Numerous customers and several small DFM's have not had recording devices to monitor winter pressures in the past. T&R does not have charts or ERX's | C2-V3 | Y |  | 313 | 110 | 114 | 170 | 98.9566 | 80.4353
60 | BHH2 | TP_CENTRAL_COAST | MTY1_2_313 | 1813, 1815 Monterey - 313 MOP system. Two stations feed the Fort Ord, Monterey area. 1st & 8th and Davis - Reservation | 8th St and 1st Ave Regulator Station 087211 and Davis-Reservation Roads Regulator Station 089572 | 35.9 | PS410, PS414, PS415 | BHH2PCE803, BHH2PCE804 | V1-Meets Plng Guide validation criteria | 313 | ASSUME CROP IS CLEARED where U/S subsystem L301B was lowered from 408 PSIG to 344 PSIG because of a CROP. | 307 | 293 | 200 | 215 | 200 | C2-NOP can be lowered to MOP-20 now | 244 | 174 |  |  | Pressure problems in Carmel and Monterey occur when the CROP is not cleared off L301B | C2-V1 | Y | Y | 313 | 200 | 215 | 200 | 89.2615 | 100
61 | BHH2 | TP_CENTRAL_COAST | L181A_DFM1_303 | 1816 - 303 PSIG system from San Jaun to Blain Street (inlet to Felton DFM) | San Juan Road Reg Station 0800062, Front St Regulator Station 0800097, Watsonville Crosstie Reg Sta 0800407 and Rob Roy Junction Pressure Limiting Sta 087212 | 34.6 | PS182, PS183, PS407, PS413, PS420, PS421, PS422 | PCE435, PCE436, PCE437, PCE438 | V3-Insufficient P data to complete validation | 303 | This section is D/S of Rob Roy which is the control point. Assumes that L1816 is back in service and not locked in at 225 PSIG. | 295 | 283 | 90 | 147 | 73 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 147 | 92 | In order to get Felton back up to 90 PSIG it is necessary to replace the existing 10" main coming out of Rob Roy (1.87 miles) with 16". This is also assuming that 1816 will be hydro tested and placed back in service. 9900' 16" x $980/ft = $9.8 million p | $10,700,000 | This analysis is based on the fact that L181A (1816) will be hydro tested and back in service from San Juan to Rob Roy to feed into Santa Cruz. | C4-V3 | Y |  | 303 | 90 | 147 | 73 | 83.862 | 103.3103
62 | BHH2 | TP_CENTRAL_COAST | DFM1_2_3_303 | 1816 and 1818 DFM (Felton and Davenport DFM's, Santa Cruz holder). Systems past Rob Roy | Rob Roy Junction Pressure Limiting Sta 087212 and the Santa Cruz Underground Holder 080393 | 37.2 | PS409, PS419, PS429 | PCE435, PCE436 | V1-Meets Plng Guide validation criteria | 303 | Controlling point is Rob Roy which L181A and B converge. Pmin is at Felton where the Santa Cruz holder will supply extra feed at 180 PSIG | 295 | 283 | 90 | 147 | 73 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 147 | 92 | See L181_DFM1_303 - Same investment needed. | See L181_DFM1_303 | This analysis is based on the fact that L181A (1816) will be hydro tested and back in service from San Juan to Rob Roy to feed into Santa Cruz. | C4-V1 | Y |  | 303 | 90 | 147 | 73 | 83.862 | 103.3103
63 | BHH2 | TP_CENTRAL_COAST | L181B_DFM2_400 | 1817 - 400 MOP system starting at Cole Road Regulator Station and endind at Rob Roy. Cole is the primary feed, and San Juan is the secondary feed | Cole Road Reg Sta 089666 and San Juan 0800062 | 16.7 | PS184, PS185, PS273, PS277 PS408, PS435 | BHH2PCE808, BHH2PCE809 | V1-Meets Plng Guide validation criteria | 400 | System reduced to determine what impacts there are. Controlling point is Rob Roy where L181A and B converge. Pmin is at Felton | 395 | 380 | 90 | 147 | 73 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 147 | 92 | See L181_DFM1_303 - Same investment needed. | See L181_DFM1_303 | This analysis is based on the fact that L181A (1816) will be hydro tested and back in service from San Juan to Rob Roy to feed into Santa Cruz. | C4-V1 | Y |  | 400 | 90 | 147 | 73 | 91.1066 | 101.8242
64 | BHH2 | TP_CENTRAL_COAST | SANTA_CRUZ_HOLDER | The underground holder is used during winter months to make up capacity to serve the Felton area. It is manually filled each time it is used during a cold event. There is no permanent connection to the transmission system that could over pressure it. | Santa Cruz Underground Holder 080393 | 2.33 | BHH2PS705 | PCE439, PCE440 | V1-Meets Plng Guide validation criteria | 618 | Undergournd holder is typically re-charged at 600-605 PSIG when the holder is used in the winter months. | 600 | 598 | 170 | 499 | 125 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 521 | 137 | See L181_DFM1_303 - Same investment needed. | See L181_DFM1_303 | Reduced capacity by reducing the holder's pressure. At 618 = 3.016 MMCF, at 598 PSIG = 2.912 MMCF (Difference 0.104 MMCF) | C4-V1 |  |  | 618 | 170 | 499 | 125 | 37.6527 | 103.7604
65 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Tap | L138A, L138B |  | 36.96 | PS130, PS131, PS126 | RLP7PCE811 | V1-Meets Plng Guide validation criteria | 800 | None | 700 | 700 | 590 | 593 | 605 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 800 | 590 | 593 | 605 | 98.7842 | 93.8592
66 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Fresno Belt Main | System d/s of Tarpey, Chestnut/Clay and FGLC |  | 36.71 | PS478 | PCE443, PCE449, RLP7PCE800 | V1-Meets Plng Guide validation criteria | 204 | 204 | 195 | 195 | 90 | 130 | 90 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Upgrading the Fresno Belt Main was previously identified and is a current project in engineering. TSP has already identified the need to complete by November 1, 2012. | TBD |  | C4-V1 |  |  | 204 | 90 | 130 | 90 | 73.7439 | 100
67 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L108 Tap | Vernalis Tap to Vernalis Field Valve Lot |  | 4.59 | PS48 | PCE154 | V1-Meets Plng Guide validation criteria | 1040 | None | 720 | 715 | 650 | 653 | 668 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 1040 | 650 | 653 | 668 | 99.4069 | 96.4005
68 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L108 Vernalis Valve Lot | Vernalis Field Valve Lot to Ripon Reg Station |  | 14.53 | PS49, PS519 | RLP7PCE809 | V1-Meets Plng Guide validation criteria | 720 | None | 715 | 715 | 395 | 426 | 564 | C2-NOP can be lowered to MOP-20 now | 400 | 545 |  |  |  | C2-V1 | Y |  | 720 | 395 | 426 | 564 | 92.9766 | 55.2753
69 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L215 | Oak Flat to West Ave Reg. |  | 45.93 | PS240, PS491, PS78 | RLP7PCE808 | V1-Meets Plng Guide validation criteria | 787 | CROP in place that reduced MOP from 890 psig to 787 psig. | 750 | 750 | 290 | 305 | 629 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 |  |  | 787 | 290 | 305 | 629 | 98.3326 | 41.7973
70 | RLP7 | TP_SAN_JOAQUIN_VALLEY | 7224-19 | Stanislaus DFM |  | 1.34 | RLP7PS702 | RLP7PCE806 | V2B-Incomplete validation - results suspect | 95 | None | 95 | 95 | 90 | 92 | 91 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 72 | 70 | Install 1.34 miles 8" or larger pipe with MAOP of 720 psig. | $3,500,000 |  | C4-V2B |  |  | 95 | 90 | 92 | 91 | 60.6486 | 80.4324
71 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Oakdale | Oakdale, Escalon, Riverbank |  | 31.76 | RLP7PS703 | PCE465 | V1-Meets Plng Guide validation criteria | 180 | None | 175 | 175 | 90 | 139 | 139 | C2-NOP can be lowered to MOP-20 now | 109 | 109 |  |  | ASD controls due to canning loads. Pressures shown above are ASD pressures. | C2-V1 |  | Y | 180 | 90 | 139 | 139 | 53.823 | 53.823
72 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Turlock-Modesto DFM | 260 psig system. Serves Modesto, Ceres, Turlock. |  | 44.62 | RLP7PS706, RLP7PS707, RLP7PS708, RLP7PS709 | PCE463, PCE464, RLP7PCE816, RLP7PCE817 | V3-Insufficient P data to complete validation | 260 | None | 255 | 255 | 125 | 199 | 201 | C2-NOP can be lowered to MOP-20 now | 179 | 179 |  |  |  | C2-V3 |  |  | 260 | 125 | 199 | 201 | 53.8701 | 52.3309
73 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Modesto | 408 psig system. |  | 49.47 | PS489, PS518, PS486, RLP7PS700, RLP7PS701 | RLP7PCE802 | V1-Meets Plng Guide validation criteria | 408 | none | 403 | 403 | 200 | 203 | 206 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | See notes. | See notes | 2012 PSEP replacement is scheduled for construction by end of 2012. This will replace about 4 miles of 8" pipe with 16" pipe on DFM 7221-10. Pressure reduction should not happen until this is complete. | C4-V1 | Y |  | 408 | 200 | 203 | 206 | 99.044 | 98.0738
74 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118N | Bradbury to Merced (V-60.45) |  | 34.45 | PS75, PS76, PS77, PS78, PS80 | RLP7PCE803, RLP7PCE804, PCE450 | V1-Meets Plng Guide validation criteria | 400 | BTU separation V60.45 is opened on Design Days to support Merced south. | 395 | 395 | 90 | 70 | 172 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | see notes | see notes | 2013 PSEP project planned to extend L352 to Herndon Jct. This will be 24" pipe with a new reg station feeding into L118. After project is complete, pressure reductions can be done. | C4-V1 | Y |  | 400 | 90 | 70 | 172 | 102.1066 | 85.8565
75 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Eight Mile Road DFM | Eight Mile Road DFM fed from L108. |  | 16.48 | PS511 | RLP7PCE822 | V3-Insufficient P data to complete validation | 412 | none | 385 | 385 | 90 | 278 | 293 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | L108, between Ripon-Modesto Meter Station and Eight Mile Road, is to be upgraded from 408 psig to 720 psig, in May 2012. The pressures above are prior to the upgrade. Eight Mile Road will be regulated to line 11. | C1-V3 |  |  | 412 | 90 | 278 | 293 | 57.1998 | 51.9011
76 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L148 | McMullin Ranch to Morgan/Whitmore |  | 17.63 | PS141, PS488, PS485 | RLP7PCE801 | V1-Meets Plng Guide validation criteria | 326 | Under MOP from 408 psig to 326 psig. Currently operating 15 psig below 326 psig. | 311 | 311 | 220 | 209 | 210 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | See notes | See notes | Hydrotest is progress. Pressure restoration 12/1/12, tentatively, to 408 psig. | C4-V1 | Y |  | 326 | 220 | 209 | 210 | 108.1536 | 107.4297
77 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Hammertown | Hammertown and Tom 'O' Shanter | Brown Rd at Red Mountain Reg OD0800470 V- R1, R2, R3, R4 | 7.22 | PS513 | RLP7PCE823 | V3-Insufficient P data to complete validation | 412 | none | 385 | 385 | 90 | 287 | 300 | C1-Existing NOP offset is 20 psi or more |  | 300 |  |  | L108, between Ripon-Modesto Meter Station and Eight Mile Road, is to be upgraded from 408 psig to 720 psig, in May 2012. The pressures above are prior to the upgrade. Hammertown will be regulated to Line 11. | C1-V3 |  |  | 412 | 90 | 287 | 300 | 54.054 | 49.3331
78 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Louise Ave DFM | Louise Ave DFM served from L108. |  | 2.61 | PS515 | PCE814 | V2B-Incomplete validation - results suspect | 408 | none | 385 | 385 | 90 | 358 | 374 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | L108, between Ripon-Modesto Meter Station and Eight Mile Road, is to be upgraded from 408 psig to 720 psig, in May 2012. The pressure above are prior to the upgrade. Lousie Ave DFM will be regulated to line 11. | C1-V2B |  |  | 408 | 90 | 358 | 374 | 24.1848 | 16.7892
79 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Zephyr Road DFM | Fed from L108 1606 at Carpenter Rd |  | 2.51 | PS509 | RLP7PCE821 | V3-Insufficient P data to complete validation | 408 | none | 385 | 385 | 90 | 330 | 348 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | L108, between Ripon-Modesto Meter Station and Eight Mile Road, is to be upgraded from 408 psig to 720 psig, in May 2012. The pressure above are prior to the upgrade. Zephyr Road DFM will be regulated to line 11. | C1-V3 |  |  | 408 | 90 | 330 | 348 | 36.3492 | 28.6429
80 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Alpine DFM | 1621-01, DREG 4939. Fed from L108. |  | 2.1 | PS537 | RLP7PCE805 | V3-Insufficient P data to complete validation | 100 | none | 100 | 100 | 90 | 93 | 91 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | 2.1 miles of 8" or larger, 720 psig. | $8,800,000 |  | C4-V3 |  |  | 100 | 90 | 93 | 91 | 71.1053 | 90.4737
81 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Manteca DFM | 1602-01. MP 0.7 - MP 2.66 |  | 2 | PS531 | RLP7PCE807 | V3-Insufficient P data to complete validation | 120 |  | 115 | 115 | 90 | 108 | 105 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 103 | 99 | Reinforce with approx 0.75 miles, 8" steel | $3,100,000 |  | C3-V3 |  |  | 120 | 90 | 108 | 105 | 43.4286 | 53.5714
82 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Hazelton DFM | Hazelton DFM, Pacific Paperboard DFM. Serves the Port of Stockton. |  | 10.95 | PS514 | PCE813 | V2B-Incomplete validation - results suspect | 175 |  | 170 | 170 | 90 | 151 | 163 | C2-NOP can be lowered to MOP-20 now | 134 | 147 |  |  |  | C2-V2B |  |  | 175 | 90 | 151 | 163 | 34.7347 | 18.0067
83 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Stockton L108 | Ripon-Modesto Meter Station to Eight Mile Road. |  | 24.4 | PS50, PS51 | RLP7PCE825 | V1-Meets Plng Guide validation criteria | 408 | This section of L108 to be upgraded from 408 psig to 720 psig in July 2012 (?), in conjunction with NCPA Lodi coming on-line. | 403 | 403 | 275 | 275 | 293 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Finish the pressure upgrade to 720 psig. |  | Pressure upgrade in progress. Once upgrade is complete to 720 psig, MOP-20 can be implemented. | C4-V1 | Y |  | 408 | 275 | 275 | 293 | 100 | 88.7449
84 | RLP7 | OTHER | Patterson DFM | Served from L-2. |  | 3.45 | RLP7PS715 | PCE149 | V3-Insufficient P data to complete validation | 395 |  | 250 | 250 | 90 | 210 | 210 | C2-NOP can be lowered to MOP-20 now | 210 | 210 |  |  | NOP is uncertain. | C2-V3 |  |  | 395 | 90 | 210 | 210 | 75.6633 | 75.6633
85 | RLP7 | OTHER | Los Banos DFM | Served from L-2. |  | 7.89 | PS507 | RLP7PCE810 | V1-Meets Plng Guide validation criteria | 394 |  | 385 | 350 | 90 | 275 | 217 | C2-NOP can be lowered to MOP-20 now | 275 | 217 |  |  | NOP is uncertain. | C2-V1 |  |  | 394 | 90 | 275 | 217 | 54.1071 | 73.5014
86 | RLP7 | OTHER | L-331 | Crosstied to L-2 and L-401 |  | 15.7 | PS308, PS309 | PCE104, PCE105 | V1-Meets Plng Guide validation criteria | 787 | CROP reduced MOP to 787 psig from 890 psig. | 610 | 610 | 120 | 150 | 150 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | ASD controls. Seasonal Load. | C1-V1 | Y |  | 787 | 120 | 150 | 150 | 98.6611 | 98.6611
87 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Jct/Elkhorn | Downstream of Helm Jct and Elkhorn. 650 psig system. |  | 158.34 | PS57, PS59, PS311, PS312, PS127, PS128, PS129, PS132, PS133, PS482, PS483 | PCE451, PCE452, PCE446, PCE447 | V1-Meets Plng Guide validation criteria | 650 |  | 645 | 645 | 225 | 304 | 328 | C2-NOP can be lowered to MOP-20 now | 229 | 320 |  |  |  | C2-V1 | Y | Y | 650 | 225 | 304 | 328 | 88.7621 | 84.6833
88 | RLP7 | TP_SAN_JOAQUIN_VALLEY | FGLC | FGLC to FJCT |  | 12.49 | PS73, PS58 | PCE448, PCE450 | V1-Meets Plng Guide validation criteria | 400 |  | 390 | 390 | 300 | 316 | 313 | C2-NOP can be lowered to MOP-20 now | 306 | 302 |  |  | 2012 PSEP replacement pipe will improve pressures. | C2-V1 |  | Y | 400 | 300 | 316 | 313 | 85.92 | 88.6157
89 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118 | FJCT to V-60.45 (Merced). |  | 126.76 | PS73, PS74, PS75, PS79 | PCE450 | V2B-Incomplete validation - results suspect | 400 |  | 395 | 395 | 90 | 63 | 136 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | PSEP to extend L352 to Herndon and install a new reg station. This is planned for 2013 or 2014. | TBD |  | C4-V2B | Y |  | 400 | 90 | 63 | 136 | 102.7196 | 93.156
90 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Ave 13 | 7211-01 |  | 3.37 | RLP7PS704 | PCE812 | V2B-Incomplete validation - results suspect | 150 | Not sure of MOP | 150 | 150 | 90 | 133 | 149 | C2-NOP can be lowered to MOP-20 now | 110 | 129 |  |  |  | C2-V2B |  |  | 150 | 90 | 133 | 149 | 33.4097 | 2.0764
91 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Selma | 1209-02. Feed to Selma. |  | 4 | RLP7PS705 | RLP7PCE815 | V3-Insufficient P data to complete validation | 230 |  | 230 | 230 | 90 | 203 | 193 | C2-NOP can be lowered to MOP-20 now | 181 | 169 |  |  | NOP is uncertain. | C2-V3 | Y |  | 230 | 90 | 203 | 193 | 26.096 | 34.9353
92 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L307/134 | Spreckels to Herndon Jct |  | 73.36 | PS290, PS291, PS292, PS119, PS120, PS479 | PCE234, PCE235 | V1-Meets Plng Guide validation criteria | 500 |  | 495 | 495 | 280 | 310 | 328 | C2-NOP can be lowered to MOP-20 now | 291 | 309 |  |  |  | C2-V1 | Y | Y | 500 | 280 | 310 | 328 | 89.6853 | 82.993
93 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Kerman | Kerman DFM serves Kerman and Biola |  | 7.86 | PS480 | RLP7PCE820 | V3-Insufficient P data to complete validation | 283 |  | 275 | 275 | 90 | 184 | 125 | C2-NOP can be lowered to MOP-20 now | 166 | 98 |  |  |  | C2-V3 |  |  | 283 | 90 | 184 | 125 | 64.2223 | 89.547
94 | RLP7 | TP_TRACY | Tracy | Serves City of Tracy. |  | 25.5 | PS155, PS516 | PCE152, PCE138 | V1-Meets Plng Guide validation criteria | 365 |  | 325 | 320 | 90 | 306 | 300 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 |  |  | 365 | 90 | 306 | 300 | 31.6396 | 34.5455
95 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Baker Commodities | Transmission along Madera Ave that feeds Foster Farms and Baker Commodities. |  | 9 | RLP7PS711 | RLP7PCE819 | V2B-Incomplete validation - results suspect | 250 |  | 200 | 200 | 90 | 166 | 200 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V2B |  |  | 250 | 90 | 166 | 200 | 64.2353 | 41.3603
96 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Herndon & Hayes | Fed from Cattern and Weber. |  | 1.23 | RLP7PS713 | RLP7PCE824 | V3-Insufficient P data to complete validation | 400 |  | 200 | 200 | 90 | 195 | 193 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V3 |  |  | 400 | 90 | 195 | 193 | 80.2995 | 80.8104
97 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Kamm Ave Feeder | Served from L111 and feed Con Agra Foods and Helm Sulfur. |  | 4.09 | RLP7PS710 | RLP7PCE818 | V2B-Incomplete validation - results suspect | 300 | MOP from Fresno T&R | 270 | 270 | 100 | 255 | 255 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | ASD controls. | C1-V2B |  |  | 300 | 100 | 255 | 255 | 31.2188 | 31.2188
98 | RLP7 | OTHER | L-186 | Serves Dos Palos from L-2. |  |  | PS190, PS191 | RLP7PCE826 | V3-Insufficient P data to complete validation | 270 |  | 250 | 250 | 90 | 186 | 186 | C2-NOP can be lowered to MOP-20 now | 186 | 186 |  |  | NOP uncertain. | C2-V3 | Y |  | 270 | 90 | 186 | 186 | 59.1111 | 59.1111
99 | RLP7 | OTHER | Nees Ave DFM | Serves Olam West (DeFrancisco) from L-2. |  | 7.52 | PS501, RLP7PS712 | PCE467 | V2B-Incomplete validation - results suspect | 620 |  | 400 | 400 | 90 | 153 | 153 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | NOP uncertain. ASD controls. | C1-V2B |  |  | 620 | 90 | 153 | 153 | 95.9317 | 95.9317
100 | RLP7 | OTHER | Newman-Gustine | Looped DFM to serve Newman and Gustine. |  | 15.75 | RLP7PS714 | PCE134, PCE142 | V3-Insufficient P data to complete validation | 150 |  | 145 | 145 | 90 | 126 | 133 | C2-NOP can be lowered to MOP-20 now | 109 | 116 |  |  | NOP is uncertain. | C2-V3 |  |  | 150 | 90 | 126 | 133 | 46 | 33.4097
101 | c5s1 | TP_SAN_JOSE | L100 | L100 from Milpitas Terminal to PLS7 | Milpitas Terminal | 12 | PS31 | c5s1PCE800 | V1-Meets Plng Guide validation criteria | 365 | Original MOP of 400 psig. Reduced to 300 psig by CPUC. CPUC approved raising of MOP to 365 psig in Dec 2011. | 350 | 345 | 225 | 249.02 | 196.54 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Parallel ~4 miles of L100 from M.P. 500.69 to MLV 144.67 with 16" pipe. | $17,400,000 | N/A | C4-V1 | Y |  | 365 | 225 | 249.02 | 196.54 | 86.2155 | 114.5242
102 | c5s1 | TP_SAN_JOSE | Dixon Landing DFM | DFM from L131 at Dixon Landing & 880 to Dixon Landing & Milpitas Blvd. | Dixon Landing & Hwy 880 Regulator Station | 0.94 | PS453 | c5s1PCE801 | V1-Meets Plng Guide validation criteria | 175 |  | 168 | 163 | 90 | 147.72 | 139.53 | C2-NOP can be lowered to MOP-20 now | 133.37 | 124.31 | N/A | N/A | N/A | C2-V1 |  |  | 175 | 90 | 147.72 | 139.53 | 39.0846 | 49.5289
103 | c5s1 | TP_SAN_JOSE | Barber DFM | DFM from Milpitas Terminal to Lundy & Murphy Station (F17) and Abbott-Milpitas Alvisio Road (E11). | Milpitas Terminal (SJDFM) | 4.1 | PS445, PS443 | PCE180 | V3-Insufficient P data to complete validation | 160 | Original MOP of 200 psig. Reduced to 160 psig by CPUC 2/2011. No indication that original MOP will be restored. | 145 | 140 | 90 | 132.21 | 127.74 | C2-NOP can be lowered to MOP-20 now | 126.94 | 122.31 | N/A | N/A | N/A | C2-V3 |  |  | 160 | 90 | 132.21 | 127.74 | 46.4029 | 53.0428
104 | c5s1 | TP_SAN_JOSE | Mabury DFM | DFM from Mabury Station at Mabury Rd & Pine Hollow (F06) to Autumn & Julian Reg Station (F47). | Mabury Road Regulator Station | 5.1 | PS457, PS447 | c5s1PCE802 | V1-Meets Plng Guide validation criteria | 200 |  | 190 | 185 | 90 | 165.44 | 153.95 | C2-NOP can be lowered to MOP-20 now | 154.24 | 141.91 | N/A | N/A | N/A | C2-V1 |  |  | 200 | 90 | 165.44 | 153.95 | 39.5912 | 51.0953
105 | c5s1 | TP_SAN_JOSE | Tully DFM | DFM from Tully Station (F78) to Roberts & Fisher Station (D24). | Tully Regulator Station | 33.5 | PS452, PS454, PS466, PS467, PS450, c5s1PS700 | PCE460 | V1-Meets Plng Guide validation criteria | 200 |  | 195 | 190 | 90 | 131.25 | 60.28 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | (1) Parallel ~0.96 miles of 0840-01 with 6" pipe from MLV 13-14C to MLV 13-J5B. (2) Parallel ~3.8 miles of 0821-02 with 12" pipe from MLV 74-A5A to Reg D26. | $20,800,000 | N/A | C4-V1 | Y |  | 200 | 90 | 131.25 | 60.28 | 71.3901 | 114.001
106 | c5s1 | TP_SAN_JOSE | Fontanoso DFM | DFM from Fontanoso Reg Station (G77) to Cottle & Poughkeepsie Reg Station (G49). | Fontanoso Road Regulator Station | 2.9 | PS448 | c5s1PCE803 | V1-Meets Plng Guide validation criteria | 400 |  | 365 | 360 | 260 | 348 | 340.48 | C1-Existing NOP offset is 20 psi or more |  |  | N/A | N/A | N/A | C1-V1 |  |  | 400 | 260 | 348 | 340.48 | 42.0952 | 47.6985
107 | c5s1 | TP_SAN_JOSE | Blossom Hill DFM | DFM from Cottle & Poughkeepsie Reg Station (G49) to endpoints of Cottle & Santa Teresa Reg Station (G73) and Rajkovich & Almaden Expressway Reg Station (G79). | Cottle & Poughkeepsie Road Regulator Station | 9 | PS449 | c5s1PCE804 | V1-Meets Plng Guide validation criteria | 242 |  | 235 | 230 | 90 | 168.26 | 114.37 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 164.25 | 108.69 | Replace approximately 1.1 miles of 6" with 10" starting 6000' downstream of G55 to G79. | $5,300,000 | N/A | C3-V1 |  |  | 242 | 90 | 168.26 | 114.37 | 59.9488 | 90.1306
108 | c5s1 | TP_GILROY | Emado DFM | DFM from Emado Reg Station (H15) to Emado & Hwy 101 Reg Station (H23). | Emado Ave Regulator Station | 0.71 | PS451 | c5s1PCE805 | V3-Insufficient P data to complete validation | 100 |  | 90 | 90 | 80 | 89.8 | 89.8 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 89.9 | 89.9 | Replace ~3700 ft (whole DFM) of 2" with 6". | $1,100,000 | N/A | C3-V3 | Y |  | 100 | 80 | 89.8 | 89.8 | 53.7767 | 53.7767
109 | c5s1 | TP_GILROY | Puppo DFM | DFM from Hwy 101 & Scheller Ave Reg Station (H18) to Monterey Hwy & Puppo R/W Reg Station (H16). | Hwy 101 and Scheller Ave Regulator Station | 0.84 | PS458 | c5s1PCE806 | V3-Insufficient P data to complete validation | 400 |  | 250 | 245 | 90 | 241.3 | 238.5 | C1-Existing NOP offset is 20 psi or more |  |  | N/A | N/A | N/A | C1-V3 |  |  | 400 | 90 | 241.3 | 238.5 | 67.0009 | 67.8853
110 | c5s1 | TP_GILROY | Cochrane DFM | DFM from Peet & Cochrane Reg Station (H01) to N/S Cochrane, w/o Hwy 101 Reg Station (H03). | Peet & Cochrane Regulator Station | 0.88 | PS455 | c5s1PCE807 | V3-Insufficient P data to complete validation | 320 |  | 308 | 303 | 90 | 235.5 | 186.4 | C2-NOP can be lowered to MOP-20 now | 225.2 | 173.3 | N/A | N/A | N/A | C2-V3 |  |  | 320 | 90 | 235.5 | 186.4 | 49.777 | 71.7445
111 | c5s1 | TP_GILROY | Diana DFM | DFM from Diana Reg Station(H06) east to Diana & L300A Reg Station (H05) and west to Diana e/o Railroad Reg Station (H09). | Diana Ave Regulator Station | 2.9 | PS444 | c5s1PCE808 | V2B-Incomplete validation - results suspect | 250 |  | 240 | 235 | 90 | 171.1 | 119.3 | C2-NOP can be lowered to MOP-20 now | 157.2 | 99.3 | N/A | N/A | An uprate of Diana DFM from an MOP of 250# to 350# is scheduled to be complete by the end of 2012. | C2-V2B |  |  | 250 | 90 | 171.1 | 119.3 | 61.075 | 88.727
112 | c5s1 | TP_GILROY | Church DFM | DFM from Church Ave Reg Station (H46) to Church & Old 101 Hwy (H33). | Church Ave Regulator Station | 2.6 | PS460, c5s1PS701 | c5s1PCE809 | V1-Meets Plng Guide validation criteria | 335 |  | 300 | 295 | 90 | 191.8 | 99.9 | C1-Existing NOP offset is 20 psi or more |  |  | N/A | N/A | N/A | C1-V1 |  |  | 335 | 90 | 191.8 | 99.9 | 72.4492 | 98.1945
113 | c5s1 | TP_GILROY | Roop DFM | DFM from Roop Road Reg Station (H95) to Roop Road & New Reg Station (H96). | Roop Road Regulator Station | 1.3 | PS446 | c5s1PCE810 | V3-Insufficient P data to complete validation | 120 |  | 115 | 110 | 90 | 104.7 | 102 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 99.4 | 96.7 | Replace ~3,450 ft of 2" with 4" from H94 at Estates Drive & Roop Road to H97 at Sugar Babe Road & Roop Road | $1,760,000 | N/A | C3-V3 | Y |  | 120 | 90 | 104.7 | 102 | 54.57 | 63.4286
114 | c5s1 | TP_GILROY | Bloomfield DFM | DFM from Bloomfield Reg Station (H73) to Kelton Dr & First Reg Station. DFM includes Calpine/Gilroy Power Plant. | Bloomfield Regulator Station | 9.1 | PS461, PS462, PS463, PS464, PS465 | c5s1PCE811 | V1-Meets Plng Guide validation criteria | 400 |  | 395 | 390 | 90 | 362.5 | 353.5 | C2-NOP can be lowered to MOP-20 now | 346.3 | 336.8 | N/A | N/A | N/A | C2-V1 |  |  | 400 | 90 | 362.5 | 353.5 | 18.8241 | 23.0663
115 | ZTR1 | TP_REDDING | L402_REDDING_600 | L402 from Redding/ Calaveras Tap (L400) to Lehigh Cement and associated DFM's | Redding Calaveras Tap OD083694 V-8, 9, 10, 11 | 54 | PS344, PS545, PS547, PS548, PS549, PS559, PS561, ZTR1PS700 | PCE374, PCE375, PCE40 | V1-Meets Plng Guide validation criteria | 600 | There is currently a CROP in place of 426 psig; however, I anticipate that CROP being lifted in June once a short section of main is replaced at DREG5477. | 594 | 590 | 120 | 386 | 419 | C2-NOP can be lowered to MOP-20 now | 364 | 400 | None |  | 086868 and GIS are off regarding Route Numbers and Pipe Descriptions. Model has not been updated to include new DR 98 at North end of Airport DFM Extension. Redding Calveras Pressure modeled with flat profile. No Growth was added to the model. | C2-V1 |  | Y | 600 | 120 | 386 | 419 | 61.0544 | 53.3678
116 | ZTR1 | TP_HUMBOLDT | 1309_ALTON_100 | 100 psig DFM served from L177A via the Alton Primary that serves Rio Dell and Scotia | Alton Primary OD082931 V-14, 15, 16, 17 | 4.2 | ZTR1PS701 | ZTR1PCE801 | V1-Meets Plng Guide validation criteria | 100 | Pipeline Engineering is currently exploring raising the MOP of this line to meet the 5/20 analysis, and projected new loads | 94 | 92 | 66 | 70 | 59 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | 4 miles of 4" Replaced with 6" at 250#, upgrade Regs as needed, 4 bores/ bridge hangings. | $5,600,000 | Minimum Design Based on R73 36# Outlet Pressure. 13.9Mcfh Commercial/ Industrial Growth consistent with current RFC. | C4-V1 |  |  | 100 | 66 | 70 | 59 | 90.3614 | 115.5032
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | Gerber Compressor OD284543 V-21, 22 | 126 | PS181, PS176, PS177, PS178, PS100, PS102, PS123, PS194 | PCE38, PCE347, PCE348, PCE356, PCE357, PCE360, PCE361, PCE345, PCE346 | V1-Meets Plng Guide validation criteria | 819 | 819#, 430#, 350#, and 250# | 819 | 819 | 90 | 89 | 215 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | 10miles 12" L177 Reinfocement; Arcata Trans Reg Rebuild, R38, R41, R09 DR Rebuilds | $16,800,000 | Assuming HBGS allowable CWD burn rate of 870 Mcfh remains unchanged. Several Reg Stations undersized for lower inlet pressures. | C4-V1 | Y |  | 819 | 90 | 89 | 215 | 100.027 | 94.2467
118 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_430 | L177A Cummins Creek to Tompkins Hill | Cummins Creek OD082474 V-2, 4, 7, 8 | 15 | PS177 | PCE347, PCE348 | V1-Meets Plng Guide validation criteria | 430 |  | 423 | 422 | 260 | 244 | 347 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 241 | 334 | Investments included in 819# Subsystem Analysis |  | Analysis completed assuming 819# setpoint at Gerber | C4-V1 | Y |  | 430 | 260 | 244 | 347 | 106.8747 | 54.9795
119 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_350 | L177A from Tompkins Hill to Ryan Slough: L126A, L126B, L189, L137B | Tompkins Hill OD183697 V-50, 51, 66, 78 | 45 | PS178, PS100, PS102, PS123, PS194 | PCE356, PCE357, PCE360, PCE361 | V1-Meets Plng Guide validation criteria | 350 |  | 340 | 340 | 130 | 121 | 266 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Investments included in 819# Subsystem Analysis |  | Analysis completed assuming 423# setpoint at Cummins Creek and 819# setpoint at Gerber | C4-V1 | Y |  | 350 | 130 | 121 | 266 | 102.1392 | 49
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 |  | 18 | PS101, PS103, PS104, PS122, PS124, ZTR1PS702 | PCE349, PCE350, PCE351, PCE352, PCE362, PCE363 | V1-Meets Plng Guide validation criteria | 167 |  | 161 | 159 | 90 | 150 | 149 | C2-NOP can be lowered to MOP-20 now | 140 | 138 |  |  | This system currently has excess capacity with Evergreen Pulp off. | C2-V1 | Y |  | 167 | 90 | 150 | 149 | 27.2323 | 28.7432
123 | ZTR1 | TP_HUMBOLDT | L137D_GIUNTOLI_250 | 10" Line from Arcata Reg to Giuntoli | Arcata Reg OD082630 V-26, 27, 30, 31 | 3.1 | PS125 | PCE345, PCE346 | V1-Meets Plng Guide validation criteria | 250 |  | 245 | 233 | 90 | 119 | 223 | C2-NOP can be lowered to MOP-20 now | 118 | 215 |  |  | Analysis completed assuming 350# setpoint at Tompkins Hill, 423# setpoint at Cummins Creek and 819# setpoint at Gerber | C2-V1 |  | Y | 250 | 90 | 119 | 223 | 88.8585 | 23.4761
124 | ZTR1 | TP_HUMBOLDT | 1310/1311_LOLETA_170 | 2 DFM's fed fro Tompkins Hill serving Loleta and Fernbridge | Tompkins Hill OD183697 V-60, 61, 62, 63 | 3.5 | ZTR1PS703, ZTR1PS704 | PCE358, PCE359 | V1-Meets Plng Guide validation criteria | 170 |  | 166 | 160 | 90 | 153 | 160 | C2-NOP can be lowered to MOP-20 now | 132 | 140 |  |  | *High APD min pressure due to low flow and elevation change. | C2-V1 | Y |  | 170 | 90 | 153 | 160 | 26.399 | 15.8654
126 | ZTR1 | TP_HUMBOLDT | 1001_REDBLUFF_470 | Rawson Road DFM serving Red Bluff West, Pactiv, and Neo Power | Red Bluff & Diamond National Primary OD082621 V-4, 5, 6, 7 | 3.4 | PS558 | ZTR1PCE800 | V1-Meets Plng Guide validation criteria | 470 | DWG 086868 lists 1001-02 as 911# MOP, GIS lists this pipe as 1001-01 | 458 | 455 | 110 | 343 | 433 | C2-NOP can be lowered to MOP-20 now | 332 | 425 |  |  |  | C2-V1 |  |  | 470 | 110 | 343 | 433 | 49.4497 | 16.0014
127 | ZTR1 | TP_CHICO | 1027_OROVILLE_110 | Oroville 110# DFM | 5th & Pomona OD0800188 V-8, 9; Lincoln & Oro Dam OD0800187 V-4, 5 | 1.9 | ZTR1PS705, ZTR1PS706 | ZTR1PCE802, ZTR1PCE803 | V1-Meets Plng Guide validation criteria | 110 |  | 105 | 102 | 85 | 96 | 92 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 91 | 87 | 3800ft of 6-in Steel Reinforcement | $900,000 | 1400ft of the 3800ft is on the 2012/13 Investment Plan. Modeling L177A Investments required for model balance. | C3-V1 | Y |  | 110 | 85 | 96 | 92 | 59.159 | 74.5846
128 | ZTR1 | TP_CHICO | 1027_OROVILLE_235 | Oroville 235# DFM | Richvaley Y OD081499 V-28, 30, 32 | 14.3 | ZTR1PS707, ZTR1PS708, ZTR1PS709, ZTR1PS710, ZTR1PS711, ZTR1PS712, ZTR1PS713 | PCE377, PCE378 | V1-Meets Plng Guide validation criteria | 235 |  | 217 | 217 | 140 | 169 | 142 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Required Investments are on L50A Subsystem and L177A Subsystem |  | Analysis assumed Fell Station and Richvale Y winter operations are unavailable due to 5/20 on Sac LT System and extensive Investments have been made on L050A and L177A | C4-V1 | Y |  | 235 | 140 | 169 | 142 | 74.8463 | 98.4168
129 | ZTR1 | TP_CHICO | 1004_ORLAND_490 | Orland 490# DFM from Primary to Secondary | Orland Primary OD082434 V-20, 21, C | 6.2 | PS555, ZTR1PS714 | ZTR1PCE804 | V1-Meets Plng Guide validation criteria | 490 |  | 400 | 387 | 130 | 386 | 385 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 490 | 130 | 386 | 385 | 40.8172 | 41.1626
130 | ZTR1 | TP_CHICO | 1004_ORLAND_170 | Orland 170# DFM from Secondary to Tertiary | Orland Secondary OD0800192 V-3, 4, 5, 6 | 1.6 | PS556 | ZTR1PCE805 | V1-Meets Plng Guide validation criteria | 170 |  | 100 | 100 | 78 | 97 | 95 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 170 | 78 | 97 | 95 | 85.4269 | 87.1099
131 | ZTR1 | TP_CHICO | L209/128_WILLOWS_479 | Manville - Willows - Ordbend 479# Line | Johns Manville Meter & Reg OD085542 V-3, 6, 10, 13 | 17 | ZTR1PS715, ZTR1PS716, ZTR1PS717 | PCE41, PCE42 | V2B-Incomplete validation - results suspect | 479 |  | 455 | 450 | 90 | 153 | 400 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | October Peak Nut Drying Season, No Load file or validation yet completed. | C1-V2B |  |  | 479 | 90 | 153 | 400 | 93.0835 | 31.3729
132 | ZTR1 | TP_CHICO | 1022_ARTOIS_200 | DFM serving Artois from Jacinto (L128) 200# | Jacinto Reg OD082893 V-25, 29, 30, 31 | 3 | ZTR1PS718 | PCE372, PCE373 | V2B-Incomplete validation - results suspect | 200 |  | 175 |  | 80 |  |  | C1-Existing NOP offset is 20 psi or more |  |  |  |  | Partially Built Model is not validated | C1-V2B |  |  | 200 | 80 | 0 | 0 | 119.0476 | 119.0476
133 | ZTR1 | TP_CHICO | 1017_PARADISE_200 | DFM from Paradise Primary to Secondary | Paradise Primary OD0800095 V-R1, R2, R3, R4 | 1.1 | PS557 | PCE806 | V1-Meets Plng Guide validation criteria | 200 |  | 190 | 187 | 150 | 183 | 182 | C2-NOP can be lowered to MOP-20 now | 172 | 171 | See L177A Subsystem |  | Assumes all investments on L177A are completed. | C2-V1 | Y |  | 200 | 150 | 183 | 182 | 37.2057 | 39.2914
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | Gerber Compressor OD284543 V-27, 28; Fell Reg & Oderizer OD082551 V-21, 22, 24, 25; Grape Way OD086447 V-4, 5, 8, 9; Butte Station OD284095 V-8, 9, 10, 11, 16, 17, 18, 19; Richvaley Y OD081499 V-28, 30, 32 | 100 | PS21, PS22, PS121, PS149, PS172, PS173, PS174, PS175, PS179, PS180, PS206, PS207, PS208, PS310, PS544, ZTR1PS719, ZTR1PS721, ZTR1PS722, ZTR1PS723 | PCE39, PCE368, PCE369, PCE376, PCE377, PCE378, PCE49, PCE50, ZTR1PCE807, ZTR1PCE808 | V1-Meets Plng Guide validation criteria | 618 | CROP Reduction from 819# to 618#. CROP may or may not be raised in 2012 depending on Thomes Creek Crossing Replacement. | 618 | 618 | 140 | 148 | 0 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 0 | 19 Miles L177A 16" Parallel from Corning Northdome (MP29.09) to Hamilton City Tap (MP9.88). 3 Miles of L050A 8" Parallel between Butte College Tap (V-37.42) and Richvale Y (MP 27.82). Rebuild Butte L177 Regs to have full opening stand-by run. Rebuild R | $9,700,000 | During current CROP, system relies heavily on support from L169B (Fell) and L050A South (Richvale Y). This analysis did not include any support from L169B or L050A as this may not be available if the 5/20 setpoint offset is implemented on the Sacramento | C4-V1 | Y |  | 618 | 140 | 148 | 0 | 99.3641 | 105.4095
135 | ZTR1 | TP_CHICO | L50_CHICO_400 | L50 from Butte Station to Richvale Y, including L50B to Paradise | Butte Station OD 284095 V-8, 9, 10, 11 | 33 | ZTR1PS723, PS544, PS557 | ZTR1PCE807, ZTR1PCE808 | V1-Meets Plng Guide validation criteria | 400 |  | 390 | 390 | 180 | 172 | 0 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 0 | See L177 Subsystem |  | Butte L136 is normally modeled at 390, L177 is modeled at 384: New Analysis utilizes 380/374. Pmin Design of 180# required for the Oroville 235# system to maintain 140#. Model does not include support from L50A South from Richvale as this support may not | C4-V1 | Y |  | 400 | 180 | 172 | 0 | 102.2069 | 125.3918
138 | ZTR1 | TP_CHICO | 1019_HAM-CITY_250 | DFM serving Prune Dryer south of Hamilton City | Hamilton City Regulator OD082877 V-56, 57, 60, 61 | 2.5 | PS551 | ZTR1PCE813 | V3-Insufficient P data to complete validation | 250 |  | 235 | 230 | 90 | 229 | 230 | C2-NOP can be lowered to MOP-20 now | 224 | 229 |  |  | Modeled 70 Mcfh Summer Prune Drying Load at Verschagin's. Pressure should be recorded at Vershagin's for July 1 - Sep 30 to validate model. | C2-V3 |  |  | 250 | 90 | 229 | 230 | 18.4908 | 17.6471
139 | ZTR1 | TP_REDDING | 1042_MCARTHUR_525 | DFM fed from L400, serving Fall River and McArthur |  | 7.5 | PS554 | ZTR1PCE814 | V3-Insufficient P data to complete validation | 525 | The MAOP is 911-960 psig for all of the pipe segments, not sure what the limiting factor is causing the MOP to be 525 psig. | 485 | 475 | 90 | 247 | 193 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | This DFM is part of the NV_FallRiver_Macarthur_H model. | C1-V3 |  |  | 525 | 90 | 247 | 193 | 80.2228 | 89.1042
140 | ZTR1 | TP_CHICO | 1009_MILLS-ORCHARD_200 | DFM fed from L177A MP9.88 to Mills Orchard and Sunsweet Dryers | Mills Orchard Primary OD0800189 V-2, 4, 5, 7 | 1.9 | ZTR1PS720 | ZTR1PCE815 | V3-Insufficient P data to complete validation | 200 |  | 180 | 170 | 90 | 163 | 170 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | Summer Prune Drying Load. | C1-V3 |  |  | 200 | 90 | 163 | 170 | 42.1034 | 34.7962
142 | HxFe | TP_KERN | HXFEPS702 | Ridgecrest | Ridgecrest Primary Reg Sta | 13.35 | HXFEPS702, HXFEPS706 | PS313 | V1-Meets Plng Guide validation criteria | 400 | GIS | 380 | 380 | 250 | 264 | 213 | C1-Existing NOP offset is 20 psi or more | 264 | 213 |  |  | While this has no immediate impact on customers, it does reduce the capacity for future expansion that is currently being offered to 2 industrial customers. | C1-V1 | Y |  | 400 | 250 | 264 | 213 | 92.6195 | 117.5703
143 | HxFe | TP_KERN | HXFEPS701 | Down Stream of the West End Reg Station | West End | 3.62 | HXEFPS701 | PS294 | V1-Meets Plng Guide validation criteria | 240 | GIS | 230 | 230 | 120 | 226 | 230 | C2-NOP can be lowered to MOP-20 now | 216 | 220 |  |  | While this has no immediate impact on customers, it does reduce the capacity for future expansion that is currently being offered to 2 industrial customers. | C2-V1 |  |  | 240 | 120 | 226 | 230 | 15.1019 | 10.8796
144 | HxFe | TP_KERN | PCE266 | Down Stream of the Trona Tap | Floats off line 300 | 64.65 | PS294, PS313 | PS295 | V1-Meets Plng Guide validation criteria | 700 | GIS | 650 | 650 | 450 | 600 | 578 | C1-Existing NOP offset is 20 psi or more | 600 | 578 |  |  | While this has no immediate impact on customers, it does reduce the capacity for future expansion that is currently being offered to 2 industrial customers. | C1-V1 | Y |  | 700 | 450 | 600 | 578 | 45.2174 | 54.2317
145 | HxFe | TP_KERN | PCE286 | Down Stream of the Lucerne Valley Tap | Floats off line 300 | 38.78 | PS297 | PS297 | V1-Meets Plng Guide validation criteria | 573 | GIS | 453 | 453 | 250 | 490 | 453 | C1-Existing NOP offset is 20 psi or more | 490 | 453 |  |  |  | C1-V1 |  |  | 573 | 250 | 490 | 453 | 33.1901 | 46.3155
146 | HxFe | TP_KERN | PCE296 | Down Stream of the Riverside Reg | Riverside Reg | 19.51 | PS298 | PS299 | V1-Meets Plng Guide validation criteria | 550 | GIS | 435 | 435 | 250 | 423 | 434 | C1-Existing NOP offset is 20 psi or more | 423 | 434 |  |  |  | C1-V1 | Y |  | 550 | 250 | 423 | 434 | 51.4879 | 47.56
147 | HxFe | TP_KERN | HXFEPS703 | Down Stream of the Hinkley Tap | Floats off line 300 | 24.29 | PS298 | PS298 | V1-Meets Plng Guide validation criteria | 861 | GIS | 500 | 500 | 450 | 466 | 500 | C1-Existing NOP offset is 20 psi or more | 466 | 500 |  |  |  | C1-V1 | Y |  | 861 | 450 | 466 | 500 | 97.28 | 91.1845
148 | HxFe | TP_KERN | HXFEPS704 | Pioneer_DFM | Bakersfield Reg Sta | 5.49 | HXFEPS704 | HXFEPCE800 | V1-Meets Plng Guide validation criteria | 240 | GIS | 210 | 210 | 90 | 176 | 163 | C1-Existing NOP offset is 20 psi or more | 176 | 163 |  |  |  | C1-V1 |  |  | 240 | 90 | 176 | 163 | 53.7859 | 62.6889
149 | HxFe | TP_KERN | HXFEPS700 | 142S Down Stream of Brundage & V | Brundage&V AND Bakersfield Reg | 2.53 | PS136 | PS136 | V1-Meets Plng Guide validation criteria | 300 | GIS | 290 | 290 | 200 | 289 | 280 | C2-NOP can be lowered to MOP-20 now | 275 | 270 |  |  |  | C2-V1 | Y |  | 300 | 200 | 289 | 280 | 12.958 | 23.2
150 | HxFe | TP_KERN | PCE419 | 142S Down Stream of Gosford | Gosford Station | 9.29 | PS135 | PS135 | V1-Meets Plng Guide validation criteria | 478 | GIS | 465 | 465 | 220 | 432 | 376 | C2-NOP can be lowered to MOP-20 now | 423 | 361 |  |  |  | C2-V1 | Y |  | 478 | 220 | 432 | 376 | 23.2447 | 48.3708
151 | HxFe | TP_KERN | PCE223 | 142N | Bakersfield Tap | 36.03 | PS134, PS314, PS315, PS316, PS317, PD318, PS319 | PS134 | V1-Meets Plng Guide validation criteria | 475 | GIS | 465 | 465 | 410 | 418 | 420 | C2-NOP can be lowered to MOP-20 now | 408 | 411 |  |  |  | C2-V1 | Y |  | 475 | 410 | 418 | 420 | 88.485 | 85.5715
152 | TCQ2 | TP_EBAY | DFM_2404_85 | 85 psig DFM near Enterprise in Newark - Salt Dryers | Timber Reg Station; RF39 | 3.1 | tcq2PS700 | tcq2PCE801 | V3-Insufficient P data to complete validation | 85 |  | 80 | 80 | 75 | 77.59 | 79.58 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 62.1 | 64.48 | RF03/RF04 Reg stations replumbed with new regs. | $160,000 | Two Distribution Regulator sets at 50 psig replumbed. May consider turning into distribution main. | C3-V3 |  |  | 85 | 75 | 77.59 | 79.58 | 75.2995 | 55.7515
153 | TCQ2 | TP_EBAY | DFM_3010_100 | Wilbur DFM | Wilbur Reg Station | 0.75 | tcq2PS709 | tcq2PCE814 | V3-Insufficient P data to complete validation | 100 |  | 95 | 95 | 85 | 65.47 | 95 | C2-NOP can be lowered to MOP-20 now | 65.47 | 95 |  |  | Pipeline Engineering is working with the only elevated customer on this line to test a 20 psig reduction. Proposal to eliminate regulation from Pipeline Engineering. | C2-V3 |  |  | 100 | 85 | 65.47 | 95 | 205.8983 | 35.1351
154 | TCQ2 | TP_EBAY | SP3_System_600 | Stanpac 3 System from Antioch to Los Medanos | Antioch Terminal - Control Valves | 14.4 | PS636, PS196, PS644 | PCE73, PCE74, PCE75 | V1-Meets Plng Guide validation criteria | 600 |  | 600 | 590 | 430 | 546.36 | 560.71 | C2-NOP can be lowered to MOP-20 now | 541.72 | 559.38 |  |  | Impacts Los Medanos Injection Capability | C2-V1 | Y |  | 600 | 430 | 546.36 | 560.71 | 35.1175 | 26.0447
155 | TCQ2 | TP_EBAY | Line_105_250 | 250 psig Line 105 from Irvington to Enrico Station | Irvington Station | 16 | PS43, PS42, PS41 | PCE163 | V1-Meets Plng Guide validation criteria | 250 |  | 245 | 245 | 160 | 237.95 | 235.14 | C2-NOP can be lowered to MOP-20 now | 222.49 | 219.49 |  |  |  | C2-V1 | Y |  | 250 | 160 | 237.95 | 235.14 | 15.9344 | 19.5371
156 | TCQ2 | TP_EBAY | Line_105B_397 | 397 psig Line 105B Herrmann to San Pablo | Hermann Station - Control Valves | 17.6 | PS38, PS39, PS389, PS390 | PCE332 | V1-Meets Plng Guide validation criteria | 397 | Recent reduction to 397 due to Chevron service downrate to 397 psig | 380 | 380 | 320 | 356.19 | 378.16 | C2-NOP can be lowered to MOP-20 now | 342.01 | 370.21 |  |  | May impact Crocket Cogen and Chevron. Currently set at 380 psig. | C2-V1 | Y | Y | 397 | 320 | 356.19 | 378.16 | 55.6751 | 26.4522
157 | TCQ2 | TP_EBAY | DFM 3004 | Port Costa Feeder from Stanpac 3 | Port Costa Reg Station | 1.2 | PS388 | PCE323, PCE324 | V2B-Incomplete validation - results suspect | 315 |  | 95 | 95 | 80 | 96.31 | 96.29 | C1-Existing NOP offset is 20 psi or more | 96.31 | 96.29 |  |  |  | C1-V2B |  |  | 315 | 80 | 96.31 | 96.29 | 96.9021 | 96.9063
158 | TCQ2 | TP_EBAY | Line_105_150 | 150 psig Oakland System | Fairway Station, Enrico Station, East Bay PLS (All Control Valves) | 47 | PS40, PS44, PS148, PS37, PS391 | PCE325, PCE326, PCE327, tcq2PCE800 | V1-Meets Plng Guide validation criteria | 121 | Currently under a TROP of 121 psig since December 2011. | 121 | 145 | 90 | 115.85 | 116.92 | C2-NOP can be lowered to MOP-20 now | 112.74 | 113.44 |  |  | Berkeley Cogen, California Oils Cogen, NCPA Cogen might be impacted due to lower than normal delivery pressure | C2-V1 | Y |  | 121 | 90 | 115.85 | 116.92 | 18.6482 | 14.8404
159 | TCQ2 | TP_EBAY | DFM_0141-01_110 | C&H Sugar DFM | Crockett Station | 23.2 | tcq2PS705 | PCE319, PCE320 | V3-Insufficient P data to complete validation | 110 |  | 100 | 100 | 90 | 89.97 | 90.02 | C1-Existing NOP offset is 20 psi or more | 89.97 | 90.02 |  |  |  | C1-V3 | Y |  | 110 | 90 | 89.97 | 90.02 | 100.135 | 99.91
160 | TCQ2 | TP_EBAY | Line_153_336 | 336 psig Line 153 from Irvington to Marina Station | Irvington Station | 18 | PS145, PS393, PS147 | PCE163, PCE165, PCE166, PCE167 | V1-Meets Plng Guide validation criteria | 336 | Current under a CROP. Reduced 20% from old 420 psig MAOP | 335 | 306 | 275 | 214.23 | 204.34 | C1-Existing NOP offset is 20 psi or more | 227.24 | 215.53 |  |  | Line under a 20% crop. New Russell City Power Plant may push for restoration of previous MAOP | C1-V1 | Y |  | 336 | 275 | 214.23 | 204.34 | 179.7685 | 190.8754
161 | TCQ2 | TP_EBAY | Line_153_246 | 246 psig Line 153 from Marina Station to the Oakland PLS | Marina Station | 10 | PS145 | PCE328 | V1-Meets Plng Guide validation criteria | 246 |  | 235 | 235 | 180 | 160.14 | 153.1 | C2-NOP can be lowered to MOP-20 now | 165.03 | 154.99 |  |  |  | C2-V1 | Y | Y | 246 | 180 | 160.14 | 153.1 | 124.0261 | 131.8694
162 | TCQ2 | TP_EBAY | Line 191-1_268 | Line 191-1 from C Street to Plaza station (pipe continues to Reliez station) | C Street Station, Martinez | 10.5 | PS201, PS202, PS203, PS204, PS205 | tcq2PCE806 | V1-Meets Plng Guide validation criteria | 268 |  | 258 | 258 | 190 | 177.27 | 176.38 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 233.1 | 224.75 |  | TBD |  | C3-V1 | Y | Y | 268 | 190 | 177.27 | 176.38 | 113.0874 | 113.9685
163 | TCQ2 | TP_EBAY | DFM_2402_01 | 150 psig Castro Valley DFM | C Street Station | 3.87 | PS392 | tcq2PCE804 | V1-Meets Plng Guide validation criteria | 160 | MAOP sheet says segments qualified for 250 psig. Segment may be U/S of regulation. | 155 | 155 | 90 | 126 | 114 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 106.55 | 85.38 | Replace RH12 with larger regulation | $80,000 | May not even need this job as 85 psig may be sufficient due to networked distribution. | C3-V1 |  |  | 160 | 90 | 126 | 114 | 55.5657 | 72.0229
164 | TCQ2 | TP_EBAY | DFM_2403_125 | 125 psig Niles DFM from Decoto to Mowry | Niles Reg Station, RF38 | 4 | tcq2PS701 | tcq2PCE802 | V1-Meets Plng Guide validation criteria | 125 |  | 120 | 120 | 90 | 96.38 | 97.03 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 77.57 | 78.37 |  | See Note | Current 2013 Uprate job will resolve this issue. | C4-V1 |  |  | 125 | 90 | 96.38 | 97.03 | 84.1979 | 82.5273
165 | TCQ2 | TP_EBAY | DFM_3001-01_170 | Moraga DFM 3001-01 | Reliez Station | 4.15 | tcq2PS706 | PCE315, PCE316 | V1-Meets Plng Guide validation criteria | 170 |  | 170 | 165 | 90 | 113.02 | 51.79 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 88 | 34.04 |  | See Note | Current 2013 Reinforcement Job will resolve this issue | C4-V1 |  |  | 170 | 90 | 113.02 | 51.79 | 77.5312 | 126.0471
166 | TCQ2 | TP_EBAY | DFM_3002_170 | Glorietta DFM | Reliez Station | 7.18 | PS201, tcq2PS2707 | PCE313, PCE314 | V1-Meets Plng Guide validation criteria | 182 | Line 191S is part of this DFM from Plaza Station to Reliez Station | 177 | 177 | 90 | 107.08 | 75.37 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 109.87 | 56.77 |  | TBD |  | C4-V1 | Y |  | 182 | 90 | 107.08 | 75.37 | 86.5484 | 109.6682
167 | TCQ2 | TP_EBAY | DFM_3006/3008_170 | Concord DFM | Vine Hill Station, Concord Meter Station | 13.67 | PS379, tcq2PS708 | PCE317, PCE318, PCE309, PCE310 | V1-Meets Plng Guide validation criteria | 170 |  | 165 | 165 | 90 | 107.24 | 100.12 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 102.3 | 93.54 |  | TBD |  | C4-V1 |  |  | 170 | 90 | 107.24 | 100.12 | 83.6518 | 90.7499
168 | TCQ2 | TP_EBAY | DFM_3004-01_338 | Foster Wheeler Cogen DFM | Foster Wheeler Meter Station off of SP3 | 0.98 | PS383 | PCE311, PCE312 | V2B-Incomplete validation - results suspect | 338 |  | 320 | 320 | 300 | 312.16 | 320.01 | C2-NOP can be lowered to MOP-20 now | 310.11 | 318.01 |  |  | LC Delivery pressure impact: Foster Wheeler Cogen. Currently at 320 psig delivery pressure | C2-V2B |  |  | 338 | 300 | 312.16 | 320.01 | 69.2961 | 48.8269
169 | TCQ2 | TP_EBAY | DFM_3010-01_338 | Antioch Vierra DFM - Can be tied to Line 191_338 psig system | Antioch/Vierra Reg station | 0.68 | PS387 | tcq2PCE809 | V3-Insufficient P data to complete validation | 338 |  | 320 | 320 | 130 | 320 | 320.16 | C2-NOP can be lowered to MOP-20 now | 318 | 318.16 |  |  | Pipeline is proposing absorbing DFM_3010_100 into this system. | C2-V3 | Y |  | 338 | 130 | 320 | 320.16 | 12.1672 | 12.0619
170 | TCQ2 | TP_EBAY | DFM_3012_172 | Dow Chemical and USS DFM | Pittsburg Town Station | 2.18 | PS711, PS710 | tcq2PCE815 | V1-Meets Plng Guide validation criteria | 172 |  | 165 | 165 | 100 | 162.74 | 165.08 | C2-NOP can be lowered to MOP-20 now | 147.51 | 150.07 |  |  |  | C2-V1 |  |  | 172 | 100 | 162.74 | 165.08 | 15.8277 | 11.9107
171 | TCQ2 | TP_EBAY | DFM_3014-01_338 | Nichols DFM Tapped off of SP3 | Nichols Reg Station | 1.56 | PS384 | tcq2PCE810 | V3-Insufficient P data to complete validation | 338 |  | 255 | 255 | 100 | 257.6 | 257.6 | C1-Existing NOP offset is 20 psi or more | 237.38 | 237.38 |  |  |  | C1-V3 | Y |  | 338 | 100 | 257.6 | 257.6 | 45.9367 | 45.9367
172 | TCQ2 | TP_EBAY | DFM_3019_275 | Rhodia_DFM | Shell Reg Station DIRC29 | 1.03 | tcq2PS712 | tcq2PCE816 | V3-Insufficient P data to complete validation | 95 |  | 90 | 90 | 90 | 90.05 | 90.15 | C2-NOP can be lowered to MOP-20 now | 90.05 | 90.15 |  |  | Potential LC pressure impact: Rhodia | C2-V3 |  |  | 95 | 90 | 90.05 | 90.15 | 99.0268 | 97.0786
173 | TCQ2 | TP_EBAY | Line SP3_405 | Stanpac 3 from Los Medanos PLS to Franklin Canyon PLS | Los Medanos PLS - Control Valves | 15 | PS637, PS645 | PCE90, PCE91 | V1-Meets Plng Guide validation criteria | 405 |  | 395 | 395 | 380 | 367.11 | 379.52 | C2-NOP can be lowered to MOP-20 now | 357.38 | 373.27 |  |  | Large Customer Pressure Impacts: Chevron Refinery | C2-V1 |  | Y | 405 | 380 | 367.11 | 379.52 | 149.0713 | 101.8577
174 | TCQ2 | TP_EBAY | Line SP3_380 | 380 psig Stanpac 3 from Franklin Canyon to San Pablo Station | Franklin Canyon PLS | 9.4 | PS638, PS639 | PCE321, PCE322 | V1-Meets Plng Guide validation criteria | 380 |  | 370 | 360 | 320 | 360.87 | 360.94 | C2-NOP can be lowered to MOP-20 now | 357.01 | 360.94 |  |  | Not currently used, but will be backup service for Chevron | C2-V1 |  |  | 380 | 320 | 360.87 | 360.94 | 33.7449 | 33.6246
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | Antioch Terminal and SP3/191 Crosstie (control valves) | 34.2 | PS197, PS198, PS199, PS643, PS200, PS385 | PCE81, PCE84, PCE94, PCE95, PCE96 | V1-Meets Plng Guide validation criteria | 338 |  | 335 | 335 | 90 | 195.33 | 90 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 137.8 | 90 | Parallel/Replace 2 miles of Danville DFM | $5,280,000 | Large reinforcement necessary due to reductions on three separate interelated subsystems. Everything comes back to Danvile DFM | C4-V1 | Y |  | 338 | 90 | 195.33 | 90 | 71.6858 | 100
176 | TCQ2 | TP_EBAY | DFM_2408-01 | Stanley DFM in Pleasanton | Isabel Staiton/ Santa Rita Station | 8.83 | PS396 | PCE329, PCE330 | V1-Meets Plng Guide validation criteria | 160 |  | 155 | 155 | 90 | 139.83 | 136.82 | C2-NOP can be lowered to MOP-20 now | 123.14 | 119.75 |  |  |  | C2-V1 | Y |  | 160 | 90 | 139.83 | 136.82 | 34.5575 | 39.3159
177 | TCQ2 | TP_EBAY | DFM_2408-05_497 | Dublin and Blackhawk DFM's | Bay Area Loop - Control Valves | 17.22 | PS397, PS399 | PCE329 | V1-Meets Plng Guide validation criteria | 497 | MOP depends on Line 131/114 MOP (Bay Area Loop) | 400 | 400 | 90 | 264.16 | 163.52 | C1-Existing NOP offset is 20 psi or more | 264.19 | 163.59 |  |  | Floats off Line 131. Always 20 psig under MAOP | C1-V1 |  |  | 497 | 90 | 264.16 | 163.52 | 74.1824 | 92.1984
178 | TCQ2 | TP_EBAY | DFM_2805-05_215 | San Ramon DFM | Altimrano/Arnold reg station | 7.92 | PS398 | tcq2PCE808 | V1-Meets Plng Guide validation criteria | 215 |  | 210 | 210 | 90 | 152.88 | 147.9 | C2-NOP can be lowered to MOP-20 now | 132.45 | 126.84 |  |  |  | C2-V1 |  |  | 215 | 90 | 152.88 | 147.9 | 59.9415 | 63.8704
179 | TCQ2 | TP_EBAY | DFM_2403_240 | 240 psig Isabel DFM 2403-02 and 2403-01 | Smith Reg Station, RF-41 | 3.71 | tcq2PS702 | tcq2PCE803 | V2B-Incomplete validation - results suspect | 240 |  | 220 | 220 | 90 | 211.35 | 207.73 | C1-Existing NOP offset is 20 psi or more | 211.35 | 208.03 |  |  |  | C1-V2B |  |  | 240 | 90 | 211.35 | 207.73 | 26.1236 | 29.1884
180 | TCQ2 | TP_EBAY | DFM 0107.02 | 160 psig Coral/Tunis DFM (near Oakland Airport) | Coral and Tunis Regulator Station | 0.75 | tcq2PS703 | tcq2PCE805 | V2B-Incomplete validation - results suspect | 160 |  | 155 | 155 | 90 | 145.14 | 141.72 | C2-NOP can be lowered to MOP-20 now | 129.08 | 125.26 |  | See Note | Validation Data required. | C2-V2B | Y |  | 160 | 90 | 145.14 | 141.72 | 25.9107 | 31.5168
181 | TCQ2 | TP_EBAY | DFM_CCPP | Contra Costa Power Plant DFM | Antioch Terminal valves 155, 156, 157, 173 | 1 | tcq2PS704 | PCE82, PCE83 | V3-Insufficient P data to complete validation | 195 |  | 180 | 180 | 155 | 180 | 160 | C2-NOP can be lowered to MOP-20 now | 175 | 155 |  | See Note | LC Delivery Pressure impact. Genon PP DFM is currently 15 psig below MOP. Under high demand (6 Mmcfh) Lo Lo alarms will be breached. | C2-V3 |  |  | 195 | 155 | 180 | 160 | 40.1786 | 88.75
182 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY |  |  | PS93, PS168, PS583, PS586, PS582, PS85, PS85, PS563 | PCE404, DRJ4PCE820 | V2B-Incomplete validation - results suspect | 500 |  | 493 | 490 | 90 |  | 452 | C2-NOP can be lowered to MOP-20 now |  | 437 | none |  | DRJ4: This analysis only looks at a lateral off of the L123_L173_500, and should be treated as part of that analysis. Therefore, the pressure should NOT be reduced until further analysis. | C2-V2B | Y |  | 500 | 90 | 0 | 452 | 103.3485 | 18.8905
183 | MUMY | TP_SACRAMENTO_VALLEY | 0605_GALT_395 | Galt Primary Reg Sta (PCE) and Thornton Reg Sta (PCE) to the town of Galt at the inlet to DR R_SCSTA_B07. |  | 9.54 | PS571 | DRJE802, DRJ4PCE803 | V1-Meets Plng Guide validation criteria | 395 | The Galt DFM is supplied by two regulator stations, Galt Primary at 360 psig and Thornton Meter Station at 355 psig | 360 | 360 | 90 | 250 | 165 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | CWD was Res Pmin 110% was estimated and not modeled. | C1-V1 |  |  | 395 | 90 | 250 | 165 | 63.2246 | 87.0712
184 | MUMY | TP_SACRAMENTO_VALLEY | 0606_ELK_GROVE_150 | Elk Grove Emergency Backfeed Sta (PCE) to the inlet to DR R_SRSTA-B17. |  | 12.55 | drj4PS701 | DRJ4PCE804 | V1-Meets Plng Guide validation criteria | 150 |  | 145 | 145 | 80 | 133 | 127 | C2-NOP can be lowered to MOP-20 now | 116 | 112 |  |  |  | C2-V1 |  |  | 150 | 80 | 133 | 127 | 29.882 | 39.5714
185 | MUMY | TP_SACRAMENTO_VALLEY | 0609_FLORIN_150 | Florin Rd & Munson Way Reg Sta (PCE) to DFM 0609. |  | 2.03 | drj4PS702 | DRJ4PCE808 | V1-Meets Plng Guide validation criteria | 150 |  | 147 | 147 | 90 | 98 | 74 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V1 |  |  | 150 | 90 | 98 | 74 | 89.5556 | 118.2222
186 | MUMY | TP_SACRAMENTO_VALLEY | 0611_MATHER_240 | 20th Av & Martin Luther King Jr Blvd Reg Sta (PCE) to Blue Ravine Reg Station in Folsom - Mather DFM system serving south Sacramento and Rancho Cordova. The Pmin Design Shown is in Folsom at DR R_SCSTA-51 which receives backfeed support from the Folsom D |  | 44.74 | drj4PS703 | DRJ4PCE809 | V1-Meets Plng Guide validation criteria | 240 |  | 235 | 233 | 90 |  |  | C2-NOP can be lowered to MOP-20 now |  |  |  |  | DRJ: Has a backfeed from Folsom DFM, and Folsom DFM is not constrained. Need a pressure recorder at the end of the Douglas-Sunrise DFM to Validate | C2-V1 |  |  | 240 | 90 | 0 | 0 | 116.3636 | 116.3636
187 | MUMY | TP_SACRAMENTO_VALLEY | 0613_SAC_FLOATER_260 | Sacramento Gas Load Center (PCE) to North Sacramento Holder and North Sacramento 180 psig DFM. Provides the lead supply to the DFM to a secondary backup supply off of L119B/C. The North Sacramento Holder is operated during winter season morning peak hou |  | 6.24 | PS565 | PCE393, PCE394 | V3-Insufficient P data to complete validation | 260 |  | 250 | 250 | 90 | 195 | 165 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V3 |  |  | 260 | 90 | 195 | 165 | 49.7059 | 67.8571
188 | MUMY | TP_SACRAMENTO_VALLEY | 0615_SAC_METRO_425 | El Centro Rd & Hwy 80 Reg Sta (PCE) to the Sacramento Metropolitan Airport. |  | 6.79 | drj4PS704 | DRJ4PCE801 | V1-Meets Plng Guide validation criteria | 425 |  | 410 | 390 | 90 | 275 | 246 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 |  |  | 425 | 90 | 275 | 246 | 60.8607 | 69.6183
189 | MUMY | TP_SACRAMENTO_VALLEY | 0617_KIRBY_150 | Roseville Rd Reg Sta (PCE) to the inlet to DR R_SCSTA-A37. |  | 0.97 | drj4PS705 | PCE389 | V3-Insufficient P data to complete validation | 150 |  | 145 | 145 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V3 |  |  | 150 | 90 | 0 | 0 | 156.25 | 156.25
190 | MUMY | TP_SACRAMENTO_VALLEY | 0618_ANTELOPE_WALERGA_175 | Antelope Meter Sta (PCE) to Antelope at the inlet to DR . |  | 2.94 | drj4PS706 | PCE381,PCE382 | V3-Insufficient P data to complete validation | 175 |  | 170 | 170 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V3 |  |  | 175 | 90 | 0 | 0 | 135.96 | 135.96
191 | ANY3 | TP_SACRAMENTO_VALLEY | 0619_SOUTH_RIVER_150 | 0619-01: 150# (South River) Included in distribution model: ESDZONE_SA_WEST_SAC_H_W1112_APD_452_(MOP_MINUS_20_STUDY) |  | 1.21 | drj4PS707 | DRJ4PCE810 | V3-Insufficient P data to complete validation | 150 |  | 147 | 145 | 80 |  | 137 | C2-NOP can be lowered to MOP-20 now |  | 115 | none |  | SOURCE REG: WS-012 - System Configuration may change due to potential WRO relocation of 6" DFM ("Raley Landing" project). DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. | C2-V3 |  |  | 150 | 80 | 0 | 137 | 139.7516 | 23.1739
192 | ANY3 | TP_SACRAMENTO_VALLEY | 0621_ARMFIELD_190 | 0621-01: 190# (Teichert Modeled) Included in distribution model: ESDZONE_SA_WOODLAND_HL_W1112_CFD_452_(w_Teichert)_(MOP_MINUS_20_STUDY) |  | 0.96 | drj4PS708 | DRJ4PCE811 | V3-Insufficient P data to complete validation | 190 |  | 180 | 180 | 80 |  | 131 | C2-NOP can be lowered to MOP-20 now | 117 |  | none |  | SOURCE REG: WO-16; CFD is controlling season. DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. Pac Coast Prod. Load was modified from LCSea from 900 mcfh to 600 mcfh to align better with AMR usage (60 psig delivery pressure). | C2-V3 |  |  | 190 | 80 | 0 | 131 | 121.5488 | 63.7677
193 | ANY3 | TP_SACRAMENTO_VALLEY | 0627_UCDAVIS_175 | 0627-01: 175# Davis Meter and Reg Sta (PCE) to UC Davis Campus at the inlet to DR R_SCDA-001. (AFTER 1st & A St MWC 47 job) Included in distribution model: ESDZONE_SA_DAVIS_H_W1112_CWD_452_(MOP_MINUS_20_STUDY)_1st_&_A_St_Upgrade) |  | 0.7 | drj4PS709 | PCE384, PCE385 | V3-Insufficient P data to complete validation | 175 |  | 170 | 168 | 85 | 133 |  | C2-NOP can be lowered to MOP-20 now | 113 |  | none |  | DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. SOURCE REG: DA-11; CWD is the controlling season Should validate system performance once PM 30882075 is constructed which will remove bottleneck and increase utilization out of DA- | C2-V3 |  |  | 175 | 85 | 133 | 0 | 55.2821 | 130.8761
194 | LRS3 | TP_SACRAMENTO_VALLEY | 0630_COLUSA_MERIDIAN_240 | Lurline Rd Sta (PCE) to closed MAOP sdeparation valve V-5. Serves the town of Colusa and Sunsweet Driers. The Pmin Design shown is in Colusa at the inlet to DR R_SCC008 (55 psig Distr system). Lurline DFM Included in distribution model: 07-J07colusaAS |  | 4.2 | PS593 | DRJ4PCE812 | V2B-Incomplete validation - results suspect | 240 |  | 223 | 220 | 85 |  | 99 | C2-NOP can be lowered to MOP-20 now |  | 93 | none |  | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. Min pressure is at node where future added load is applied near the end of the dfm | C2-V2B | Y |  | 240 | 85 | 0 | 99 | 114.3424 | 94.8864
195 | LRS3 | TP_SACRAMENTO_VALLEY | 0630_COLUSA_MERIDIAN_430 | Marysville Buttes Sta (PCE) to closed MAOP separation valve V-5. Colusa DFM Included in distribution model: 07-J07colusaASD_UTM_Qrc+20%+Noncore_452_MOP_MINUS_20_STUDY.MDB |  | 12.86 | drj4PS710 | DRJ4PCE813 | V2B-Incomplete validation - results suspect | 430 |  | 385 | 375 | 90 |  | 348 | C2-NOP can be lowered to MOP-20 now |  | 315 | none |  | DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. The station feeding butte station reg is operated by Meridian | C2-V2B |  |  | 430 | 90 | 0 | 348 | 104.5814 | 36.0837
196 | LRS3 | TP_SACRAMENTO_VALLEY | 0632_WILLIAMS_180 | Williams Primary (PCE) to the town of Williams DR R_FM_SCWL04. Williams DFM Included in distribution model: 11-J11WILLIAMSCFD_UTM_45_MOP_MINUS_20_STUDY |  | 3.72 | PS597 | DRJ4PCE815 | V3-Insufficient P data to complete validation | 180 |  | 175 | 174 | 80 |  | 61 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 80 | 4,200 ft of 6" pipe starting at source | $2,646,000 | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. Rice loads in fall are constraining loads. Construction costs of $630/ft based on highly congested cost provided by Gas Construction Cost Guide Rev 4/16/2012 provided by GPS | C4-V3 |  |  | 180 | 80 | 0 | 61 | 124.6154 | 110.3038
197 | MUMY | TP_SACRAMENTO_VALLEY | 0635_WALNUT_GROWER_210 | West Beehive Bend Reg Sta (PCE) |  | 1.16 | drj4PS711 | DRJ4PCE824 | V3-Insufficient P data to complete validation | 210 |  | 200 | 200 | 90 | [8 empty] | V3 |  |  | 210 | 90 | 0 | 0 | 122.5 | 122.5
198 | LRS3 | TP_SACRAMENTO_VALLEY | 124C-1_BEALE_AFB_395 | Camp Far West Meter Sta (PCE) to Beale Air Force Base. Beale DFM Included in distribution model: ESDZONE_08-J08wheatbelAPD_UTM_45_MOP_MINUS_20_STUDY |  | 4.48 | PS97 | PCE402, PCE403 | V3-Insufficient P data to complete validation | 395 |  | 375 | 372 | 90 |  | 364 | C1-Existing NOP offset is 20 psi or more |  | 364 | none |  | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. Already operating at MOP-20# | C1-V3 |  |  | 395 | 90 | 0 | 364 | 105.4757 | 15.906
199 | LRS3 | TP_SACRAMENTO_VALLEY | 1502_DIST10_120 | Magnolia Rd Sta (PCE) to DFM 1502. District 10 DFM north of Magnolia Rd Reg Station Included in distribution model: 10-J10mryASD_UTM_45_MOP_MINUS_20_STUDY |  | 5.11 | drj4PS713 | DRJ4PCE817 | V2B-Incomplete validation - results suspect | 120 |  | 115 | 112 | 70 |  | 74 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 70 | 2,400 ft of 6" pipe starting at source | $1,512,000 | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. 51# at end of DFM w/o reinf. Pmin = 70 for rice drier cust reg sets at end of DFM. Construction costs of $630/ft based on highly congested cost provided by Gas Construction Cost | C4-V2B | Y |  | 120 | 70 | 0 | 74 | 151.5789 | 93.9368
200 | LRS3 | TP_SACRAMENTO_VALLEY | 1504_NICOLAUS_274 | Lincoln Jct (PCE) to the town of Lincoln DR R_SRSTA-602 and R_SRSTA-603. Lincoln DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY |  | 2.53 | PS579 | PCE405, PCE406 | V1-Meets Plng Guide validation criteria | 274 |  | 250 | 247 | 80 |  | 229 | C1-Existing NOP offset is 20 psi or more |  |  | none |  | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. Already operating at MOP-20#. Sierra & Sac models merged. Preesure points in dstr system to force balance does not effect this DFM capacity/pressures. | C1-V1 |  |  | 274 | 80 | 0 | 229 | 109.3191 | 32.9591
201 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L124B_1502_400 | Yuba City Holder (PCE) to Lincoln Jct - 400 psig system serving Marysville and subsystem 1504_NICOLAUS_274. The Pmin Design shown is in Lincoln at the inlet to Lincoln Jct. |  | 39.85 | PS18, PS95, PS575 | DRJ4PCE806 | V1-Meets Plng Guide validation criteria | 400 |  | 395 | 395 | 250 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V1 |  |  | 400 | 250 | 0 | 0 | 164.1026 | 164.1026
202 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L151_250 | Gridley Jct (PCE) to Richvale Y and Yuba City Holder (PCE). Yuba City Holder is normally set as a secondary supply and not flowing into L050A. A CROP in place on L151, which is part of the subsystem, requires operating the subsystem in two HIS - Gridley |  | 51.66 | PS19, PS20, PS144, PS581 | PCE370, PCE371, PCE376 | V1-Meets Plng Guide validation criteria | 210 | A CROP is in place reducing the MOP from 250 psig to 210 psig, with the regulators set at 190 psig due to creep. | 190 | 190 | 90 |  |  | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 210 | 90 | 0 | 0 | 122.5 | 122.5
203 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVN_412 | Las Vinas Sta (PCE) to BTU MLV 66.14. Serves South Sacramento. The Pmin Design shown is in South Sacramento at the inlet to DR R_SCSTA-B39 and DR R_SCSTA-B37. |  | 41.16 | PS52, PS53, PS54 | PCE61, PCE62 | V1-Meets Plng Guide validation criteria | 400 | A CROP is currently in place reducing the MOP from 410 to 400 psig. This is not expected to be cleared before the winter season. | 385 | 385 | 90 |  |  | C2-NOP can be lowered to MOP-20 now | [5 empty] | C2-V1 | Y |  | 400 | 90 | 0 | 0 | 105.3325 | 105.3325
204 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVS_412 | Las Vinas Sta (PCE) to 8-mile Rd PLS (PCE). Supplies Turner Rd Sta and NCPA-Lodi. The Pmin Design shown is at Armstrong Rd at the inlet to DR R_LOHP77. |  | 10.3 | PS51 | PCE61, PCE62 | V1-Meets Plng Guide validation criteria | 400 | A CROP is currently in place reducing the MOP from 410 to 400 psig. This is not expected to be cleared before the winter season. | 385 | 385 | 90 |  |  | C2-NOP can be lowered to MOP-20 now | [5 empty] | C2-V1 | Y |  | 400 | 90 | 0 | 0 | 105.3325 | 105.3325
205 | MUMY | TP_SACRAMENTO_VALLEY | L108_SGLC_412 | Sacramento Gas Load Center (PCE) to closed BTU Separation valve V-66.14. Supplies South Sacramento area and subsystem 0611_MATHER_240. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609- |  | 15 | PS54 | PCE395, PCE396, PCE397 | V1-Meets Plng Guide validation criteria | 410 | MOP was lowered from 412 psig (MAOP) to 410 psig MOP per validation test that was done on L-108 (MP-61.66 Elk Grove Station to MP-74.50 Sac Load Center) on 1/8/09. | 385 | 385 | 180 |  |  | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 410 | 180 | 0 | 0 | 123.8762 | 123.8762
206 | MUMY | TP_SACRAMENTO_VALLEY | L116_L119A_720 | Swingel Jct (PCE) to Sacramento Gas Load Center and North Sacramento Holder. Supplies North Natomas area, North Sacramento and subsystems L119B_L119C_0617_FOLSOM_500, 0613_SAC_FLOATER_260, L119D_0614_NSAC_180, and 0615_SAC_METRO_425. The Pmin Design show |  | 31.98 | PS82, PS83, PS68, PS70, PS71, PS72, PS166 | PCE398, PCE399 | V1-Meets Plng Guide validation criteria | 720 | A CROP at 533 psig is in place, but is scheduled to be cleared through a Validation Dig or replacement the week of 4/16. | 710 | 700 | 90 |  |  | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 720 | 90 | 0 | 0 | 101.5873 | 101.5873
207 | BHH2 | TP_SACRAMENTO_VALLEY | L119D_0614_NSAC_180 | North Sacramento Holder Sta (PCE) to DFM 0614. The North Sacramento Underground Holder storage is manually operated during winter season mornning hours to take over supplying the DFM at 180 psig. |  | 34.75 | PS86, PS562 | PCE407, PCE408, PCE409 | V3-Insufficient P data to complete validation | 180 |  | 180 | 180 | 80 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V3 |  |  | 180 | 80 | 0 | 0 | 124.6154 | 124.6154
208 | MUMY | TP_SACRAMENTO_VALLEY | L121_485 | Marysville Buttes Sta (PCE) to Yuba City Holder Sta (PCE). Yuba City Holder Sta provides backup supply into L121 at 420 psig when the Yuba City Cogen comes on-line to maintain an elevated delivery service pressure of 375 psig at the meter. |  | 17.34 | PS89, PS90, PS91, PS92, PS580 | DRJ4PCE814 | V3-Insufficient P data to complete validation | 485 |  | 478 | 465 | 90 |  |  | C2-NOP can be lowered to MOP-20 now | [5 empty] | C2-V3 | Y |  | 485 | 90 | 0 | 0 | 103.5663 | 103.5663
209 | MUMY | TP_SACRAMENTO_VALLEY | L123_L173_500, L119B_L119C_0617_FOLSOM_500 | Lincoln Junction (PCE) to North Sacramento Underground Holder (PCE) 500 psig system serving Auburn and El Dorado Hills. These two subsystems have the same MAOP and operate as a single system under Design Day conditions across L123 Open BTU MLV 3.42 at Ba |  | 118.5 | PS93, PS168, PS583, PS586, PS582, PS85, PS85, PS563 | PCE404, DRJ4PCE820 | V1-Meets Plng Guide validation criteria | 500 |  | 495 | 495 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V1 | Y |  | 500 | 90 | 0 | 0 | 103.3485 | 103.3485
210 | MUMY | TP_SACRAMENTO_VALLEY | L124A_L202_1511_600 | Yuba City Holder (PCE) to Lincoln Jct - 600 psig system serving Grass Valley and subsystem L123_L173_500. The Pmin design shown is in Grass Valley at DR R_SRSTA-112. |  | 67.32 | PS94, PS227, PS576, PS584 | PCE413 | V1-Meets Plng Guide validation criteria | 600 | SCADA sensing line is downstream of regulators and record a lower pressure out of the station than at the regulators. | 595 | 591 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V1 | Y |  | 600 | 90 | 0 | 0 | 102.3018 | 102.3018
211 | MUMY | TP_SACRAMENTO_VALLEY | L150_0626_0600_125 | Pleasant Creek Line 159 Reg Sta (PCE) to Davis at the inlet to DR R_SCSTA-D13. |  | 20.16 | PS142 | PCE379, PCE380 | V3-Insufficient P data to complete validation | 125 |  | 120 | 120 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V3 | Y |  | 125 | 90 | 0 | 0 | 207.6412 | 207.6412
212 | MUMY | TP_SACRAMENTO_VALLEY | L172A_500 | Swingle Jct (PCE) to Sacramento Gas Load Center. Supplies West Sacramento and subsystem L108_SGLC_412. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609-02. |  | 13.81 | PS164 | PCE400, PCE401 | V1-Meets Plng Guide validation criteria | 500 |  | 495 | 495 | 180 |  |  | C2-NOP can be lowered to MOP-20 now | [5 empty] | C2-V1 | Y |  | 500 | 180 | 0 | 0 | 114.8897 | 114.8897
213 | MUMY | TP_SACRAMENTO_VALLEY | L172A_N_L169_L167_800 | Hershey Jct North (PCE) to Fell Station and Yuba City Holder. Receives withdrawal gas from Wild Goose Storage Field (PCE) and local California Production in the Willows Field area. The Pmin Design shown is in Grass Valley at the inlet to DR R_SRSTA-112 |  | 142.78 | PS163, PS162, PS157, PS158, PS159, PS160, PS596 | PCE51, PCE54 | V1-Meets Plng Guide validation criteria | 800 | A CROP at 733 psig is currently in place but scheduled to be cleared the week of 4/23. Another CROP at 750 psig is currently in place on 8" L167-1, but may be cleared by records soon. | 798 | 798 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  |  |  | A CROP further reducing the MOP to 708 psig due to SSAW seam is pending. | C4-V1 | Y |  | 800 | 90 | 0 | 0 | 101.2818 | 101.2818
214 | MUMY | TP_SACRAMENTO_VALLEY | L172A_S_800 | Hershey Jct (PCE) and Yolo Jct (PCE) to L172-220 Xtie and Swingle Jct. The Pmin Design shown is in Davis at the inlet to Swingle Jct. |  | 42.72 | PS163 | PCE43, PCE44, PCE45, PCE52 | V1-Meets Plng Guide validation criteria | 800 |  | 798 | 798 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V1 | Y |  | 800 | 90 | 0 | 0 | 101.2818 | 101.2818
215 | MUMY | TP_SACRAMENTO_VALLEY | L195_L196_L200_L210B_800 | Creed Sta (PCE) to Las Vinas Sta. The Pmin Design shown is in South Sacramento at the inlet to DR R_SCSTA-B37 and DR R_SCSTA-B05. |  | 53.35 | PS210, PS214, PS215, PS222, PS235 | PCE56 | V1-Meets Plng Guide validation criteria | 658 | A CROP is in effect reducing the MOP from 800 to 686 psig and is not expected to be cleared before the winter season. | 635 | 632 | 90 |  |  | C2-NOP can be lowered to MOP-20 now |  |  |  |  | A CROP - UP is pending final authorization restoring the MOP to 792 psig. | C2-V1 | Y |  | 658 | 90 | 0 | 0 | 101.9065 | 101.9065
216 | MUMY | TP_SACRAMENTO_VALLEY | L197_1614_TURNER_300 | Las Vinas Sta (PCE) and Turner Rd Sta (PCE) to Lodi, Ione and Valley Springs. The Pmin Design shown is in Ione at the inlet to DR R_LOHP24 and in Sutter at the inlet to DR MARHP-01. General Mills has a Pmin requirement for an elevated delivery service pr |  | 93.36 | PS216, PS217, PS218, PS219, PS220, PS522, PS523 | PCE61, PCE64, DRJ4PCE800 | V2A-Fails validation criteria - results suspect | 300 |  | 295 | 290 | 90 |  |  | C2-NOP can be lowered to MOP-20 now | [5 empty] | C2-V2A | Y |  | 300 | 90 | 0 | 0 | 109.8901 | 109.8901
217 | MUMY | TP_SACRAMENTO_VALLEY | L220_500 | Lines 172 & 220 Crosstie (PCE) to Davis Meter and Reg Sta |  |  | PS243 | PCE386, PCE387 | V1-Meets Plng Guide validation criteria | 500 | A CROP reducing the MOP of L220 from 792 psig to 541 psig is in effect. As a result, L220 north of Rio Vista "Y" is operating at a MOP of 500 psig out of Lines 172 & 220 Crosstie. | 480 | 480 | 188 |  |  | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 500 | 188 | 0 | 0 | 116.4654 | 116.4654
218 | LRS3 | TP_SACRAMENTO_VALLEY | South Sutter Co Reg Sta (PCE) to DR R_FM_B-85. South Sutter DFM Included in distribution model: 09-J09YUBACITYaSd_UTM_45_MOP_MINUS_20_STUDY | South Sutter DFM |  | 17.88 | PS589 | DRJ4PCE816 | V2B-Incomplete validation - results suspect | 234 |  | 230 | 227 | 80 |  | 61 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 80 | 450 ft of 8" pipe south of Hutchinson Rd (from node 214G205F) to reinforce 4". This will extend existing 8" | $283,500 | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. DFM has been reinforced with 8" in past by WRO pipe replacement jobs. Construction costs of $630/ft based on highly congested cost provided by Gas Construction Cost Guide Rev 4/16 | C4-V2B | Y |  | 234 | 80 | 0 | 61 | 113.2352 | 105.5402
219 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | District 10 DFM between L-50 tap & Magnolia Rd (no source Reg) Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY |  |  | PS93, PS168, PS583, PS586, PS582, PS85, PS85, PS563 | PCE404, DRJ4PCE820 | V2B-Incomplete validation - results suspect | 400 |  | 385 | 385 | 150 |  | 234 | C2-NOP can be lowered to MOP-20 now |  | 199 | none |  | DRJ4: This analysis only looks at a lateral off of the L123_L173_500, and should be treated as part of that analysis. Therefore, the pressure should NOT be reduced until further analysis. Reduced pressure from 385 to 365 at tap. End pressure is inlet to | C2-V2B | Y |  | 400 | 150 | 0 | 234 | 116.3636 | 76.5411
220 | ANY3 | TP_SACRAMENTO_VALLEY | 0600_DIXON_158 | Dixon Reg Sta (PCE) to Dixon at the inlet to DR R_FM_R-22. 0600-05: 158# Included in distribution model:ESDZONE_SA_DIXON_H_W1112_APD_452_(MOP_MINUS_20_STUDY) |  | 2.78 | drj4PS700 | DRJ4PCE805 | V1-Meets Plng Guide validation criteria | 158 |  | 140 | 135 | 90 |  | 124 | C2-NOP can be lowered to MOP-20 now |  |  | none |  | DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. SOURCE REG: RR-19 (Dixon Primary) MODELED SETPOINT IS ALREADY 23 psi below MOP. NOP is 140 psig and may be operating as such in the field. | C2-V1 |  |  | 158 | 90 | 0 | 124 | 148.0313 | 56.8548
221 | LRS3 | TP_SACRAMENTO_VALLEY | 0634_COLUSA_GLENN_DRIER_600 | Maxwell Primary Reg Sta (PCE) to Maxwell and Comet Rice Drier. Included in distribution model: -BASE_08-J07maxwellAPD_UTM_452_MOP_MINUS_STUDY.MDB |  | 5.92 | PS595 | DRJ4PCE823 | V2B-Incomplete validation - results suspect | 600 |  | 590 | 570 | 80 |  | 514 | C1-Existing NOP offset is 20 psi or more |  |  | none |  | Already operating at MOP-30 | C1-V2B |  |  | 600 | 80 | 0 | 514 | 101.81 | 27.0939
222 | LRS3 | TP_SACRAMENTO_VALLEY | 0643_ARBUCKLE_150 | Arbuckle DFM Included in distribution model: BASE-07-J07ArbuckleAPD_UTM_452_MOP_MINUS_20_STUDY.MDB |  | 0.79 | drj4PS712 | PCE47, PCE48 | V1-Meets Plng Guide validation criteria | 150 |  | 143 | 133 | 80 |  | 45 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 80 | 1,250 FT OF 6" pipe starting at source | $787,500 | Currently an uprate is planned for 2013, the length of pipe shown would replace the uprate if that decision is made. Construction costs of $630/ft based on highly congested cost provided by Gas Construction Cost Guide Rev 4/16/2012 provided by GPS | C4-V1 |  |  | 150 | 80 | 0 | 45 | 139.7516 | 127.1739
223 | LRS3 | TP_SACRAMENTO_VALLEY | 1514_TOWNSHIP_150 | North Township DFM Included in distribution model: 09-J09YUBACITYaSd_UTM_45_MOP_MINUS_20_STUDY |  | 2.21 | drj4PS714 | DRJ4PCE818 | V3-Insufficient P data to complete validation | 150 |  | 145 | 135 | 80 |  | 133 | C2-NOP can be lowered to MOP-20 now |  | 117 | none |  | Reg set = 120 at MOP-20 | C2-V3 |  |  | 150 | 80 | 0 | 133 | 139.7516 | 29.882
224 | ANY3 | TP_SACRAMENTO_VALLEY | L116_L150_200 | L-150/L-116: 200# Davis Meter and Reg Sta (PCE) to Davis at the inlet to DR R_SCSTA-D08. -included in distribution model: ESDZONE_SA_DAVIS_H_W1112_APD_452_(MOP_MINUS_20_STUDY)_1st_&_A_St_Upgrade) |  | 5.92 | PS69, PS143 | PCE383 | V3-Insufficient P data to complete validation | 200 |  | 200 | 200 | 90 |  | 148 | C2-NOP can be lowered to MOP-20 now |  | 115 | none |  | DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. SOURCE DAVIS MTR/REG STA (105R & 106R) Pmin occurs at end of 750', 2" tap to DA- 06 Need charts for inlet to DA-06 | C2-V3 | Y |  | 200 | 90 | 0 | 148 | 125.3918 | 56.7273
225 | ANY3 | TP_SACRAMENTO_VALLEY | L158_L220_500 | D. Q. Scott Reg Sta (PCE) to Clark Pacific Concrete Plant. L-158/L-220 (Woodland?) Included in distribution model: ESDZONE_SA_WOODLAND_HL_W1112_APD_452_(w_Teichert)_(MOP_MINUS_20_STUDY) |  | 2.5 | PS151, PS243 | DRJ4PCE821 | V1-Meets Plng Guide validation criteria | 500 |  | 400 | 320 | 90 |  | 319 | C1-Existing NOP offset is 20 psi or more |  |  | none |  | DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. SOURCE REG: D.Q. Scott TS-09; ASD is controlling season NOP (350 psig) is already 150 psig below MOP (500 psig). Need to manually add 20 mcfh load for Clark Pacific to node 460G41 | C1-V1 | Y |  | 500 | 90 | 0 | 319 | 103.3485 | 61.2811

## Reference (hidden)
Monthly Tasks
Check ECTS for OP Events |  | https://catsweb.utility.pge.com/catsweb/main.aspx?WCI=Main&WCE=ViewDashboard&WCU=s%3dOKBSKCNWII1I1N8F2SIGBQO7I2742L34%7c*%7er%3dCorrective%20Action%20Management%7c*%7eq%3d1%7c*%7eg%3d0
Link to ECTS
Link to OPE 2011-2013 MOP Excursion Master (GTCC > Over Pressure Elimination Task Force > SCADA Reports)
Check detail tab that all fields are filled out
On the Pivot Tab
Run pivot tables for month / small-large excursion by trans/LP/HP (A-116)
Run by clicking in the table > right click > refresh
Run pivot tables for month /cause (A-102)
Run by clicking in the table > right click > refresh
Tracking Year by Month Tab
Update monthly # of OP events
Update YTD and EOY for # of OP events (change formulas as applicable)
Check Red-Amber-Green Status is correct for month/ytd/eoy actuals
Green = 0 difference
Amber = 1 difference
Red > 2 difference
On the Charts Tab
Update Bar Chart (and row formulas below for YTD)
Update Pie Chart (on chart tab)
Format MonthlyReportDetail tab for detailed explanations from tracking detail tab
Paste monthly report detail info as picture into Monthly OP report tab
Copy Metric monthly report stats to e-mail and send out to Asset Family Owner metric reporters
Update the GSO Keys to Success Monthly Report | [8 empty] | Currently from Dan
Link to Keys site (GTCC > Documents > GSO Keys to Success Monthly Report)
http://wssuo/gso/gc/GSO%20Keys%20To%20Success%20Monthly%20Report/Forms/AllItems.aspx
Update 2014 KTS Dashboard_GSO_Month (Excel spreadsheet)
Operate the system > Gas Over Pressure Event Frequency > columns D-G
Update Gas System Operations Report Month_Yeardraft (Word Document)
Metrics > Table: Gas Over-Pressure Event Frequency
Metrics > Table: OP Events by Quarter
Metrics > Observations
Primary Drivers, OP events, and their brief descriptions
Monthly OP Events > Table
Paste Pie Charts and Data Tables from Tracking 2013 by Month tab
Enter Corporate Dashboard comment info |  |  | http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx | [5 empty] | Currently from Tim Huckabay
Link to Corporate Dashboard
Gas Data Sheet
http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Update Tab: Data
Appropriate information for the Month (Searchable by Gas Metric: Gas Over-Pressure Event Frequency (OPF) Metric Reporter: Kevin Dang/Kevin Singer)
OPE per location detail
Update Tab: Variance Explanation
|  |  |  | Gas Over Pressure Event Frequency (OPF) - Columns F-H |  |  | i.e. | F | G | H
AFO/AFH | [5 empty] | Send monthly updates to Maria Bernal, Tyson Len, Tim Huckabay, Bryan Badgett
CAP updates?
Link to CAP Dashboard (Corrective Action Management)
CAP Updates
https://catsweb.utility.pge.com/catsweb/main.aspx?WCI=Main&WCE=ViewDashboard&WCU=s%3D8YWR64G9BGDM01CDL5PF3OVMC97RTZH4%7C*~r%3DCorrective%2520Action%2520Management%7C*~q%3D1
Update CAP number
2011-2013 Expanded Data tab
Update Cap number in Gas Event ID#/CAP ID #
use link of similar event
If nothing is indicated - Email Todd Novak about entering the OPE into CAP
these
Information that may help
Gas Logs
\\Appgas01\OPC\SHARE\GOCS
TCG(mon,day-year)
Open with notepad
Note on L52: Singer, Kevin D: For November there were 2 transmissions events, 0 HP distribution events and 1 LP distribution event (on par with the expectations for monthly totals). Preliminary root cause: 2 events were human factor error-related and 1 event was equipment-related.
Note on M52: Singer, Kevin D: OP Team reviews root causes of overpressure events. Plan additional training to address human-error related OP events. Detail review of equipment-related events to formulate corrective action plan.
Note on N52: Singer, Kevin D: As process improvement initiatives are implemented, expect this metric to return to green in December

## Tracking2019 by Month (hidden)
2019 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Expected Path: Goal OP events* | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 13 | 16
Amber Goal - Lowest end of range* | 4 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 |  |  | 20 | 25
Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  |  | 31 | 33 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Goal - HP Distribution Mains | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 7 | 8
Actual - HP Distribution Mains | 1 | 1 | 0 | 3 | 0 | 0 | 1 | 2 | 0 | 5 | 4 | 2 |  |  | 19 | 20 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | change these colors at End of Month |  |  |  |  | 0
Goal - Distribution Main Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 7 | 8 | [9 empty] | 1
Actual - Distribution Main Total | 1 | 1 | 0 | 3 | 0 | 0 | 1 | 2 | 0 | 5 | 4 | 2 |  |  | 19 | 20 |  |  |  |  | change these colors at End of Month |  |  |  |  | 2
Goal - Distribution Services Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 7 | 8
Actual - Distribution Services Total | 1 | 1 | 0 | 3 | 0 | 0 | 1 | 2 | 0 | 5 | 4 | 2 |  |  | 19 | 20 |  |  |  |  | change these colors at End of Month |  |  |  |  | 3
Goal - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 7 | 8
Actual - Transmission | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 1 |  |  | 11 | 12 |  |  |  |  | change these colors at End of Month
Goal - All Large OP Events1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 5 | 6 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 2 | 2 | 1 |  |  | 8 | 8
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 |  |  | 3 | 3
Actual - Total All Large OP | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  |  | 11 | 11
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 8 | 8
Actual - All Equipment Failure | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
Goal - All Operator Error | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 |  |  | 8 | 8
Actual - All Operator Error | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 |  |  | 9 | 9
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 3 | 4 | New for 2018
Actual - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 |  |  | 4 | 5 | New for 2018
Goal - All Safety | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 4 | New for 2018
Actual - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Goal - Small OP Events | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 9 | 10
Actual - Total Small OP | 1 | 2 | 2 | 2 | 0 | 0 | 1 | 2 | 1 | 3 | 4 | 2 |  |  | 20 | 21
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.201, 619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.201, 619-621
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events | Large OP Events | [11 empty] | Small OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2019 Target |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2019 Target |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2019 Target
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 16 |  |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 6 |  |  | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 20 | 12
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 18
2019 Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  |  | 31 | 31
2019 Goal OP events | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 9 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 5 | 5
2019 Actual - Total All Large Ops | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  |  | 11 | 11
2019 Goal - All Large OPs1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 6 | 6
| Jan: Total OP Events; Nov: Large OP Events | [9 empty] | Small OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual |  |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 | 21 |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 2 | 9 |  |  | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5 | 12
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 | 0 |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 |  |  | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2 | 0
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 | 21 |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 2 | 9 |  |  | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7 | 12
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 | 10 |  | 8 | 3 | 4 | 3 | 2 | 4 | 7 | 3 | 2 |  |  | 104 | 71 | 16 | 7 | 11 | 4 | 6 | 6 | 8
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 |  |  | 754 | 302 | 23 | 11 | 22 | 8 | 9 | 13 | 20
[11 empty] | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 YTD
[10 empty] | HU | 13 | 4 | 7 | 4 | 5 | 6 | 3 | 0 | 9
[10 empty] | EQ | 8 | 3 | 2 | 3 | 2 | 4 | 8 | 5 | 18
Proposed Scenario | 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 4 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A63: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx

## Tracking2020 by Month (hidden)
2020 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Expected Path: Goal OP events* | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 |  |  | 6 | 16
Amber Goal - Lowest end of range* | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 4 |  |  | 10 | 52
Actual - All Events | 4 | 7 | 5 | 1 | 2 | 4 | 4 | 4 | 3 | 5 | 0 | 3 |  |  | 42 | 43 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Goal - HP Distribution Mains | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 5 | 8
Actual - HP Distribution Mains | 2 | 5 | 2 | 1 | 2 | 1 | 3 | 1 | 2 | 3 | 0 | 3 |  |  | 25 | 28 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 1 |  |  |  |  | change these colors at End of Month
Goal - Distribution Main Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 3 | 8
Actual - Distribution Main Total | 2 | 5 | 3 | 1 | 2 | 1 | 3 | 1 | 2 | 3 | 0 | 3 |  |  | 26 | 30 |  |  |  |  | change these colors at End of Month
Goal - Distribution Services Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 1 | 8
Actual - Distribution Services Total | 2 | 5 | 3 | 1 | 2 | 1 | 3 | 1 | 2 | 3 | 0 | 3 |  |  | 26 | 33 |  |  |  |  | change these colors at End of Month
Goal - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 3 | 8
Actual - Transmission | 1 | 2 | 2 | 0 | 0 | 3 | 1 | 5 | 1 | 2 | 0 | 1 |  |  | 18 | 23 |  |  |  |  | change these colors at End of Month
Goal - All Large OP Events1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 1 | 6 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 1
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 1 | 1 | 0 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 |  |  | 8 | 8
Actual - Total All Large OP | 0 | 1 | 1 | 0 | 0 | 2 | 3 | 0 | 1 | 1 | 0 | 0 |  |  | 9 | 13
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 4 | 8
Actual - All Equipment Failure | 2 | 6 | 3 | 1 | 2 | - | - | - | - | - | - | - |  |  | 14 | 18 | [6 empty] | >8
Goal - All Operator Error | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 |  |  | 1 | 8 | [6 empty] | 8
Actual - All Operator Error | 1 | 1 | 2 | 0 | 0 | - | - | - | - | - | - | - |  |  | 4 | 11 | [6 empty] | 6
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 0 | 4 | New for 2018 | [5 empty] | 4
Actual - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - |  |  | 0 | 4 | New for 2018
Goal - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Actual - All Safety | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - |  |  | 0 | 0 | New for 2018
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - |  |  | 0 | 0
Goal - Small OP Events | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 3 | 10
Actual - Total Small OP | 4 | 6 | 4 | 1 | 2 | - | - | - | - | - | - | - |  |  | 17 | 24
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621; Jun: 192.201
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621; Jun: 192.201
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
See JobAid for additional details on Variance and Recovery comments to be added to the monthly report.
| Jan: Total OP Events | Large OP Events | [11 empty] | Small OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 YTD |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 YTD |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 YTD
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 |  |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 |  |  | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 20 | 33
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 18
2019 Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  |  | 31 | 31
2020 Actual - All Events | 3 | 7 | 5 | 1 | 2 | 4 | 4 | 6 | 3 | 5 | 0 | 3 |  |  | 43 | 43
2020 Goal OP events | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 9 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 5 | 5
2019 Actual - Total All Large Ops | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  |  | 11 | 11
2020 Actual - Total All Large Ops | 0 | 1 | 1 | 0 | 0 | 2 | 3 | 0 | 1 | 1 | 0 | 0 |  |  | 9 | 9
2020 Goal - All Large OPs1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 6 | 6
| Jan: Total OP Events; Nov: Large OP Events | [9 empty] | Small OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 | 21 | 24 |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 2 | 9 | 1 |  | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5 | 12 | 23
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 | 0 | 1 |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2 | 0 | 1
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 | 21 | 25 |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 2 | 9 | 1 |  | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7 | 12 | 24
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 | 10 | 18 |  | 8 | 3 | 4 | 3 | 2 | 4 | 7 | 3 | 2 | 8 |  | 104 | 71 | 16 | 7 | 11 | 4 | 6 | 6 | 8 | 10
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 |  | 754 | 302 | 23 | 11 | 22 | 8 | 9 | 13 | 20 | 34
| Oct: Large; Nov: 2011; Dec: 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
| Oct: HU; Nov: 13; Dec: 4 | 7 | 4 | 5 | 6 | 3 | 0 | 9
| Oct: EQ; Nov: 8; Dec: 3 | 2 | 3 | 2 | 4 | 8 | 5 | 18
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 4 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11
NEW as of December 2020 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: Large OP Events under STIP are reported and forecasted quarterly which may change the projections over a month-to-month basis.

## Tracking2021 by Month (hidden)
2021 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Expected Path: Goal OP events* | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 14 | 16
Amber Goal - Lowest end of range* | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 |  |  | 47 | 52
Actual - All Events | 1 | 7 | 1 | 3 | 2 | 1 | 5 | 4 | 1 | 3 | 4 | 2 |  |  | 34 | 36 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Goal - HP Distribution Mains | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 7 | 8
Actual - HP Distribution Mains | 1 | 4 | 1 | 1 | 2 | 1 | 0 | 2 | 0 | 1 | 3 | 0 |  |  | 16 | 17 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | change these colors at End of Month
Goal - Distribution Main Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 1 | 8
Actual - Distribution Main Total | 1 | 4 | 1 | 1 | 2 | 1 | 0 | 2 | 0 | 1 | 3 | 0 |  |  | 16 | 21 |  |  |  |  | change these colors at End of Month
Goal - Distribution Services Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 1 | 8
Actual - Distribution Services Total | 1 | 4 | 1 | 1 | 2 | 1 | 0 | 2 | 0 | 1 | 3 | 0 |  |  | 16 | 23 |  |  |  |  | change these colors at End of Month
Goal - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 7 | 8
Actual - Transmission | 0 | 3 | 0 | 2 | 0 | 0 | 5 | 2 | 1 | 2 | 1 | 2 |  |  | 18 | 20 |  |  |  |  | change these colors at End of Month
Goal - All Large OP Events1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 1 |  |  | 6 | 7 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  |  | 3 | 3
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 |  |  | 2 | 2
Actual - Total All Large OP | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 |  |  | 5 | 6
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 1 | 8
Actual - All Equipment Failure | [14 empty] | 0 | 7 | bar: Jan to Dec
Goal - All Operator Error | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 |  |  | 0 | 8
Actual - All Operator Error | [14 empty] | 0 | 8 | bar: Jan to Dec
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 0 | 4 | New for 2018
Actual - All Latent Org Weakness | [14 empty] | 0 | 4 | New for 2018 | bar: Jan to Dec
Goal - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Actual - All Safety | [14 empty] | 0 | 0 | New for 2018 | bar: Jan to Dec
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | [14 empty] | 0 | 0 | bar: Jan to Dec
Goal - Small OP Events | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 1 | 10
Actual - Total Small OP | [14 empty] | 0 | 9 | bar: Jan to Dec
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10%
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
See JobAid for additional details on Variance and Recovery comments to be added to the monthly report.
| Jan: Total OP Events | Large OP Events | [10 empty] | Small OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 YTD |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 YTD | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 | 9 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 | 5 | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 20 | 33 | 4
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 18
2019 Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  |  | 31 | 31
2020 Actual - All Events | 4 | 7 | 5 | 1 | 2 | 4 | 4 | 4 | 3 | 5 | 0 | 3 |  |  | 42 | 42
2021 Actual - All Events | Jan: 1; Feb: 7; Mar: 1; Apr: 3; May: 2 |  |  | 14
2021 Goal OP events | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 9 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 5 | 5
2019 Actual - Total All Large Ops | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  |  | 11 | 11
2020 Actual - Total All Large Ops | 0 | 1 | 1 | 0 | 0 | 2 | 3 | 0 | 1 | 1 | 0 | 0 |  |  | 9 | 9
2021 Actual - Total All Large Ops | Jan: 0; Feb: 0; Mar: 0; Apr: 0; May: 1 |  |  | 1
2021 Goal - All Large OPs1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 6 | 6
| Jan: Total OP Events | Large OP Events | [10 empty] | Small OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 | 21 | 24 | 10 |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 0 | 4 | 2 | 3 | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5 | 12 | 21 | 9
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 | 0 | 2 | 0 |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2 | 0 | 2 | 0
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 | 21 | 26 | 10 |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 0 | 4 | 2 | 3 | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7 | 12 | 23 | 9
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 | 10 | 16 | 4 |  | 8 | 3 | 4 | 3 | 2 | 4 | 7 | 5 | 7 | 6 | 2 | 104 | 71 | 16 | 7 | 11 | 4 | 6 | 6 | 8 | 12 | 4
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 | 14 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 8 | 5 | 754 | 302 | 23 | 11 | 22 | 8 | 9 | 13 | 20 | 35 | 13
[11 empty] | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
[10 empty] | HU | 13 | 4 | 7 | 4 | 5 | 6 | 3 | 0
[10 empty] | EQ | 8 | 3 | 2 | 3 | 2 | 4 | 8 | 5
Proposed Scenario | 2015-2020 Performance Outcomes
[12 empty] | Year | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
[12 empty] | LG HPD OP Events | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 0 | 4
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 4 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5
NEW as of December 2019/20 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 8*
*Chevron was not an overpressure event based on doucmentation found after the event, but documented by leadership as a large op event
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, wrt metrics

## Pivot (hidden)
OP/Near Hit? | (Multiple Items)
Large/Small OP Event | (Multiple Items)
Count of Month | Column Labels
Row Labels | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Grand Total
2011 | 4 | 3 | 2 |  | 5 | 2 |  | 1 | 1 | 2 |  | 1 | 21
2012 | 2 |  | 1 |  | 1 |  |  |  | 1 |  |  | 2 | 7
2013 | 2 | 1 | 1 | 1 |  |  |  | 2 | 1 |  | 1 |  | 9
2014 | 3 | [6 empty] | 2 |  |  | 2 |  | 7
2015 | 2 |  | 1 |  |  |  | 1 | 3 |  |  |  |  | 7
2016 |  |  |  | 1 |  | 3 | 1 | 1 |  | 2 | 1 | 1 | 10
2017 | 1 |  |  | 2 | 1 |  | 1 | 1 | 1 | 4 |  |  | 11
2018 | [6 empty] | 1 |  |  | 1 | 2 | 1 | 5
2019 | 1 |  |  | 1 | 1 | 1 | 1 | 1 |  | 2 | 2 | 1 | 11
2020 |  | 1 | 1 |  |  | 2 | 2 | 3 | 1 |  |  |  | 10
2021 |  |  |  |  | 1 |  | 1 |  |  | 1 | 1 |  | 4
Grand Total | 15 | 5 | 6 | 5 | 9 | 8 | 8 | 14 | 5 | 12 | 9 | 6 | 102

## Tracking2022byMonth (hidden)
2022 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Expected Path: Goal OP events* | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 10 | 33
Amber Goal - Lowest end of range* | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 |  |  | 5 | 74
Actual - All Events | 1 | 2 | 1 | 2 | 2 | 1 | 2 | 5 | 2 | 2 | 5 | 2 |  |  | 27 | 33 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Goal - HP Distribution Mains | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 8 | 8
Actual - HP Distribution Mains | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 4 | 0 | 1 | 4 | 1 |  |  | 14 | 16 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 1 | 1 |  |  |  |  | change these colors at End of Month
Goal - Distribution Main Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 8 | 8
Actual - Distribution Main Total | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 5 | 0 | 1 | 4 | 1 |  |  | 15 | 17 |  |  |  |  | change these colors at End of Month
Goal - Distribution Services Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 1 | 8
Actual - Distribution Services Total | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 5 | 0 | 1 | 4 | 1 |  |  | 15 | 22 |  |  |  |  | change these colors at End of Month
Goal - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 8 | 8
Actual - Transmission | 0 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 11 | 15 |  |  |  |  | change these colors at End of Month
Goal - All Large OP Events1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 |  |  | 5 | 5 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 |  |  | 4 | 4
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 |  |  | 5 | 5
Actual - Total All Large OP | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 0 |  |  | 9 | 10
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 1 | 8
Actual - All Equipment Failure | [14 empty] | 0 | 7 | bar: Jan to Dec
Goal - All Operator Error | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 |  |  | 0 | 8
Actual - All Operator Error | [14 empty] | 0 | 8 | bar: Jan to Dec
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 0 | 4 | New for 2018
Actual - All Latent Org Weakness | [14 empty] | 0 | 4 | New for 2018 | bar: Jan to Dec
Goal - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Actual - All Safety | [14 empty] | 0 | 0 | New for 2018 | bar: Jan to Dec
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | [14 empty] | 0 | 0 | bar: Jan to Dec
Goal - Small OP Events | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 1 | 10
Actual - Total Small OP | [14 empty] | 0 | 9 | bar: Jan to Dec
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10%
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
See JobAid for additional details on Variance and Recovery comments to be added to the monthly report.
Total OP Events
Total | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43 | 34 | 27
Large OP Events
Large | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022
T&D Total | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 | 5 | 9
Small OP Events
Small | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022
T&D Total | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 20 | 34 | 29 | 18
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 18
2019 Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  |  | 31 | 31
2020 Actual - All Events | 4 | 7 | 5 | 1 | 2 | 4 | 5 | 4 | 3 | 5 | 0 | 3 |  |  | 43 | 43
2021 Actual - All Events | 1 | 7 | 1 | 3 | 2 | 1 | 5 | 4 | 1 | 3 | 4 | 2 |  |  | 34 | 34
2022 Actual - All Events | 1 | 2 | 1 | 2 | 2 | 1 | 2 | 5 | 2 | 2 | 5 | 2 |  |  | 27 | 27
2022 Goal OP events | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 9 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 5 | 5
2019 Actual - Total All Large Ops | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  |  | 11 | 11
2020 Actual - Total All Large Ops | 0 | 1 | 1 | 0 | 0 | 2 | 2 | 2 | 1 | 0 | 0 | 0 |  |  | 9 | 9
2021 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 |  |  | 5 | 5
2022 Actual - Total All Large Ops | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 0 |  |  | 9 | 9
2022 Goal - All Large OPs1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 6 | 6
| Jan: Total OP Events |  | Large OP Events | [11 empty] | Small OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2022 YTD |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2022 Actual | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2022 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 | 21 | 19 | 16 | 13 |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 0 | 4 | 2 | 3 | 3 | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5 | 12 | 21 | 13 | 10
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 | 0 | 2 | 0 | 1 |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2 | 0 | 2 | 0 | 1
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 | 21 | 21 | 16 | 2 |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 0 | 4 | 2 | 3 | 3 | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7 | 12 | 23 | 13 | 11
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 | 10 | 22 | 18 | 13 |  | 8 | 3 | 4 | 3 | 2 | 4 | 7 | 5 | 7 | 7 | 6 | 6 | 104 | 71 | 16 | 7 | 11 | 4 | 6 | 6 | 8 | 12 | 12 | 7
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43 | 34 | 27 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 | 9 | 9 | 754 | 302 | 23 | 11 | 22 | 8 | 9 | 13 | 20 | 35 | 25 | 18
[11 empty] | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
[10 empty] | HU | 13 | 4 | 7 | 4 | 5 | 6 | 3 | 0
[10 empty] | EQ | 8 | 3 | 2 | 3 | 2 | 4 | 8 | 5
Proposed Scenario | 2015-2020 Performance Outcomes
[12 empty] | Year | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
[12 empty] | LG HPD OP Events | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 0 | 4
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 4 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5
NEW as of December 2019/20 (STIP 2021) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 9
*Chevron was not an overpressure event based on doucmentation found after the event, but documented by leadership as a large op event
NEW as of 2021 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 | 34
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 6
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 8* | 5
NEW as of 2022 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22 | ‘23
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A | N/A | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 | 34 | 27
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 5 | 7
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 8* | 5 | 9
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, wrt metrics

## OP & Near Hits Data
Columns Removed due to Confidential Nature - Point Description/Locations, Descriptions
Worksheets Removed - Guidance, Metrics, Tracking2023byMonth, Resources, & OP Event Classification
Data can be provided to CPUC upon request.
OP/Near Hit? | CAP# | TELVENT Point Name | Division | Date | Max Value | MAOP Value | Pressure Difference | Percent over MAOP | Primary Event Category | HU / EQ | P | Simplified cause (OP Events) | Corrective/Future Planned Actions | Transmission/ Distribution | Large/Small OP Event | Avoid by lower setpoints | At Compr Stn or Storage | Borescope/ Debris | RCE | Slam shut activation? | Runs | FLOC | Operating Diagram | Working Reg Setpoints (psig) | Primary OPP Setpoints (psig) | Secondary OPP Setpoints (psig)
OP | 7011203 | N/A | North Bay | 2011-01-01 | 140 | 60 | 80 | 133.3% | Maintenance Operations Quality |  |  |  | Immediate corrective actions were taken to reduce pressure: • Existing service immediately was shutoff. • CNG was called in to service the distribution customer during the repairs. • Existing service line was capped from the DFM, and a new service was bored in and from the distribution system. • The field could not locate the HPR | HP Distribution | Large OP Event | No | No | No | No |  |  | #N/A
OP | N/A | KT2_PT0014 | Topock District | 2011-01-01 07:22 | 673 | 660 | 13 | 1.97% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | Small Excursion | Yes | yes | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-03 02:10 | 10.6102 | 10.5 | 0.11019 | 1.049% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | KT2_PT0014 | Topock District | 2011-01-03 13:31 | 669 | 660 | 9 | 1.364% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | KT2_PT0014 | Topock District | 2011-01-04 00:30 | 677 | 660 | 17 | 2.576% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | Small Excursion | Yes | yes | No | No |  |  | #N/A
OP | N/A | BMD_PT0020 | McDonald Island District | 2011-01-04 07:51 | 1057 | 1025 | 32 | 3.122% | Unknown/ Not Recorded |  |  |  |  | Transmission | Large OP Event | no | yes | No | No |  | H-19 | GT.STAT.COMP.MCDONLDISL
OP | N/A | K09_PT0001 | Kettleman District | 2011-01-05 05:10 | 757.7654 | 757 | 0.76538 | 0.1011% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | N9M_PT0002 | San Francisco | 2011-01-07 | 10.5965 | 10.5 | 0.096452 | 0.9186% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-01-07 12:35 | 11.2 | 10.5 | 0.7 | 6.667% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | N9M_PT0002 | San Francisco | 2011-01-08 | 10.6491 | 10.5 | 0.1491 | 1.42% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 34 | JSJ_PT0035 | San Jose | 2011-01-08 03:18 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | N9M_PT0002 | San Francisco | 2011-01-09 | 10.6491 | 10.5 | 0.1491 | 1.42% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | N9M_PT0002 | San Francisco | 2011-01-10 | 10.8025 | 10.5 | 0.30247 | 2.881% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | N9M_PT0002 | San Francisco | 2011-01-11 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | AAN_PT0114S | Los Medanos District | 2011-01-11 03:54 | 502.5 | 500 | 2.5 | 0.5% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 2490 | RUN_PT0002 | North Coast | 2011-01-12 02:47 | 194.7291 | 167 | 27.7291 | 16.6% | Gas Contaminants - Sulfur | EQ |  |  |  | Transmission | Large OP Event | no | no | No | ACE |  | H-14 | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-12 14:51 | 10.5736 | 10.5 | 0.073562 | 0.7006% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | K4B_PT0002 | Kettleman District | 2011-01-12 23:28 | 807.514 | 803 | 4.514 | 0.5621% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-13 01:28 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | K09_PT0001 | Kettleman District | 2011-01-13 03:35 | 758.9099 | 757 | 1.9099 | 0.2523% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-13 23:15 | 10.5919 | 10.5 | 0.091874 | 0.875% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-14 00:37 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-01-14 01:16 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-14 01:25 | 10.6743 | 10.5 | 0.17428 | 1.66% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-01-14 02:45 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2011-01-14 11:01 | 12.1 | 10.5 | 1.6 | 15.24% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-15 00:38 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-15 01:31 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-01-15 03:10 | 11.48 | 10.5 | 0.98002 | 9.334% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-16 00:46 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-01-16 01:55 | 11.1229 | 10.5 | 0.62293 | 5.933% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-01-16 02:37 | 10.5083 | 10.5 | 0.0082722 | 0.07878% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-16 23:57 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-17 00:01 | 10.894 | 10.5 | 0.39403 | 3.753% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-17 00:24 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-18 01:19 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-18 01:43 | 10.6377 | 10.5 | 0.13765 | 1.311% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-01-18 14:40 | 10.5541 | 10.5 | 0.054052 | 0.5148% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | N9M_PT0002 | San Francisco | 2011-01-19 | 10.5072 | 10.5 | 0.0071793 | 0.06837% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-19 01:09 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SL2_PT0002 | Sacramento | 2011-01-19 10:32 | 505.6822 | 500 | 5.6822 | 1.136% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-01-20 13:19 | 10.699 | 10.5 | 0.19903 | 1.895% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-21 01:35 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | KT2_PT0100B | Topock District | 2011-01-21 08:20 | 698.1 | 660 | 38.1 | 5.773% | Maintenance Operations Quality | HU |  |  |  | Transmission | Large OP Event | no | yes | No | No |  | H-19 | GT.STAT.COMP.TOPOCK____
OP | N/A | JSJ_PT0035 | San Jose | 2011-01-21 16:38 | 10.894 | 10.5 | 0.39403 | 3.753% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-22 01:06 | 10.5095 | 10.5 | 0.0094681 | 0.09017% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-22 02:55 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-01-22 17:50 | 11.1229 | 10.5 | 0.62293 | 5.933% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | MMT_PT0083 | Milpitas District | 2011-01-22 19:04 | 304 | 300 | 4 | 1.333% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | N9M_PT0002 | San Francisco | 2011-01-23 | 10.5255 | 10.5 | 0.025492 | 0.2428% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-23 00:32 | 10.5003 | 10.5 | 0.00031185 | 0.00297% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-23 01:24 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-01-23 13:21 | 10.7842 | 10.5 | 0.28415 | 2.706% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-24 02:29 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-24 03:11 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | MIR_PT0011 | Milpitas District | 2011-01-24 13:36 | 323.9091 | 302 | 21.9091 | 7.255% | Unknown/ Not Recorded |  |  |  |  | Transmission | Small Excursion | no | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-25 00:02 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-25 03:16 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-26 00:10 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-01-26 23:06 | 10.6651 | 10.5 | 0.16512 | 1.573% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-27 00:27 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-28 01:12 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-29 01:25 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-01-29 03:11 | 11.5991 | 10.5 | 1.0991 | 10.47% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-01-30 01:53 | 11.7181 | 10.5 | 1.2181 | 11.6% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-01-30 03:09 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-01-31 02:15 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | JTL_PT0005 | San Jose | 2011-02-01 | 201.7 | 200 | 1.7 | 0.85% | Gas Contaminants - Liquids | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-02-01 01:29 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-01 02:14 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2528 | KT2_PT0100B | Topock District | 2011-02-01 12:54 | 724.7 | 660 | 64.7 | 9.803% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | Large OP Event | no | yes | No | ACE |  | H-19 | GT.STAT.COMP.TOPOCK____
OP | N/A | OC1_PT0041 | East Bay | 2011-02-02 01:03 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-02 01:25 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | BMD_PT0020 | McDonald Island District | 2011-02-02 06:34 | 1034 | 1025 | 9 | 0.878% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | BBC_PT0090 | Tracy District | 2011-02-02 06:44 | 873 | 871 | 2 | 0.2296% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0049 | East Bay | 2011-02-02 12:40 | 11.7 | 10.5 | 1.2 | 11.43% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | RAC_PT0002 | Humboldt | 2011-02-02 15:49 | 41.6302 | 40 | 1.6302 | 4.076% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-02-04 01:23 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-04 01:45 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | KT2_PT0100B | Topock District | 2011-02-04 07:55 | 726.5 | 528 | 198.5 | 37.59% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | Large OP Event | no | yes | No | No |  | H-19 | GT.STAT.COMP.TOPOCK____
OP | N/A | JSJ_PT0035 | San Jose | 2011-02-04 17:03 | 10.894 | 10.5 | 0.39403 | 3.753% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-02-05 20:23 | 11.1229 | 10.5 | 0.62293 | 5.933% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-02-05 23:41 | 10.5003 | 10.5 | 0.00031185 | 0.00297% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-02-05 23:43 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-05 23:48 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | KA2_PT0003 | Hinkley District | 2011-02-06 | 575.6 | 573 | 2.6 | 0.4538% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 2550 | N/A | Peninsula | 2011-02-06 | 45 | 5 | 40 | 800% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | Large OP Event |  | no | No | ACE |  | H-14 | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-02-06 00:51 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-06 01:15 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-02-06 01:26 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-02-06 01:33 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-02-06 01:58 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | K12_PT0004 | Kettleman District | 2011-02-06 02:20 | 673.376 | 669 | 4.376 | 0.6541% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-02-06 02:36 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-02-06 04:08 | 11.5991 | 10.5 | 1.0991 | 10.47% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-02-07 00:34 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-07 00:54 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-02-07 01:00 | 10.5827 | 10.5 | 0.082718 | 0.7878% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0043 | East Bay | 2011-02-07 01:30 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-02-07 02:14 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0048 | East Bay | 2011-02-07 02:47 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-02-07 05:08 | 11.0039 | 10.5 | 0.5039 | 4.799% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | AAN_PT0SP5 | Los Medanos District | 2011-02-07 11:39 | 344.5 | 338 | 6.5 | 1.923% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-08 00:09 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-02-08 00:12 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-02-08 00:58 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | JAW_PT0002 | San Jose | 2011-02-08 14:39 | 60.4094 | 60 | 0.40943 | 0.6824% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | ABC_PT0002 | Willows District | 2011-02-10 | 981.7 | 965 | 16.7 | 1.731% | Failure - Equipment | EQ |  |  |  | Transmission | Small Excursion | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-10 02:18 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | BBC_PT0001 | Tracy District | 2011-02-10 16:19 | 877 | 871 | 6 | 0.6889% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-11 00:56 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-02-12 01:51 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-12 02:36 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-13 01:16 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-14 00:57 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-02-14 00:59 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-02-14 23:38 | 10.5278 | 10.5 | 0.027781 | 0.2646% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-02-15 01:02 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-15 03:16 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-02-16 00:30 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-16 01:08 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-02-16 01:41 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0045 | East Bay | 2011-02-20 06:38 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | MMT_PT0017 | Milpitas District | 2011-02-21 00:46 | 308 | 300 | 8 | 2.667% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | AIR# | MIR_PT0007 | Milpitas District | 2011-02-24 16:06 | 257.5634 | 250 | 7.5634 | 3.025% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | AIR# | BRT_PT1144U | Tracy District | 2011-02-25 03:38 | 724 | 720 | 4 | 0.5556% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | AIR# | AAN_PTCCPP | Los Medanos District | 2011-02-27 | 197 | 195 | 2 | 1.026% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | AIR# | JDL_PT0001 | Hollister District | 2011-02-27 | 396.9 | 396 | 0.9 | 0.2273% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | NMA_PT0030 | Milpitas District | 2011-02-28 11:18 | 214.5675 | 203 | 11.5675 | 5.698% | Unknown/ Not Recorded |  |  |  |  | Transmission | Small Excursion | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-02-28 12:13 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2558 | JGC_PT0001 | DeAnza | 2011-02-28 12:24 | 186.2397 | 180 | 6.2397 | 3.467% | Gas Contaminants - Liquids | EQ |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-02-28 15:38 | 10.775 | 10.5 | 0.275 | 2.619% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-03-01 14:10 | 10.7178 | 10.5 | 0.21777 | 2.074% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-01 23:51 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-02 01:00 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-03-02 01:20 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-02 01:36 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-03-02 14:51 | 10.6743 | 10.5 | 0.17428 | 1.66% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | MSH_PT0003 | Milpitas District | 2011-03-03 | 528.3 | 476 | 52.3 | 10.99% | Design Issue |  |  |  |  | Transmission | Large OP Event | no | no | No | No |  |  | #N/A
OP | AIR# | AGE_PT0002 | Willows District | 2011-03-03 00:25 | 916 | 907 | 9 | 0.9923% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-03 00:43 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-03 02:02 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-03-03 03:00 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-03-03 12:20 | 10.8666 | 10.5 | 0.36656 | 3.491% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-04 00:40 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | AGE_PT0002 | Willows District | 2011-03-04 01:27 | 917 | 907 | 10 | 1.103% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-04 01:48 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OOA_PT0002 | East Bay | 2011-03-04 15:04 | 163.6734 | 150 | 13.6734 | 9.116% | Maintenance Operations Quality |  |  |  |  | Transmission | Small Excursion | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-05 00:41 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-05 02:50 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-03-06 01:05 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-06 02:44 | 10.9 | 10.5 | 0.4 | 3.81% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2011-03-06 02:57 | 10.5827 | 10.5 | 0.082718 | 0.7878% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-06 03:06 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-03-07 00:05 | 10.5369 | 10.5 | 0.036937 | 0.3518% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-07 00:22 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-07 00:52 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-03-07 01:07 | 10.5278 | 10.5 | 0.027781 | 0.2646% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-08 01:56 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-08 01:56 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSC_PT0001 | Central Coast | 2011-03-08 12:45 | 61.6989 | 60 | 1.6989 | 2.832% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-09 00:33 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-09 01:03 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | AGE_PT0002 | Willows District | 2011-03-09 05:12 | 916 | 907 | 9 | 0.9923% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-10 00:19 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-10 02:17 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JLF_PT0002 | San Jose | 2011-03-10 11:58 | 11.7181 | 10.5 | 1.2181 | 11.6% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NHL_PT0004 | Milpitas District | 2011-03-10 14:57 | 209.7649 | 203 | 6.7649 | 3.332% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-11 00:55 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-11 01:36 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-12 04:04 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2570 | N/A | North Bay | 2011-03-13 | 180.27 | 175 | 5.27 | 3.011% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-13 03:08 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FCT_PT0008 | Yosemite | 2011-03-14 01:13 | 10.6834 | 10.5 | 0.18344 | 1.747% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-03-14 01:23 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2011-03-14 01:57 | 10.5438 | 10.5 | 0.043804 | 0.4172% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-14 02:33 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-03-14 02:44 | 10.6065 | 10.5 | 0.10653 | 1.015% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | RFR_PT0002 | North Coast | 2011-03-14 10:53 | 154.8348 | 150 | 4.8348 | 3.223% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2105 | East Bay | 2011-03-14 13:50 | 11.5 | 10.5 | 1 | 9.524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-03-15 00:09 | 10.656 | 10.5 | 0.15597 | 1.485% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2011-03-15 01:05 | 10.6262 | 10.5 | 0.12621 | 1.202% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-03-15 01:13 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FCT_PT0008 | Yosemite | 2011-03-15 02:13 | 10.6926 | 10.5 | 0.19259 | 1.834% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-03-15 02:41 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-15 03:28 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-03-16 01:19 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FCT_PT0008 | Yosemite | 2011-03-16 01:28 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2011-03-16 01:50 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-03-16 03:47 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-03-16 04:03 | 10.6377 | 10.5 | 0.13765 | 1.311% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | KGF_PT0002 | Kern | 2011-03-16 11:43 | 483.6828 | 481 | 2.6828 | 0.5577% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-03-17 01:49 | 10.5095 | 10.5 | 0.0094681 | 0.09017% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0037 | Stockton | 2011-03-17 14:03 | 11.187 | 10.5 | 0.68703 | 6.543% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2011-03-19 23:40 | 14 | 10.5 | 3.5 | 33.33% | Maintenance Operations Quality | HU |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2011-03-20 00:25 | 14.2 | 10.5 | 3.7 | 35.24% | Failure - Flooding | EQ |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-03-22 03:06 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-03-24 01:21 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2572 | N9M_PT0002 | San Francisco | 2011-03-26 | 20 | 10.5 | 9.5 | 90.48% | Failure - Flooding | EQ |  |  |  | LP Distribution | Large OP Event |  | no | No | ACE |  | H-14 | GD.STAT.LPRS
OP | N/A | OC2_PT2108 | East Bay | 2011-03-26 02:25 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-28 02:11 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-03-29 03:02 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NHL_PT0004 | Milpitas District | 2011-03-29 14:45 | 205.9499 | 203 | 2.9499 | 1.453% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-30 01:36 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-03-30 01:54 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-03-30 16:18 | 10.5255 | 10.5 | 0.025492 | 0.2428% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FCT_PT0008 | Yosemite | 2011-03-30 23:51 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-03-30 23:57 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SMY_PT0031 | Sierra | 2011-03-31 | 10.7936 | 10.5 | 0.2936 | 2.796% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | SFR_PT0001 | Sacramento | 2011-03-31 00:28 | 156.4401 | 150 | 6.4401 | 4.293% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-03-31 00:53 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0048 | East Bay | 2011-03-31 01:14 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-03-31 01:17 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-03-31 01:45 | 10.6743 | 10.5 | 0.17428 | 1.66% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-03-31 01:47 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-03-31 02:01 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | JDX_PT0002 | San Jose | 2011-03-31 02:47 | 56.5486 | 55 | 1.5486 | 2.816% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0044 | San Jose | 2011-03-31 08:32 | 10.5003 | 10.5 | 0.00031185 | 0.00297% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-03-31 15:06 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-03-31 17:26 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0048 | East Bay | 2011-04-01 01:04 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-04-01 01:13 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-04-01 01:32 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-04-01 01:49 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-04-01 02:04 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-04-01 02:07 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-04-01 02:22 | 10.6065 | 10.5 | 0.10653 | 1.015% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-04-01 03:45 | 10.6834 | 10.5 | 0.18344 | 1.747% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | K09_PT0001 | Kettleman District | 2011-04-01 05:32 | 761.7331 | 757 | 4.7331 | 0.6252% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | K4B_PT0002 | Kettleman District | 2011-04-01 05:56 | 809.04 | 803 | 6.04 | 0.7522% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | SMY_PT0031 | Sierra | 2011-04-01 06:12 | 10.9035 | 10.5 | 0.40347 | 3.843% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-04-02 01:21 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-04-02 01:57 | 10.6651 | 10.5 | 0.16512 | 1.573% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-04-02 02:13 | 10.6285 | 10.5 | 0.1285 | 1.224% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-04-02 03:33 | 10.6743 | 10.5 | 0.17428 | 1.66% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-04-03 02:50 | 10.8666 | 10.5 | 0.36656 | 3.491% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-04-04 00:49 | 10.8299 | 10.5 | 0.32993 | 3.142% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-04-05 02:34 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-04-05 03:20 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-04-05 23:17 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0039 | Stockton | 2011-04-06 02:45 | 10.8666 | 10.5 | 0.36656 | 3.491% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | K09_PT0031 | Kern | 2011-04-06 09:04 | 12.478 | 10.5 | 1.978 | 18.84% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | AGE_PT0002 | Willows District | 2011-04-09 02:44 | 914 | 907 | 7 | 0.7718% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | NHL_PT0004 | Milpitas District | 2011-04-11 11:22 | 206.9799 | 203 | 3.9799 | 1.961% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-04-12 01:11 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2597 | AGE_PT0002 | Willows District | 2011-04-13 07:20 | 921 | 907 | 14 | 1.544% | Gas Control Center Operations | HU |  |  |  | Transmission | Small Excursion | Yes | yes | No | ACE |  |  | #N/A
OP | N/A | SSA_PT0104 | Sacramento | 2011-04-13 09:09 | 157.0124 | 150 | 7.0124 | 4.675% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0131 | Sacramento | 2011-04-14 13:53 | 12.9361 | 10.5 | 2.4361 | 23.2% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-04-16 00:47 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-04-17 00:34 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-04-17 01:33 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-04-18 00:53 | 10.656 | 10.5 | 0.15597 | 1.485% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-04-18 01:10 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-04-18 02:46 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Yosemite | 2011-04-18 13:29 | 11.9928 | 10.5 | 1.4928 | 14.22% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2600 | JCU_PT0001 | San Jose | 2011-04-18 16:44 | 343.5551 | 335 | 8.5551 | 2.554% | Gas Contaminants - Sulfur | EQ |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | MMT_PT0012 | Milpitas District | 2011-04-18 20:32 | 472 | 469 | 3 | 0.6397% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-04-19 01:12 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-04-19 01:36 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-04-20 01:42 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-04-20 01:43 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | AAN_PT0SP5 | Los Medanos District | 2011-04-20 07:13 | 346 | 338 | 8 | 2.367% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | AIR# | JCU_PT0001 | San Jose | 2011-04-20 21:49 | 311.8519 | 307 | 4.8519 | 1.58% | Gas Contaminants - Sulfur | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-04-21 11:05 | 13.5145 | 10.5 | 3.0145 | 28.71% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | KUA_PT0001 | Kern | 2011-04-22 13:29 | 51.4135 | 51 | 0.41348 | 0.8108% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | KT2_PT0014 | Topock District | 2011-04-23 07:20 | 529 | 528 | 1 | 0.1894% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-04-23 13:12 | 10.585 | 10.5 | 0.085007 | 0.8096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SMY_PT0031 | Sierra | 2011-04-27 11:32 | 10.6563 | 10.5 | 0.15626 | 1.488% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Yosemite | 2011-04-27 14:54 | 11.8737 | 10.5 | 1.3737 | 13.08% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | N/A | Milpitas District | 2011-04-28 09:39 | 415.6 | 400 | 15.6 | 3.9% | Failure - Equipment | EQ |  |  |  | Transmission | Small Excursion | Yes | no | No | No |  |  | #N/A
OP | N/A | OPL_PT0001 | Mission | 2011-04-28 14:22 | 163.8652 | 160 | 3.8652 | 2.416% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 2653 | N/A | North Valley | 2011-05-01 | 71 | 60 | 11 | 18.33% | Maintenance Operations Quality |  |  |  |  | HP Distribution | Large OP Event |  | no | No | ACE |  | H-14 | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-01 01:11 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SFS_PT0002 | Sacramento | 2011-05-02 00:34 | 60.1201 | 60 | 0.1201 | 0.2002% | Unknown/ Not Recorded |  |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-02 00:38 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-05-02 16:25 | 10.5026 | 10.5 | 0.0026016 | 0.02478% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-05-03 00:57 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-03 01:04 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-05-04 01:04 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-05-04 01:32 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-04 01:34 | 10.6834 | 10.5 | 0.18344 | 1.747% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0031 | East Bay | 2011-05-04 11:38 | 12.2 | 10.5 | 1.7 | 16.19% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | AP1_PT0001 | Diablo | 2011-05-05 | 101.14 | 100 | 1.14 | 1.14% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-05-05 01:15 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-05-05 01:18 | 10.5552 | 10.5 | 0.055249 | 0.5262% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-05-05 02:08 | 10.7652 | 10.5 | 0.26523 | 2.526% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-05 03:17 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | KT2_PT0014 | Topock District | 2011-05-05 12:06 | 538 | 528 | 10 | 1.894% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | ART_PT0002 | North Valley | 2011-05-05 13:54 | 604.5582 | 600 | 4.5582 | 0.7597% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FME_PT0032 | Yosemite | 2011-05-05 14:22 | 13.4733 | 10.5 | 2.9733 | 28.32% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-05-05 15:24 | 10.6102 | 10.5 | 0.11019 | 1.049% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-05-05 15:52 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-05-06 00:26 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-06 01:17 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-05-06 01:34 | 10.7652 | 10.5 | 0.26523 | 2.526% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JDX_PT0002 | San Jose | 2011-05-06 03:55 | 55.198 | 55 | 0.19804 | 0.3601% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | KA2_PT0003 | Hinkley District | 2011-05-06 04:02 | 573.125 | 555 | 18.125 | 3.266% | SP Too Close to MOP |  |  |  |  | Transmission | Small Excursion | Yes | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2011-05-06 09:17 | 13.2884 | 10.5 | 2.7884 | 26.56% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0043 | Stockton | 2011-05-06 09:17 | 11.8554 | 10.5 | 1.3554 | 12.91% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FME_PT0032 | Yosemite | 2011-05-06 10:38 | 12.283 | 10.5 | 1.783 | 16.98% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2675 | OC2_PT2109 | East Bay | 2011-05-07 | 17.4 | 10.5 | 6.9 | 65.71% | Failure - Flooding | EQ |  |  |  | LP Distribution | Large OP Event |  | no | No | ACE |  | H-14 | GD.STAT.LPRS
OP | AIR# | KT2_PT0014 | Topock District | 2011-05-07 07:09 | 532 | 528 | 4 | 0.7576% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-05-07 09:40 | 10.5415 | 10.5 | 0.041515 | 0.3954% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FME_PT0032 | Yosemite | 2011-05-09 11:40 | 11.024 | 10.5 | 0.52404 | 4.991% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-05-09 15:06 | 12.8 | 10.5 | 2.3 | 21.9% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-05-09 16:01 | 11.1847 | 10.5 | 0.68474 | 6.521% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2678 | OCK_PT0002 | East Bay | 2011-05-09 21:03 | 408.3367 | 405 | 3.3367 | 0.8239% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | SRE_PT0003 | Sacramento | 2011-05-10 10:45 | 50.9289 | 50 | 0.92892 | 1.858% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Yosemite | 2011-05-10 11:17 | 11.4068 | 10.5 | 0.90677 | 8.636% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0047 | East Bay | 2011-05-10 11:32 | 13.5 | 10.5 | 3 | 28.57% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0043 | East Bay | 2011-05-11 13:23 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0047 | East Bay | 2011-05-11 13:23 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0048 | East Bay | 2011-05-11 13:23 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-05-12 11:14 | 11.139 | 10.5 | 0.63896 | 6.085% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-13 01:12 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FME_PT0032 | Yosemite | 2011-05-13 07:19 | 12.8095 | 10.5 | 2.3095 | 22% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-05-13 12:42 | 10.9032 | 10.5 | 0.40318 | 3.84% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0031 | Fresno | 2011-05-14 08:47 | 10.5552 | 10.5 | 0.055249 | 0.5262% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2682 | FSN_PT0004 | Stockton | 2011-05-16 12:19 | 13.2655 | 10.5 | 2.7655 | 26.34% | Failure - Equipment | EQ |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | FST_PT0043 | Stockton | 2011-05-16 12:19 | 11.8646 | 10.5 | 1.3646 | 13% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FCT_PT0008 | Yosemite | 2011-05-17 09:37 | 11.6082 | 10.5 | 1.1082 | 10.55% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131678 | N/A | Kern | 2011-05-18 | 64 | 31 | 33 | 106.5% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | Large OP Event |  | no | No | ACE |  | H-15 | GT.STAT.LVCR.0000000423
OP | AIR# | RCV_PT0103 | Santa Rosa | 2011-05-18 09:09 | 32.2811 | 25 | 7.2811 | 29.12% | Unknown/ Not Recorded |  |  |  |  | HP Distribution | Large OP Event |  | no | No | No |  | H-14 | #N/A
OP | N/A | FST_PT0051 | Yosemite | 2011-05-19 15:03 | 11.4617 | 10.5 | 0.96171 | 9.159% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-20 00:34 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | REU_PT0001 | North Coast | 2011-05-20 01:25 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | BRT_PTO144D | Tracy District | 2011-05-20 22:45 | 726 | 723 | 3 | 0.4149% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | BRT_PTO144D | Tracy District | 2011-05-21 00:13 | 730 | 723 | 7 | 0.9682% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-21 03:37 | 10.6743 | 10.5 | 0.17428 | 1.66% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-22 01:53 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-05-22 02:21 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FCT_PT0008 | Yosemite | 2011-05-24 11:50 | 12.652 | 10.5 | 2.152 | 20.5% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0037 | Stockton | 2011-05-24 13:00 | 11.6448 | 10.5 | 1.1448 | 10.9% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0031 | East Bay | 2011-05-24 14:08 | 13.8 | 10.5 | 3.3 | 31.43% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2698 | N/A | North Coast | 2011-05-25 | 160 | 60 | 100 | 166.7% | Design Issue |  |  |  |  | HP Distribution | Large OP Event |  | no | No | ACE |  | H-15 | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-25 00:50 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-05-25 01:19 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | FST_PT0039 | Stockton | 2011-05-25 15:20 | 12.2858 | 10.5 | 1.7858 | 17.01% | Maintenance Operations Quality | HU |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2109 | East Bay | 2011-05-26 09:59 | 13.7 | 10.5 | 3.2 | 30.48% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-05-26 11:33 | 12.5 | 10.5 | 2 | 19.05% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | KB2_PT0004 | Hinkley District | 2011-05-27 06:32 | 576.25 | 576 | 0.25 | 0.0434% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | KT2_PT0107A | Topock District | 2011-05-27 23:03 | 869.7 | 865 | 4.7 | 0.5434% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-05-29 02:30 | 10.5369 | 10.5 | 0.036937 | 0.3518% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-05-31 11:22 | 11.4983 | 10.5 | 0.99833 | 9.508% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | RHN_PT0021S | North Bay | 2011-06-02 10:02 | 254.5151 | 250 | 4.5151 | 1.806% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-04 03:43 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-06-05 04:19 | 10.5369 | 10.5 | 0.036937 | 0.3518% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | MGY_PT0001 | San Jose | 2011-06-06 | 400.927 | 400 | 0.927 | 0.2318% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | REU_PT0001 | North Coast | 2011-06-06 00:32 | 10.5736 | 10.5 | 0.073562 | 0.7006% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Yosemite | 2011-06-06 01:22 | 11.5166 | 10.5 | 1.0166 | 9.682% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0049 | East Bay | 2011-06-06 14:13 | 12.8 | 10.5 | 2.3 | 21.9% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-07 01:56 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | NLP_PT0101 | Milpitas District | 2011-06-07 08:38 | 148.1852 | 145 | 3.1852 | 2.197% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2107 | East Bay | 2011-06-07 10:26 | 12.2 | 10.5 | 1.7 | 16.19% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2105 | East Bay | 2011-06-07 11:44 | 12.6 | 10.5 | 2.1 | 20% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | AAN_PT0191 | Los Medanos District | 2011-06-07 15:45 | 602 | 600 | 2 | 0.3333% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-08 00:49 | 10.5095 | 10.5 | 0.0094681 | 0.09017% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-06-08 01:56 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SYO_PT0004S | Willows District | 2011-06-08 13:40 | 822.0907 | 800 | 22.0907 | 2.761% | Maintenance Operations Quality | HU |  |  |  | Transmission | Small Excursion | no | no | No | No |  |  | #N/A
OP | N/A | RRF_PT0001 | North Bay | 2011-06-08 16:42 | 472.7342 | 450 | 22.7342 | 5.052% | Unknown/ Not Recorded |  |  |  |  | Transmission | Small Excursion | no | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-09 02:09 | 10.7652 | 10.5 | 0.26523 | 2.526% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-09 03:00 | 10.5095 | 10.5 | 0.0094681 | 0.09017% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-10 00:11 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-10 01:56 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131686 | JVL_PT0001 | DeAnza | 2011-06-10 10:38 | 46.8888 | 30 | 16.8888 | 56.3% | Gas Contaminants - Liquids | EQ |  |  |  | HP Distribution | Large OP Event |  | no | No | ACE |  | H-14 | #N/A
OP | N/A | OC2_PT2111 | East Bay | 2011-06-10 12:36 | 12.6 | 10.5 | 2.1 | 20% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-11 02:01 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-12 02:17 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-13 01:45 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-13 02:03 | 10.6285 | 10.5 | 0.1285 | 1.224% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-14 01:22 | 10.6285 | 10.5 | 0.1285 | 1.224% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-14 02:29 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-06-15 01:57 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-15 02:36 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | JDX_PT0002 | San Jose | 2011-06-15 02:53 | 55.3964 | 55 | 0.39642 | 0.7208% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-15 18:29 | 10.6285 | 10.5 | 0.1285 | 1.224% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-16 01:55 | 10.6285 | 10.5 | 0.1285 | 1.224% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-16 03:34 | 10.7652 | 10.5 | 0.26523 | 2.526% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-17 02:54 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-18 02:02 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-18 02:21 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JWD_PT0002 | Central Coast | 2011-06-18 16:10 | 60.0127 | 60 | 0.012661 | 0.0211% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-19 02:05 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-06-20 01:45 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-20 03:03 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0037 | Stockton | 2011-06-20 15:06 | 11.6448 | 10.5 | 1.1448 | 10.9% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-20 17:25 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-21 02:04 | 11.0826 | 10.5 | 0.58265 | 5.549% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-06-21 02:48 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-21 16:54 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-22 03:12 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSW_PT0002 | Sacramento | 2011-06-22 07:59 | 536.0405 | 531 | 5.0405 | 0.9492% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-22 19:13 | 10.6285 | 10.5 | 0.1285 | 1.224% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-23 01:35 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-23 01:35 | 10.7652 | 10.5 | 0.26523 | 2.526% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-06-23 02:04 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131690 | RCL_PT0005 | North Bay | 2011-06-23 09:06 | 253.1417 | 250 | 3.1417 | 1.257% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-24 01:44 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | KKT_PT0001 | Kettleman District | 2011-06-24 09:54 | 704 | 667 | 37 | 5.547% | Maintenance Operations Quality | HU |  |  |  | Transmission | Large OP Event | no | yes | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-25 01:47 | 10.7652 | 10.5 | 0.26523 | 2.526% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-06-25 02:32 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-26 01:38 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-26 02:44 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-06-27 01:31 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-27 01:53 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-27 02:25 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0020 | East Bay | 2011-06-27 14:35 | 218.2 | 218 | 0.2 | 0.09174% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | SSW_PT0002 | Sacramento | 2011-06-27 20:11 | 533.0648 | 531 | 2.0648 | 0.3888% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-06-28 01:35 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-06-28 02:21 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-28 02:53 | 10.7652 | 10.5 | 0.26523 | 2.526% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-29 01:38 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | RBR_PT0001 | North Bay | 2011-06-30 | 172.2 | 172 | 0.2 | 0.1163% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-06-30 02:10 | 10.7652 | 10.5 | 0.26523 | 2.526% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | KUA_PT0001 | Kern | 2011-06-30 09:44 | 52.8251 | 51 | 1.8251 | 3.579% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-01 01:37 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-01 02:00 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-02 01:36 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-02 01:55 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-07-02 14:29 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-03 01:41 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-03 05:13 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-07-03 16:47 | 10.6377 | 10.5 | 0.13765 | 1.311% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-04 01:56 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-04 02:44 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-07-04 17:28 | 10.7475 | 10.5 | 0.24753 | 2.357% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-07-05 01:02 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-05 01:28 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-05 02:57 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JDX_PT0002 | San Jose | 2011-07-05 03:03 | 55.0912 | 55 | 0.091213 | 0.1658% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | ADE_PT0002B | Willows District | 2011-07-05 05:27 | 1047 | 1040 | 7 | 0.6731% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | AIR# | ATN_PT0002B | Burney District | 2011-07-05 06:37 | 912 | 905 | 7 | 0.7735% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | yes | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-06 01:24 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-06 01:50 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2737 | NSF_PT0014 | San Francisco | 2011-07-06 10:12 | 13.412 | 10.5 | 2.912 | 27.73% | Maintenance Operations Quality | HU |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-07 01:41 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-07 01:42 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | SCS_PT0001 | Sacramento | 2011-07-07 09:38 | 240.45 | 240 | 0.45 | 0.1875% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 131693 | SYC_PT0003 | Sierra | 2011-07-07 22:15 | 493.1689 | 485 | 8.1689 | 1.684% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | AIR# | MSH_PT0003 | Milpitas District | 2011-07-08 | 441.15 | 440 | 1.15 | 0.2614% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-08 02:40 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-08 02:49 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | KBW_PT0001 | Kettleman District | 2011-07-08 14:42 | 632.1732 | 624 | 8.1732 | 1.31% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-09 03:02 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-10 02:35 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-10 04:08 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-11 01:24 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-11 01:56 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-12 01:41 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-13 02:50 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-13 03:14 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FME_PT0030 | Yosemite | 2011-07-13 09:32 | 61.7066 | 60 | 1.7066 | 2.844% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-14 04:30 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-15 02:32 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-15 02:39 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JFT_PT0002 | San Jose | 2011-07-15 12:21 | 382.3622 | 375 | 7.3622 | 1.963% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-16 01:44 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-17 01:52 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-17 06:16 | 10.6309 | 10.5 | 0.13094 | 1.247% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-18 02:13 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-18 04:29 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-19 01:00 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | JDX_PT0002 | San Jose | 2011-07-19 03:00 | 55.1751 | 55 | 0.17515 | 0.3185% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0049 | East Bay | 2011-07-19 03:02 | 11.1 | 10.5 | 0.6 | 5.714% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0106 | Sacramento | 2011-07-19 12:10 | 10.5739 | 10.5 | 0.073852 | 0.7033% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-20 01:14 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-20 03:50 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-21 00:56 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-21 02:49 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-22 01:45 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-22 02:15 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | RNW_PT0006 | North Bay | 2011-07-22 09:11 | 261.1028 | 250 | 11.1028 | 4.441% | Unknown/ Not Recorded |  |  |  |  | Transmission | Small Excursion | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-23 00:48 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-23 02:20 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSW_PT0002 | Sacramento | 2011-07-23 04:05 | 531.844 | 531 | 0.84399 | 0.1589% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0048 | East Bay | 2011-07-24 01:14 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-24 01:31 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-24 02:40 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-25 01:31 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-25 01:57 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-26 01:00 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-26 03:25 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0103 | Sacramento | 2011-07-26 12:15 | 11.0957 | 10.5 | 0.59575 | 5.674% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-27 01:07 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-27 03:43 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | K12_PT0004 | Kettleman District | 2011-07-27 10:11 | 673.1471 | 672 | 1.1471 | 0.1707% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0049 | East Bay | 2011-07-27 11:10 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | RHN_PT0004 | North Bay | 2011-07-27 15:06 | 404.9795 | 400 | 4.9795 | 1.245% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | AIR# | K4B_PT0004 | Kettleman District | 2011-07-27 22:03 | 631.105 | 631 | 0.10498 | 0.01664% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-28 01:16 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-28 02:18 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | BBC_PT0090 | Tracy District | 2011-07-28 10:55 | 882 | 865 | 17 | 1.965% | Design Issue |  |  |  |  | Transmission | Small Excursion | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-29 01:29 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-29 02:53 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-30 02:40 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-30 03:03 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-07-31 01:46 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-07-31 04:08 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-08-01 02:15 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-01 02:43 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | NSU_PT0002 | Milpitas District | 2011-08-01 14:15 | 299.755 | 145 | 154.755 | 106.7% | Maintenance Operations Quality | HU |  |  |  | Transmission | Large OP Event | no | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2108 | East Bay | 2011-08-02 01:44 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-02 03:43 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0103 | Sacramento | 2011-08-02 11:02 | 11.1415 | 10.5 | 0.64153 | 6.11% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-04 03:47 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2111 | East Bay | 2011-08-04 23:49 | 11.8 | 10.5 | 1.3 | 12.38% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2111 | East Bay | 2011-08-05 00:17 | 11.7 | 10.5 | 1.2 | 11.43% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-05 03:05 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-06 03:57 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-07 04:22 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-08 02:46 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-09 02:03 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-08-09 03:46 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2778 | SNH_PT0007 | Sacramento | 2011-08-09 13:17 | 508.133 | 500 | 8.133 | 1.627% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-10 01:43 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-11 02:37 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | BBC_PT0090 | Tracy District | 2011-08-11 06:22 | 863 | 861 | 2 | 0.2323% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2106 | East Bay | 2011-08-12 11:41 | 11.5 | 10.5 | 1 | 9.524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-13 02:26 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-14 04:16 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-15 01:29 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-16 01:45 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-17 04:19 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-18 02:13 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JDX_PT0002 | San Jose | 2011-08-18 02:42 | 55.0683 | 55 | 0.068325 | 0.1242% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-19 03:42 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | BBX_PT0007 | Tracy District | 2011-08-19 05:06 | 876 | 871 | 5 | 0.5741% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 131713 | KT2_PT0107A | Topock District | 2011-08-20 09:24 | 871.9 | 865 | 6.9 | 0.7977% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | Yes | No | ACE |  |  | #N/A
OP | AIR# | RUN_PT0001 | North Coast | 2011-08-21 | 350.5 | 350 | 0.5 | 0.1429% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-21 04:53 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-22 03:28 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-23 02:02 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2800 | JDX_PT0002 | San Jose | 2011-08-24 03:02 | 55.1904 | 55 | 0.19041 | 0.3462% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-24 04:16 | 10.7652 | 10.5 | 0.26523 | 2.526% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-25 02:30 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2106 | East Bay | 2011-08-25 09:00 | 13.1 | 10.5 | 2.6 | 24.76% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-26 02:11 | 11.0826 | 10.5 | 0.58265 | 5.549% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-08-27 01:32 | 10.6491 | 10.5 | 0.1491 | 1.42% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-27 02:18 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | BBC_PT0090 | Tracy District | 2011-08-27 05:28 | 862 | 861 | 1 | 0.1161% | Design Issue |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0131 | Sacramento | 2011-08-27 20:07 | 12.286 | 10.5 | 1.786 | 17.01% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | SSA_PT0131 | Sacramento | 2011-08-28 | 13.6 | 12 | 1.6 | 13.33% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-28 02:45 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-29 03:08 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0031 | East Bay | 2011-08-29 12:02 | 10.9 | 10.5 | 0.4 | 3.81% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2105 | East Bay | 2011-08-29 23:03 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2105 | East Bay | 2011-08-30 00:37 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-30 01:18 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0045 | East Bay | 2011-08-30 11:13 | 12.7 | 10.5 | 2.2 | 20.95% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-08-31 01:16 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-01 03:58 | 10.6309 | 10.5 | 0.13094 | 1.247% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-02 01:33 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-03 03:19 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-04 03:24 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-05 03:10 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-06 01:38 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-07 03:28 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0037 | Stockton | 2011-09-08 01:00 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-08 01:41 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-09 01:31 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0043 | Stockton | 2011-09-09 02:30 | 10.5827 | 10.5 | 0.082718 | 0.7878% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0048 | East Bay | 2011-09-10 01:44 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-09-10 01:56 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-10 03:28 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | STF_PT0002 | North Valley | 2011-09-10 11:01 | 10.6903 | 10.5 | 0.19029 | 1.812% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-09-11 02:08 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-11 02:33 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0043 | Stockton | 2011-09-11 04:14 | 10.5827 | 10.5 | 0.082718 | 0.7878% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-12 01:20 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0043 | Stockton | 2011-09-12 02:16 | 10.5827 | 10.5 | 0.082718 | 0.7878% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0046 | East Bay | 2011-09-12 11:49 | 13.3 | 10.5 | 2.8 | 26.67% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-13 02:00 | 11.0826 | 10.5 | 0.58265 | 5.549% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0037 | Stockton | 2011-09-13 16:42 | 11.6448 | 10.5 | 1.1448 | 10.9% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-14 02:57 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FME_PT0032 | Yosemite | 2011-09-14 14:02 | 10.8104 | 10.5 | 0.3104 | 2.956% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2011-09-15 01:52 | 10.5209 | 10.5 | 0.020913 | 0.1992% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-15 03:38 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131725 | JTL_PT0005 | San Jose | 2011-09-16 | 209.133 | 200 | 9.133 | 4.567% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-16 01:24 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SED_PT0001 | Sierra | 2011-09-16 06:08 | 60.0057 | 60 | 0.0056534 | 0.009422% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0035 | San Jose | 2011-09-16 09:41 | 11.1229 | 10.5 | 0.62293 | 5.933% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-17 05:16 | 10.6309 | 10.5 | 0.13094 | 1.247% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-18 04:43 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-09-19 00:59 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-19 03:03 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131728 | N/A | San Jose | 2011-09-20 | 55 | 50 | 5 | 10% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | Large OP Event |  | no | No | ACE |  | H-14 | #N/A
OP | AIR# | SSW_PT0002 | Sacramento | 2011-09-20 | 490.642 | 490 | 0.642 | 0.131% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-09-20 00:33 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-20 01:08 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0033 | San Jose | 2011-09-20 13:05 | 12.2546 | 10.5 | 1.7546 | 16.71% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | NHF_PT0002 | Peninsula | 2011-09-20 15:10 | 50.0019 | 50 | 0.0019073 | 0.003815% | Unknown/ Not Recorded |  |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0048 | East Bay | 2011-09-21 00:13 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-21 01:21 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-09-21 01:51 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | JDX_PT0002 | San Jose | 2011-09-21 02:56 | 55.0149 | 55 | 0.014912 | 0.02711% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-22 02:17 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | OCH_PT0001 | East Bay | 2011-09-22 02:58 | 50.0256 | 50 | 0.025562 | 0.05112% | Unknown/ Not Recorded |  |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-23 01:14 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-09-23 03:01 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-09-23 12:42 | 11.5258 | 10.5 | 1.0258 | 9.77% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0048 | East Bay | 2011-09-24 01:53 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-24 02:15 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-09-24 03:06 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | JDX_PT0002 | San Jose | 2011-09-24 03:44 | 54.9157 | 53 | 1.9157 | 3.615% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-25 03:38 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-09-26 04:25 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-09-27 06:05 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-09-28 01:56 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-28 01:58 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-29 03:08 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-09-29 03:26 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-09-30 03:59 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-01 03:01 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-02 02:51 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-02 05:20 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-03 00:39 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-10-03 02:40 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-04 01:08 | 10.6102 | 10.5 | 0.11019 | 1.049% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-04 01:40 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-05 01:54 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-05 02:11 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131737 | JSJ_PT0003 | San Jose | 2011-10-05 09:36 | 59.0207 | 30 | 29.0207 | 96.74% | Unknown/ Not Recorded |  |  |  |  | HP Distribution | Large OP Event |  | no | No | ACE |  | H-14 | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-06 00:35 | 10.6102 | 10.5 | 0.11019 | 1.049% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-07 00:41 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-08 04:58 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | RNW_PT0003 | North Bay | 2011-10-09 | 150.089 | 150 | 0.089 | 0.05933% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-09 01:44 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-09 04:52 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-10 00:59 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-10 04:23 | 10.6102 | 10.5 | 0.11019 | 1.049% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | BRT_PT0131S | Tracy District | 2011-10-10 07:55 | 338 | 324 | 14 | 4.321% | Maintenance Operations Quality |  |  |  |  | Transmission | Small Excursion | Yes | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-10-11 01:36 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-10-11 02:26 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-11 02:31 | 10.9239 | 10.5 | 0.42394 | 4.038% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-12 00:59 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-10-13 01:34 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-13 02:09 | 10.692 | 10.5 | 0.19199 | 1.828% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-10-13 02:57 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-10-14 01:34 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-10-14 02:01 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-14 02:20 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-14 04:00 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-10-15 01:22 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-15 01:52 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-10-15 02:12 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-10-15 03:03 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-15 05:21 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-10-16 02:41 | 10.5278 | 10.5 | 0.027781 | 0.2646% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-16 03:03 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-10-16 04:42 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-17 00:58 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-10-17 10:31 | 11.1 | 10.5 | 0.6 | 5.714% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-10-18 01:46 | 10.5278 | 10.5 | 0.027781 | 0.2646% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-18 01:46 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0048 | East Bay | 2011-10-18 02:48 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-18 04:31 | 10.6102 | 10.5 | 0.11019 | 1.049% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0043 | East Bay | 2011-10-18 10:22 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2109 | East Bay | 2011-10-18 13:57 | 10.9 | 10.5 | 0.4 | 3.81% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2011-10-18 13:58 | 10.5118 | 10.5 | 0.011757 | 0.112% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2011-10-19 01:05 | 10.5186 | 10.5 | 0.018624 | 0.1774% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-19 01:20 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-19 01:42 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-20 01:19 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-20 01:32 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0061 | Yosemite | 2011-10-20 09:13 | 11.0863 | 10.5 | 0.58631 | 5.584% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0046 | East Bay | 2011-10-20 10:45 | 16.3 | 10.5 | 5.8 | 55.24% | Maintenance Operations Quality | HU |  |  |  | LP Distribution | Large OP Event |  | no | No | No |  | H-14 | GD.STAT.LPRS
OP | AIR# | SSW_PT0002 | Sacramento | 2011-10-20 11:02 | 539.474 | 538 | 1.474 | 0.274% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-21 01:25 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-21 02:04 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0045 | East Bay | 2011-10-21 09:46 | 10.9 | 10.5 | 0.4 | 3.81% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-22 05:03 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-23 02:47 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2011-10-23 03:08 | 10.5644 | 10.5 | 0.064405 | 0.6134% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-23 06:18 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-24 01:18 | 10.7774 | 10.5 | 0.27744 | 2.642% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0041 | East Bay | 2011-10-24 02:15 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-24 02:40 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-25 04:05 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-25 22:43 | 10.6102 | 10.5 | 0.11019 | 1.049% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-26 02:33 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-10-26 11:40 | 10.9361 | 10.5 | 0.43615 | 4.154% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-27 03:50 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-28 00:38 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-29 05:39 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | SSW_PT0007 | Sacramento | 2011-10-29 08:22 | 511.2979 | 500 | 11.2979 | 2.26% | Unknown/ Not Recorded |  |  |  |  | Transmission | Small Excursion | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-30 05:53 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-10-31 05:06 | 10.6102 | 10.5 | 0.11019 | 1.049% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-11-01 01:40 | 10.601 | 10.5 | 0.10103 | 0.9622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2011-11-01 02:09 | 10.6187 | 10.5 | 0.11874 | 1.131% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-11-01 09:54 | 10.656 | 10.5 | 0.15597 | 1.485% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-11-02 01:04 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-11-03 03:17 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-11-04 01:01 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSW_PT0007 | Sacramento | 2011-11-04 05:26 | 522.102 | 500 | 22.102 | 4.42% | Failure - Equipment | EQ |  |  |  | Transmission | Small Excursion | no | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-11-05 00:40 | 10.7201 | 10.5 | 0.22006 | 2.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0041 | San Jose | 2011-11-06 01:07 | 10.8391 | 10.5 | 0.33909 | 3.229% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | KA2_PT0003 | Hinkley District | 2011-11-07 04:43 | 583.75 | 576 | 7.75 | 1.345% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-11-11 00:22 | 10.5083 | 10.5 | 0.0082722 | 0.07878% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0111 | Sacramento | 2011-11-11 12:49 | 11.7733 | 10.5 | 1.2733 | 12.13% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0102 | Sacramento | 2011-11-11 12:49 | 10.7661 | 10.5 | 0.26613 | 2.535% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0106 | Sacramento | 2011-11-11 12:49 | 10.7844 | 10.5 | 0.28444 | 2.709% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0104 | Fresno | 2011-11-12 22:08 | 60.0649 | 60 | 0.064857 | 0.1081% | SP Too Close to MOP |  |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-11-12 23:49 | 10.5235 | 10.5 | 0.023532 | 0.2241% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-11-13 13:00 | 10.5159 | 10.5 | 0.015902 | 0.1514% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0104 | Fresno | 2011-11-14 00:50 | 60.0649 | 60 | 0.064857 | 0.1081% | SP Too Close to MOP |  |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-11-14 12:22 | 10.5235 | 10.5 | 0.023532 | 0.2241% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0104 | Fresno | 2011-11-18 00:30 | 60.0649 | 60 | 0.064857 | 0.1081% | SP Too Close to MOP |  |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-11-18 00:42 | 10.5159 | 10.5 | 0.015902 | 0.1514% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-11-19 03:46 | 10.5369 | 10.5 | 0.036937 | 0.3518% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JLF_PT0002 | San Jose | 2011-11-19 09:31 | 12.1759 | 10.5 | 1.6759 | 15.96% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0031 | East Bay | 2011-11-20 03:45 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-11-21 01:33 | 10.5461 | 10.5 | 0.046093 | 0.439% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0031 | East Bay | 2011-11-21 02:19 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JLF_PT0002 | San Jose | 2011-11-21 09:17 | 11.2443 | 10.5 | 0.74425 | 7.088% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2011-11-21 14:43 | 10.5781 | 10.5 | 0.078139 | 0.7442% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0031 | East Bay | 2011-11-22 01:01 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0039 | San Jose | 2011-11-23 01:56 | 10.5369 | 10.5 | 0.036937 | 0.3518% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0104 | Fresno | 2011-11-23 17:07 | 60.0649 | 60 | 0.064857 | 0.1081% | SP Too Close to MOP |  |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0104 | Fresno | 2011-11-24 00:24 | 60.0649 | 60 | 0.064857 | 0.1081% | SP Too Close to MOP |  |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-11-28 01:07 | 10.5006 | 10.5 | 0.00064182 | 0.006113% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2011-11-28 13:15 | 10.6949 | 10.5 | 0.19488 | 1.856% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0044 | San Jose | 2011-11-30 16:42 | 12.4414 | 10.5 | 1.9414 | 18.49% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | AKH_PT0004 | Rio Vista District | 2011-12-02 04:17 | 969.8203 | 965 | 4.8203 | 0.4995% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-02 14:04 | 10.5006 | 10.5 | 0.00064182 | 0.006113% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-03 14:16 | 10.5617 | 10.5 | 0.061683 | 0.5875% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-04 13:25 | 10.5693 | 10.5 | 0.069313 | 0.6601% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131756 | N/A | Peninsula | 2011-12-05 | 61 | 60 | 1 | 1.667% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | #REF! |  | No | No | ACE |  |  | #N/A
OP | N/A | OC2_PT2109 | East Bay | 2011-12-05 13:39 | 11.4 | 10.5 | 0.9 | 8.571% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-05 14:12 | 10.5312 | 10.5 | 0.031162 | 0.2968% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | AKH_PT0004 | Rio Vista District | 2011-12-06 02:49 | 968.9386 | 965 | 3.9386 | 0.4081% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | BMD_PT0020 | McDonald Island District | 2011-12-06 11:38 | 1029 | 1025 | 4 | 0.3902% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | Yes | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-06 12:51 | 10.6532 | 10.5 | 0.15324 | 1.459% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-07 13:39 | 10.5693 | 10.5 | 0.069313 | 0.6601% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SCI_PT0002 | North Valley | 2011-12-07 17:06 | 71.2447 | 60 | 11.2447 | 18.74% | Unknown/ Not Recorded |  |  |  |  | HP Distribution | Large OP Event |  | no | No | No |  | H-14 | #N/A
OP | N/A | NSU_PT0002 | Milpitas District | 2011-12-08 05:39 | 153.1646 | 145 | 8.1646 | 5.631% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-08 15:29 | 10.5998 | 10.5 | 0.099833 | 0.9508% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-09 13:40 | 10.5998 | 10.5 | 0.099833 | 0.9508% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-10 12:31 | 10.5922 | 10.5 | 0.092203 | 0.8781% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-11 14:17 | 10.6151 | 10.5 | 0.11509 | 1.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-12 01:37 | 10.5312 | 10.5 | 0.031162 | 0.2968% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-13 23:23 | 10.5693 | 10.5 | 0.069313 | 0.6601% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-14 00:56 | 10.6685 | 10.5 | 0.1685 | 1.605% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | AKH_PT0004 | Rio Vista District | 2011-12-15 14:11 | 975.8562 | 965 | 10.8562 | 1.125% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | Small Excursion | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-15 22:54 | 10.6227 | 10.5 | 0.12272 | 1.169% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | AKH_PT0004 | Rio Vista District | 2011-12-16 12:23 | 969.2777 | 965 | 4.2777 | 0.4433% | Design Issue- 3rd Party Supply |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-16 14:08 | 10.5998 | 10.5 | 0.099833 | 0.9508% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-17 14:13 | 10.5693 | 10.5 | 0.069313 | 0.6601% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-18 12:35 | 10.5998 | 10.5 | 0.099833 | 0.9508% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | AIR# | KKT_PT0006 | Kettleman District | 2011-12-19 11:54 | 846 | 839 | 7 | 0.8343% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | Yes | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-19 15:28 | 10.5998 | 10.5 | 0.099833 | 0.9508% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-20 23:35 | 10.6151 | 10.5 | 0.11509 | 1.096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-21 01:51 | 10.6227 | 10.5 | 0.12272 | 1.169% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-22 13:30 | 10.5769 | 10.5 | 0.076943 | 0.7328% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC1_PT0045 | East Bay | 2011-12-23 05:05 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-23 18:08 | 10.699 | 10.5 | 0.19903 | 1.895% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2011-12-24 14:04 | 10.6056 | 10.5 | 0.10561 | 1.006% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-24 18:29 | 10.6761 | 10.5 | 0.17614 | 1.677% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2011-12-25 14:47 | 10.5346 | 10.5 | 0.034648 | 0.33% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-25 16:32 | 10.6838 | 10.5 | 0.18377 | 1.75% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2011-12-26 14:41 | 10.5804 | 10.5 | 0.080429 | 0.766% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-26 15:19 | 10.6838 | 10.5 | 0.18377 | 1.75% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2011-12-27 13:21 | 10.6308 | 10.5 | 0.13079 | 1.246% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-27 13:45 | 10.6838 | 10.5 | 0.18377 | 1.75% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2011-12-28 13:28 | 10.6926 | 10.5 | 0.19259 | 1.834% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | ACD_PT008A | Rio Vista District | 2011-12-28 14:42 | 660 | 651 | 9 | 1.382% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2011-12-28 14:54 | 10.5232 | 10.5 | 0.023203 | 0.221% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-28 22:24 | 10.7906 | 10.5 | 0.29059 | 2.767% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | RCV_PT0103 | Santa Rosa | 2011-12-28 23:54 | 25.0478 | 25 | 0.047827 | 0.1913% | Gas Contaminants - Liquids | EQ |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2011-12-29 00:22 | 10.6079 | 10.5 | 0.1079 | 1.028% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2011-12-29 14:43 | 10.5575 | 10.5 | 0.057538 | 0.548% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-29 23:31 | 10.6761 | 10.5 | 0.17614 | 1.677% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-30 00:17 | 10.6838 | 10.5 | 0.18377 | 1.75% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | RBR_PT0002 | North Bay | 2011-12-30 01:32 | 25.1195 | 25 | 0.11951 | 0.4781% | Unknown/ Not Recorded |  |  |  |  | HP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2011-12-30 15:28 | 10.6193 | 10.5 | 0.11934 | 1.137% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2011-12-31 00:16 | 10.638 | 10.5 | 0.13798 | 1.314% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 7009748 | N/A | Sacramento | 2012-01-01 | 126 | 125 | 1 | 0.8% | Maintenance Operations Quality |  |  |  | Lower pressure set points update maps | Transmission | #REF! | Yes | No | No | ACE |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-01-01 | 10.6331 | 10.5 | 0.13308 | 1.267% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-01 | 10.7219 | 10.5 | 0.22192 | 2.113% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2947 | N/A | Sacramento | 2012-01-01 | 110 | 60 | 50 | 83.33% | Failure - Equipment | EQ |  |  |  | HP Distribution | Large OP Event |  | no | No | ACE |  | H-14 | #N/A
OP | N/A | OC2_PT2105 | East Bay | 2012-01-01 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-02 | 10.6685 | 10.5 | 0.1685 | 1.605% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Fresno | 2012-01-02 | 10.5736 | 10.5 | 0.073562 | 0.7006% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | K1B_PT0004 | Topock District | 2012-01-02 18:39 | 780.6558 | 779 | 1.6558 | 0.2126% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-01-03 | 10.7246 | 10.5 | 0.22464 | 2.139% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-03 | 10.5922 | 10.5 | 0.092203 | 0.8781% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-01-03 | 10.569 | 10.5 | 0.068983 | 0.657% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131772 | N/A | Sacramento | 2012-01-03 | 175 | 60 | 115 | 191.7% | Design Issue | EQ |  |  |  | HP Distribution | Large OP Event |  | no | No | ACE |  | H-14 | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-04 | 10.6685 | 10.5 | 0.1685 | 1.605% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-01-04 | 10.5781 | 10.5 | 0.078139 | 0.7442% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-05 | 10.6377 | 10.5 | 0.13771 | 1.312% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2953 | JMD_PT0002 | San Jose | 2012-01-05 | 60.07 | 60 | 0.07 | 0.1167% | Failure - Equipment | EQ |  |  |  | HP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | RRF_PT0001 | North Bay | 2012-01-05 13:30 | 452.3239 | 450 | 2.3239 | 0.5164% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-01-06 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Fresno | 2012-01-06 | 10.5825 | 10.5 | 0.082472 | 0.7854% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2977 | OC2_PT0102 | East Bay | 2012-01-09 | 13.8 | 10.5 | 3.3 | 31.43% | Maintenance Operations Quality | HU |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | OC2_PT2105 | East Bay | 2012-01-09 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-10 | 10.5767 | 10.5 | 0.076673 | 0.7302% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-11 | 10.5385 | 10.5 | 0.038523 | 0.3669% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2111 | East Bay | 2012-01-12 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-13 | 10.569 | 10.5 | 0.069043 | 0.6576% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-01-13 | 10.7427 | 10.5 | 0.2427 | 2.311% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-14 | 10.5385 | 10.5 | 0.038523 | 0.3669% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-01-14 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-01-16 08:49 | 181.258 | 180 | 1.258 | 0.6989% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Fresno | 2012-01-17 | 10.9304 | 10.5 | 0.4304 | 4.099% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-01-17 06:14 | 181.6242 | 180 | 1.6242 | 0.9024% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OS3_PT0005 | Los Medanos District | 2012-01-17 08:43 | 338.72 | 338 | 0.72001 | 0.213% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 131777 | SPR_PT0001 | North Valley | 2012-01-17 10:43 | 205.2966 | 200 | 5.2966 | 2.648% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | SNH_PT0007 | Sacramento | 2012-01-17 16:55 | 500.6134 | 500 | 0.61343 | 0.1227% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Fresno | 2012-01-18 | 11.2783 | 10.5 | 0.77833 | 7.413% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OS3_PT0005 | Los Medanos District | 2012-01-18 00:05 | 338.4148 | 338 | 0.41481 | 0.1227% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-01-18 08:49 | 181.258 | 180 | 1.258 | 0.6989% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-19 | 10.5462 | 10.5 | 0.046153 | 0.4396% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Fresno | 2012-01-19 | 11.1593 | 10.5 | 0.6593 | 6.279% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-20 | 10.5309 | 10.5 | 0.030893 | 0.2942% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2106 | East Bay | 2012-01-20 | 11 | 10.5 | 0.5 | 4.762% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 2991 | OC2_PT2107 | East Bay | 2012-01-20 | 11.7 | 10.5 | 1.2 | 11.43% | Failure - Flooding | EQ |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-21 | 10.5385 | 10.5 | 0.038523 | 0.3669% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-01-21 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2106 | East Bay | 2012-01-21 | 11.3 | 10.5 | 0.8 | 7.619% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2107 | East Bay | 2012-01-21 | 12.1 | 10.5 | 1.6 | 15.24% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-22 | 10.5004 | 10.5 | 0.00037289 | 0.003551% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-01-22 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-23 | 10.5538 | 10.5 | 0.053783 | 0.5122% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-24 | 10.5233 | 10.5 | 0.023263 | 0.2216% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-25 | 10.5385 | 10.5 | 0.038523 | 0.3669% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0012 | San Francisco | 2012-01-25 | 10.7198 | 10.5 | 0.21981 | 2.093% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-01-25 18:26 | 180.3424 | 180 | 0.34242 | 0.1902% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-26 | 10.5233 | 10.5 | 0.023263 | 0.2216% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-01-26 | 10.523 | 10.5 | 0.022958 | 0.2186% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0012 | San Francisco | 2012-01-26 | 10.848 | 10.5 | 0.34799 | 3.314% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-01-26 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | BRT_PTOO24 | Tracy District | 2012-01-26 09:18 | 892 | 890 | 2 | 0.2247% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 3054 | AGE_PT0002 | Willows District | 2012-01-27 | 912 | 907 | 5 | 0.5513% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | Yes | No | ACE |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-27 | 10.5385 | 10.5 | 0.038523 | 0.3669% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-01-27 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-01-27 | 10.7564 | 10.5 | 0.25644 | 2.442% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-28 | 10.5614 | 10.5 | 0.061413 | 0.5849% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-01-28 | 10.5092 | 10.5 | 0.0092239 | 0.08785% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2105 | East Bay | 2012-01-28 | 10.9 | 10.5 | 0.4 | 3.81% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-29 | 10.508 | 10.5 | 0.0080032 | 0.07622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-01-29 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2105 | East Bay | 2012-01-29 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-01-30 | 10.5462 | 10.5 | 0.046153 | 0.4396% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-02 | 10.5614 | 10.5 | 0.061413 | 0.5849% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0012 | San Francisco | 2012-02-02 | 10.7198 | 10.5 | 0.21981 | 2.093% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | K1B_PT0004 | Topock District | 2012-02-02 04:47 | 781.2485 | 779 | 2.2485 | 0.2886% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | KPG_PT0004 | Hinkley District | 2012-02-02 08:30 | 683.2796 | 682 | 1.2796 | 0.1876% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-02-03 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-02-05 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-05 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT2105 | East Bay | 2012-02-05 | 10.9 | 10.5 | 0.4 | 3.81% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FCT_PT0003 | Yosemite | 2012-02-05 16:02 | 180.2277 | 180 | 0.22767 | 0.1265% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 3037 | N/A | East Bay | 2012-02-06 | 16 | 15 | 1 | 6.667% | Failure - Flooding | EQ |  |  |  | HP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | NSF_PT0012 | San Francisco | 2012-02-06 | 10.6008 | 10.5 | 0.10078 | 0.9599% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-06 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-07 | 10.5233 | 10.5 | 0.023263 | 0.2216% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-02-07 | 10.5985 | 10.5 | 0.098495 | 0.938% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-02-08 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0012 | San Francisco | 2012-02-08 | 10.8297 | 10.5 | 0.32968 | 3.14% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-02-09 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-02-09 | 10.5916 | 10.5 | 0.091628 | 0.8726% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0012 | San Francisco | 2012-02-09 | 10.8388 | 10.5 | 0.33884 | 3.227% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-02-10 | 10.7473 | 10.5 | 0.24728 | 2.355% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-02-10 | 10.7816 | 10.5 | 0.28161 | 2.682% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0012 | San Francisco | 2012-02-10 | 10.6099 | 10.5 | 0.10994 | 1.047% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | K1A_PT0003 | Topock District | 2012-02-10 08:32 | 781.2485 | 779 | 2.2485 | 0.2886% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-02-11 | 10.5962 | 10.5 | 0.096206 | 0.9162% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-02-13 | 10.5985 | 10.5 | 0.098495 | 0.938% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-13 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-15 | 10.5996 | 10.5 | 0.099563 | 0.9482% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-15 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-16 | 10.6835 | 10.5 | 0.18349 | 1.748% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-16 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-17 | 10.508 | 10.5 | 0.0080032 | 0.07622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-02-17 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-17 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-02-17 08:58 | 180.1593 | 180 | 0.15931 | 0.0885% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-18 | 10.5538 | 10.5 | 0.053783 | 0.5122% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-02-18 | 10.5596 | 10.5 | 0.059582 | 0.5674% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-18 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-19 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-20 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-21 | 10.5538 | 10.5 | 0.053783 | 0.5122% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0012 | San Francisco | 2012-02-21 | 10.7198 | 10.5 | 0.21981 | 2.093% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-21 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-02-22 | 10.523 | 10.5 | 0.022958 | 0.2186% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-22 | 10.5309 | 10.5 | 0.030893 | 0.2942% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-02-22 | 10.7587 | 10.5 | 0.25872 | 2.464% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2012-02-22 | 10.6447 | 10.5 | 0.14468 | 1.378% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0012 | San Francisco | 2012-02-22 | 10.6099 | 10.5 | 0.10994 | 1.047% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-22 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-23 | 10.6225 | 10.5 | 0.12245 | 1.166% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-02-23 | 10.6283 | 10.5 | 0.12825 | 1.221% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-02-23 | 10.9922 | 10.5 | 0.4922 | 4.688% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0035 | Stockton | 2012-02-23 | 10.674 | 10.5 | 0.17403 | 1.657% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-23 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FCT_PT0005 | Yosemite | 2012-02-23 14:28 | 182.6189 | 180 | 2.6189 | 1.455% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-02-24 | 10.5939 | 10.5 | 0.093917 | 0.8944% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-24 | 10.5996 | 10.5 | 0.099563 | 0.9482% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-02-24 | 10.7473 | 10.5 | 0.24728 | 2.355% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-02-24 | 10.6466 | 10.5 | 0.14656 | 1.396% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-24 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-25 | 10.5004 | 10.5 | 0.00037289 | 0.003551% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-02-25 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-02-25 | 10.8709 | 10.5 | 0.37088 | 3.532% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-25 | 10.8 | 10.5 | 0.3 | 2.857% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-26 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-27 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OPP_PT0002 | Diablo | 2012-02-27 17:14 | 101.1185 | 100 | 1.1185 | 1.119% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-02-28 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-02-29 | 10.5614 | 10.5 | 0.061413 | 0.5849% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-03-01 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3048 | REU_PT0001 | North Coast | 2012-03-01 | 14 | 10.5 | 3.5 | 33.33% | Maintenance Operations Quality | HU |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-02 | 10.5004 | 10.5 | 0.00037289 | 0.003551% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-03-02 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | RNW_PT0001 | North Bay | 2012-03-02 09:48 | 451.6511 | 450 | 1.6511 | 0.3669% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-03-03 | 10.5664 | 10.5 | 0.066449 | 0.6328% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-03 | 10.5156 | 10.5 | 0.015633 | 0.1489% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-03 | 10.6283 | 10.5 | 0.12825 | 1.221% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-03 | 10.5413 | 10.5 | 0.04127 | 0.3931% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2012-03-03 | 10.777 | 10.5 | 0.27704 | 2.638% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-03-03 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-03-04 | 10.5436 | 10.5 | 0.043559 | 0.4148% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-04 | 10.5538 | 10.5 | 0.053783 | 0.5122% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-04 | 10.7473 | 10.5 | 0.24728 | 2.355% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-04 | 11.1753 | 10.5 | 0.67532 | 6.432% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FST_PT0043 | Stockton | 2012-03-04 | 10.5916 | 10.5 | 0.091628 | 0.8726% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2012-03-04 | 10.7953 | 10.5 | 0.29535 | 2.813% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-03-04 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FCT_PT0003 | Yosemite | 2012-03-04 15:05 | 180.4566 | 180 | 0.45657 | 0.2536% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-03-05 | 10.5367 | 10.5 | 0.036692 | 0.3494% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-05 | 10.5309 | 10.5 | 0.030893 | 0.2942% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-05 | 10.7473 | 10.5 | 0.24728 | 2.355% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-05 | 10.8228 | 10.5 | 0.32282 | 3.074% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2012-03-05 | 10.6901 | 10.5 | 0.19005 | 1.81% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-03-05 | 14.5 | 10.5 | 4 | 38.1% | Maintenance Operations Quality | HU |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-06 | 10.508 | 10.5 | 0.0080032 | 0.07622% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-06 | 10.6283 | 10.5 | 0.12825 | 1.221% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-06 | 10.7885 | 10.5 | 0.28848 | 2.747% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SMY_PT0031 | Sierra | 2012-03-06 | 11.2695 | 10.5 | 0.76946 | 7.328% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-03-08 | 10.5367 | 10.5 | 0.036692 | 0.3494% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-08 | 10.6283 | 10.5 | 0.12825 | 1.221% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | M19_PT0106 | Hollister District | 2012-03-08 08:37 | 503.2237 | 500 | 3.2237 | 0.6447% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-03-09 | 10.5321 | 10.5 | 0.032114 | 0.3058% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-09 | 10.5385 | 10.5 | 0.038523 | 0.3669% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-09 | 10.7381 | 10.5 | 0.23812 | 2.268% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-09 | 10.6305 | 10.5 | 0.13054 | 1.243% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131801 | OCM_PT0001 | Diablo | 2012-03-09 | 407.596 | 405 | 2.596 | 0.641% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 3060 | JDL_PT0001 | Hollister District | 2012-03-09 21:24 | 427.6775 | 394 | 33.6775 | 8.548% | Maintenance Operations Quality | HU |  |  |  | Transmission | Large OP Event | no | no | No | ACE |  | H-19 | GT.STAT.MISC.DOLNRDPLS_
OP | N/A | FEH_PT0003 | Stockton | 2012-03-10 | 10.5538 | 10.5 | 0.053783 | 0.5122% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-10 | 10.7473 | 10.5 | 0.24728 | 2.355% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-10 | 10.7816 | 10.5 | 0.28161 | 2.682% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0001 | Yosemite | 2012-03-10 00:13 | 180.3035 | 180 | 0.30347 | 0.1686% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-11 | 10.5092 | 10.5 | 0.0092239 | 0.08785% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-12 | 10.5156 | 10.5 | 0.015633 | 0.1489% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-12 | 10.6283 | 10.5 | 0.12825 | 1.221% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-12 | 10.6168 | 10.5 | 0.11681 | 1.112% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3061 | JQS_PT0001 | DeAnza | 2012-03-12 10:59 | 190 | 180 | 10 | 5.556% | Gas Contaminants - Liquids | EQ |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-13 | 10.6225 | 10.5 | 0.12245 | 1.166% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-13 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-13 | 10.777 | 10.5 | 0.27704 | 2.638% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-14 | 10.5233 | 10.5 | 0.023263 | 0.2216% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-14 | 10.7381 | 10.5 | 0.23812 | 2.268% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-14 | 10.6397 | 10.5 | 0.1397 | 1.33% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-03-14 20:51 | 180.3465 | 180 | 0.34647 | 0.1925% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-15 | 10.5385 | 10.5 | 0.038523 | 0.3669% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FSN_PT0004 | Stockton | 2012-03-15 | 10.8343 | 10.5 | 0.33426 | 3.183% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FEH_PT0003 | Stockton | 2012-03-16 | 10.5614 | 10.5 | 0.061413 | 0.5849% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3063 | FSN_PT0004 | Stockton | 2012-03-16 | 12.1184 | 10.5 | 1.6184 | 15.41% | Failure - Equipment | EQ |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | FST_PT0043 | Stockton | 2012-03-16 | 10.9396 | 10.5 | 0.43956 | 4.186% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2012-03-16 | 10.6063 | 10.5 | 0.10628 | 1.012% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0014 | San Francisco | 2012-03-16 | 10.7198 | 10.5 | 0.21981 | 2.093% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JMB_PT0002 | San Jose | 2012-03-16 01:08 | 200.1129 | 200 | 0.11289 | 0.05644% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-03-17 01:44 | 180.3465 | 180 | 0.34647 | 0.1925% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FME_PT0032 | Yosemite | 2012-03-18 | 14.8121 | 10.5 | 4.3121 | 41.07% | Maintenance Operations Quality | HU |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | K1A_PT0003 | Topock District | 2012-03-18 00:36 | 779.1298 | 779 | 0.12982 | 0.01667% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-03-21 | 10.6283 | 10.5 | 0.12825 | 1.221% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-21 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-03-21 13:17 | 180.1633 | 180 | 0.16334 | 0.09075% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-03-22 | 10.5115 | 10.5 | 0.011513 | 0.1096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2012-03-22 | 10.6185 | 10.5 | 0.11849 | 1.128% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0014 | San Francisco | 2012-03-22 | 10.8388 | 10.5 | 0.33884 | 3.227% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-03-22 10:08 | 180.3465 | 180 | 0.34647 | 0.1925% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | NLK_PT0002 | San Francisco | 2012-03-22 10:47 | 151.6996 | 150 | 1.6996 | 1.133% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 3067 | NSU_PT0002 | Milpitas District | 2012-03-22 10:58 | 153.714 | 145 | 8.714 | 6.01% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-24 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | NSF_PT0020 | San Francisco | 2012-03-26 | 12.2763 | 10.5 | 1.7763 | 16.92% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3077 | SSD_PT0003 | Rio Vista District | 2012-03-26 03:14 | 700.1465 | 700 | 0.14648 | 0.02093% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | SSA_PT0131 | Sacramento | 2012-03-27 | 12.8626 | 10.5 | 2.3626 | 22.5% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3084 | FSN_PT0003 | Stockton | 2012-03-29 | 178.892 | 175 | 3.892 | 2.224% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-03-30 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3085 | FSN_PT0003 | Stockton | 2012-03-30 | 178.816 | 175 | 3.816 | 2.181% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2012-03-30 | 10.6185 | 10.5 | 0.11849 | 1.128% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0001 | Yosemite | 2012-03-30 23:58 | 180.5283 | 180 | 0.52829 | 0.2935% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2012-03-31 | 10.7772 | 10.5 | 0.27719 | 2.64% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SMY_PT0031 | Sierra | 2012-03-31 | 11.8737 | 10.5 | 1.3737 | 13.08% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0001 | Yosemite | 2012-03-31 01:35 | 180.6046 | 180 | 0.60459 | 0.3359% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-03-31 03:21 | 180.5255 | 180 | 0.52554 | 0.292% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 3079 | RER_PT0001 | North Coast | 2012-03-31 03:58 | 351.5588 | 350 | 1.5588 | 0.4454% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | RRS_PT0001 | North Coast | 2012-03-31 03:59 | 351.0705 | 350 | 1.0705 | 0.3058% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | RUN_PT0001 | North Coast | 2012-03-31 03:59 | 352.131 | 350 | 2.131 | 0.6089% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JAJ_PT0002 | San Jose | 2012-03-31 11:08 | 200.3205 | 200 | 0.32045 | 0.1602% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | JMX_PT0001 | Central Coast | 2012-03-31 13:43 | 130.0224 | 130 | 0.022427 | 0.01725% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-04-02 | 10.5092 | 10.5 | 0.0092239 | 0.08785% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-04-03 | 10.5184 | 10.5 | 0.01838 | 0.175% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Fresno | 2012-04-03 | 11.6354 | 10.5 | 1.1354 | 10.81% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0101 | Sacramento | 2012-04-03 | 10.5278 | 10.5 | 0.027833 | 0.2651% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131814 | SSW_PT0002 | Sacramento | 2012-04-06 | 533.892 | 533 | 0.892 | 0.1674% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-04-07 | 10.6374 | 10.5 | 0.13741 | 1.309% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-04-08 | 10.7129 | 10.5 | 0.21294 | 2.028% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-04-08 | 10.8572 | 10.5 | 0.35715 | 3.401% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FWA_PT0030 | Yosemite | 2012-04-08 | 10.5115 | 10.5 | 0.011513 | 0.1096% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-04-09 | 10.6374 | 10.5 | 0.13741 | 1.309% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-04-10 | 10.5092 | 10.5 | 0.0092239 | 0.08785% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3101 | OC2_PT2106 | East Bay | 2012-04-10 | 11.2 | 10.5 | 0.7 | 6.667% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 3092 | SSA_PT0101 | Sacramento | 2012-04-10 | 13.9338 | 10.5 | 3.4338 | 32.7% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-04-11 07:46 | 180.1593 | 180 | 0.15931 | 0.0885% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 131815 | AAN_PT0191 | Los Medanos District | 2012-04-14 06:01 | 602 | 600 | 2 | 0.3333% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 3105 | F1J_PT0030 | Yosemite | 2012-04-15 | 10.6328 | 10.5 | 0.13283 | 1.265% | SP Too Close to MOP |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 3106 | F1J_PT0030 | Yosemite | 2012-04-16 | 10.5985 | 10.5 | 0.098495 | 0.938% | SP Too Close to MOP |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 3107 | FFN_PT0041 | Fresno | 2012-04-16 | 10.519 | 10.5 | 0.019 | 0.181% | SP Too Close to MOP |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | F1J_PT0030 | Yosemite | 2012-04-17 | 10.6923 | 10.5 | 0.19234 | 1.832% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3126 | JSJ_PT0037 | San Jose | 2012-04-17 | 10.6063 | 10.5 | 0.10628 | 1.012% | SP Too Close to MOP |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 3108 | FFN_PT0041 | Fresno | 2012-04-18 | 10.51 | 10.5 | 0.01 | 0.09524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2012-04-18 | 10.765 | 10.5 | 0.26498 | 2.524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3102 | OC2_PT2106 | East Bay | 2012-04-18 | 11.6 | 10.5 | 1.1 | 10.48% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | SSA_PT0101 | Sacramento | 2012-04-18 | 13.5493 | 10.5 | 3.0493 | 29.04% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2012-04-19 | 10.765 | 10.5 | 0.26498 | 2.524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3109 | FWA_PT0030 | Yosemite | 2012-04-20 | 10.5161 | 10.5 | 0.016091 | 0.1533% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2012-04-20 | 11.0824 | 10.5 | 0.58239 | 5.547% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3110 | OC1_PT0041 | East Bay | 2012-04-20 | 11.5 | 10.5 | 1 | 9.524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 3112 | OC1_PT0047 | East Bay | 2012-04-20 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | K1A_PT0003 | Topock District | 2012-04-20 10:17 | 779.7225 | 779 | 0.72254 | 0.09275% | Unknown/ Not Recorded |  |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | 131821 | ATN_PT0002 | Burney District | 2012-04-21 | 908 | 905 | 3 | 0.3315% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | Yes | No | ACE |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2012-04-21 | 11.0824 | 10.5 | 0.58239 | 5.547% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 131820 | MIR_PT0007 | Milpitas District | 2012-04-21 | 250.086 | 250 | 0.086 | 0.0344% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 3115 | OC1_PT0046 | East Bay | 2012-04-21 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 3117 | FSN_PT0004 | Stockton | 2012-04-22 | 10.539 | 10.5 | 0.038981 | 0.3713% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 3119 | FST_PT0051 | Stockton | 2012-04-22 | 10.546 | 10.5 | 0.046 | 0.4381% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | JSJ_PT0037 | San Jose | 2012-04-22 | 11.0824 | 10.5 | 0.58239 | 5.547% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3111 | OC1_PT0041 | East Bay | 2012-04-22 | 10.6 | 10.5 | 0.1 | 0.9524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 3116 | OC1_PT0046 | East Bay | 2012-04-22 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 131822 | MIR_PT0007 | Milpitas District | 2012-04-22 02:44 | 250.0801 | 250 | 0.080105 | 0.03204% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | SNH_PT0010 | Sacramento | 2012-04-22 16:25 | 180.5255 | 180 | 0.52554 | 0.292% | SP Too Close to MOP |  |  |  |  | Transmission | Small OP Event | Yes | no | No | No |  |  | #N/A
OP | 3118 | FSN_PT0004 | Stockton | 2012-04-23 | 10.5298 | 10.5 | 0.029825 | 0.284% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 131824 | JSJ_PT0037 | San Jose | 2012-04-23 | 11.0702 | 10.5 | 0.57018 | 5.43% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 131826 | JSI_PT0002 | Milpitas District | 2012-04-23 13:24 | 206.9707 | 201 | 5.9707 | 2.971% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 131824 | JSJ_PT0037 | San Jose | 2012-04-24 | 10.765 | 10.5 | 0.26498 | 2.524% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | N/A | RRF_PT0001 | North Bay | 2012-04-29 02:23 | 450.7492 | 450 | 0.74924 | 0.1665% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Fresno | 2012-04-30 | 11.7544 | 10.5 | 1.2544 | 11.95% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0101 | Sacramento | 2012-05-01 | 11.2603 | 10.5 | 0.7603 | 7.241% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0041 | Fresno | 2012-05-04 | 10.5092 | 10.5 | 0.0092239 | 0.08785% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3122 | JSJ_PT0031 | San Jose | 2012-05-04 | 13.6131 | 10.5 | 3.1131 | 29.65% | Maintenance Operations Quality | HU |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 3128 | SNH_PT0010 | Sacramento | 2012-05-07 08:11 | 180.3424 | 180 | 0.34242 | 0.1902% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | N/A | SSA_PT0101 | Sacramento | 2012-05-08 | 11.8097 | 10.5 | 1.3097 | 12.47% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FME_PT0032 | Yosemite | 2012-05-09 | 11.4549 | 10.5 | 0.95488 | 9.094% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | OC2_PT0102 | East Bay | 2012-05-10 | 10.7 | 10.5 | 0.2 | 1.905% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | SSA_PT0101 | Sacramento | 2012-05-10 | 10.9398 | 10.5 | 0.43985 | 4.189% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | N/A | FFN_PT0053 | Fresno | 2012-05-16 | 10.5825 | 10.5 | 0.082472 | 0.7854% | Unknown/ Not Recorded |  |  |  |  | LP Distribution | #REF! |  | no | No | No |  |  | #N/A
OP | 3142 | N/A | Sacramento | 2012-05-16 | 635 | 275 | 360 | 130.9% | Failure - Equipment | EQ |  |  |  | Transmission | Large OP Event | no | no | No | ACE |  | H-14 | GT.STAT.MISC.CORDELIACH
OP | 131843 | OC2_PT2106 | East Bay | 2012-05-24 | 11 | 10.5 | 0.5 | 4.762% | Maintenance Operations Quality | HU |  |  |  | LP Distribution | #REF! |  | no | No | ACE |  |  | #N/A
OP | 131844 | SYC_PT0001 | Sierra | 2012-05-25 | 608 | 600 | 8 | 1.333% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 131845 | SHS_PT0004 | Willows District | 2012-05-28 | 755 | 737 | 18 | 2.442% | Gas Control Center Operations | HU |  |  |  | Transmission | Small Excursion | Yes | no | No | ACE |  |  | #N/A
OP | 131858 | NMA_PT0011 | Milpitas District | 2012-06-12 | 153.394 | 145 | 8.394 | 5.789% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 131866 | K12_PT0002 | Kettleman District | 2012-06-26 | 673.986 | 669 | 4.986 | 0.7453% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | Yes | No | ACE |  |  | #N/A
OP | 131881 | SSD_PT0003 | Rio Vista District | 2012-07-25 03:42 | 703.44 | 700 | 3.44 | 0.4914% | SP Too Close to MOP |  |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 3270 | OIS_PT0001 | Tracy District | 2012-07-28 08:49 | 164.514 | 160 | 4.514 | 2.821% | Maintenance Operations Quality |  |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 131891 | RCI_PT0003 | North Coast | 2012-08-06 17:43 | 151.05 | 150 | 1.05 | 0.7% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 131906 | BMD_PT0001 | McDonald Island District | 2012-08-14 10:45 | 1027 | 1025 | 2 | 0.1951% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | Yes | No | ACE |  |  | #N/A
OP | 3379 | N/A | Humboldt | 2012-09-01 | 395 | 60 | 335 | 558.3% | Failure - Equipment | EQ |  |  |  | HP Distribution | Large OP Event | no | no | No | ACE |  | H-10 | #N/A
OP | 131928 | K2A_PT0003 | Topock District | 2012-09-02 09:57 | 682.38 | 682 | 0.38 | 0.05572% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 131967 | Unknown | North Bay | 2012-10-17 | 177 | 175 | 2 | 1.143% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 131970 | SNH_PT0011 | Sacramento | 2012-10-19 | 180.346 | 180 | 0.346 | 0.1922% | Failure - Equipment | EQ |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 131971 | OMA_PT0001 | East Bay | 2012-10-19 | 120.514 | 120 | 0.514 | 0.4283% | Failure - Equipment |  |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 131974 | FHE_PT0002 | Yosemite | 2012-10-23 | 400.6 | 400 | 0.6 | 0.15% | Maintenance Operations Quality | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 131979 7000333 | AAN_PT0SP5 | Los Medanos District | 2012-10-26 | 344.5 | 338 | 6.5 | 1.923% | Gas Control Center Operations | HU |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 154277 | N/A | Sacramento | 2012-11-21 | 435 | 425 | 10 | 2.353% | Gas Contaminants - Sulfur | EQ |  |  |  | Transmission | #REF! | Yes | no | No | ACE |  |  | #N/A
OP | 154272 | N/A | East Bay | 2012-12-02 08:00 | 10.8 | 10.5 | 0.3 | 2.857% | Failure - Flooding | EQ |  |  |  | LP Distribution | #REF! | no | no | No | ACE |  |  | #N/A
OP | 154270 | FST_PT0035 | Stockton | 2012-12-02 09:37 | 12.8 | 10.5 | 2.3 | 21.9% | Failure - Flooding | EQ |  |  |  | LP Distribution | #REF! | no | no | No | ACE |  |  | #N/A
OP | 154271 | FST_PT0037 | Stockton | 2012-12-02 09:40 | 14.5657 | 10.5 | 4.0657 | 38.72% | Failure - Flooding | EQ |  |  |  | LP Distribution | #REF! | no | no | No | ACE |  |  | #N/A
OP | 150325/154282 | N/A | North Valley | 2012-12-06 | 120 | 60 | 60 | 100% | Design Issue | EQ |  |  |  | HP Distribution | Large OP Event | no | no | No | ACE |  | H-14 | #N/A
OP | 154268 | SI_ELD_R512 | Sierra | 2012-12-14 | 64.4 | 60 | 4.4 | 7.333% | Gas Contaminants - Liquids | EQ |  |  |  | HP Distribution | #REF! | no | no | No | ACE |  |  | #N/A
OP | 154280 | ACD_PT0033 | Rio Vista District | 2012-12-23 | 719 | 650 | 69 | 10.62% | Design Issue | EQ |  |  |  | Transmission | Large OP Event | no | no | No | ACE |  | H-19 | #N/A
OP | 154269 | Relief Valve | Stockton | 2013-01-02 11:00 | 80 | 60 | 20 | 33.33% | Maintenance Operations Quality | HU | P50.2 | Relief vavle was inadvertently closed. | Filing self-report on non-OQ operation; preparing broad communication plan/tailboard on root causes of events and new corrective action program; | HP Distribution | Large OP Event | no | no |  | ACE |  | H-14 | GD.STAT.DIST.00778
OP | 154251 | M19_PT0106 | Hollister District | 2013-01-12 08:33 | 508.412 | 500 | 8.412 | 1.682% | SP Too Close to MOP |  |  |  | Need investment plan to implement 5/20 policy at this station; on-site evaluation of controls and valves will recommend station rebuild for controls and valve actuators at end of service life; training and communication on regulator and monitor setpoint required deltas | Transmission | #REF! | Yes | no |  | ACE |  | CAT A | GT.STAT.MISC.HLLSTRPLS_ | 282255.pdf
OP | 154254 | Gauge | Sacramento | 2013-01-15 07:45 | 650 | 57 | 593 | 1040% | Maintenance Operations Quality | HU | P95.8 | Relief vavle was inadvertently closed. | Filing self-report on non-OQ operation being evaluated; preparing broad communication plan/tailboard on root causes of events and new corrective action program; replacing service and High-Pressure Regulator (HPR) | HP Distribution | Large OP Event | no | no |  | ACE |  | H-14 | GD.STAT.DIST
OP | 150462 | Chart Recorder | Sacramento | 2013-01-18 03:00 | 51.5 | 50 | 1.5 | 3% | Gas Contaminants - Sulfur | EQ |  | Found some sulfur in the pilots and R-1 failed initial lock up | Crew rebuilt all the pilots, regs, and monitors on both runs as a precaution. Will have Sulfur Gone filters installed. | HP Distribution | #REF! | no | no |  | ACE |  | H14 | GD.STAT.DIST.01030
OP | 154250 7000078 7000278 | ACD_PT0033 | Rio Vista District | 2013-01-18 05:38 | 525.7 | 520 | 5.7 | 1.096% | Design Issue |  |  |  | Team working to resolve Becker valve controls package problems (linking gas past o-rings causes valve actuator to malfunction leading to loss of pressure control) | Transmission | #REF! | Yes | no |  | ACE |  | CAT A | GT.STAT.MISC.CREEDPLS__ | 182416.pdf
OP | 154250 7000078 7000278 | ACD_PT009B | Rio Vista District | 2013-01-18 06:44 | 652.4 | 650 | 2.4 | 0.3692% | Failure - Equipment |  |  |  | Team working to resolve Becker valve controls package problems (linking gas past o-rings causes valve actuator to malfunction leading to loss of pressure control). Monitor tuned to provide better control below MAOP of 650 psig. | Transmission | #REF! | Yes | no |  | ACE |  | CAT A | GT.STAT.MISC.CREEDPLS__ | 182416.pdf
Near Hit | 154231 7000330 | OC2_PT2109 | East Bay | 2013-01-18 10:21 | 14 | 10.5 | 3.5 | 33.33% | Communication |  |  |  | • East Bay T&R to replace the DATEL RTU equipment with new, updated communication equipment. The DATEL RTU equipment at this site is to be replace by the end of 2013 in an ongoing RTU equipment replacement project by Gas Engineering • see 7003570 | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00096 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\182416.pdf
OP | 154249 | SNH_PT0007 | Sacramento | 2013-01-20 04:24 | 510.1 | 500 | 10.1 | 2.02% | Maintenance Operations Quality | HU |  |  | Filing self-report on non-OQ operation; preparing broad communication plan/tailboard on root causes of events and new corrective action program; identifying gaps in OQ and in training for gas control techs | Transmission | Small Excursion | Yes | no |  | ACE |  | CAT A | GT.STAT.MISC.NSACHOLDER | 382860.pdf
OP | 154242 | FFN_PT0104 | Fresno | 2013-01-24 01:11 | 60.0649 | 60 | 0.0649 | 0.1082% | SP Too Close to MOP |  |  |  | Field to complete B inspection to determine root cause | HP Distribution | #REF! | no | no |  | ACE |  | H14 | GD.STAT.DIST.00663
OP | 154243 | Gauge | Stockton | 2013-02-04 10:14 | 216 | 120 | 96 | 80% | Maintenance Operations Quality | HU | P50.2 | Operated valve without watching gauge pressure. | Will file self-report on non-OQ operation; | Transmission | Large OP Event | no | no |  | ACE |  | H-14 | GT.STAT.MISC |  | H14
OP | 154244 7000279 | FRI_PT0002 | Tracy District | 2013-02-04 10:59 | 415.825 | 408 | 7.825 | 1.918% | Maintenance Operations Quality | HU |  |  | DOT Drug Test administered; preparing broad communication plan/tailboard on root causes of events and new corrective action program; Contributing cause is Standard-Policy Conflict - cannot implement 5/20 | Transmission | #REF! | Yes | no |  | ACE |  | CAT A | GT.STAT.MISC.RIPONMDSTO | 183972.pdf
OP | 154314 | Chart Recorder | Yosemite | 2013-02-04 14:00 | 61 | 60 | 1 | 1.667% | Gas Contaminants - Debris | EQ |  | found mill scale in the pilot regulator filter affecting flow to the pilot | The outlet pressure was immediately re-set below 60 psi to prevent another occurrance, then an internal inspection was performed to resolve the pressure control issues. | HP Distribution | #REF! | no | no |  | ACE |  | H14 | GD.STAT.DIST.00727
OP | 159652 7000136 | SSA_PT0104 | Sacramento | 2013-03-15 08:59 | 151.61 | 147 | 4.61 | 3.136% | Maintenance Operations Quality | HU |  |  | DOT Drug Test administered; preparing broad communication plan/tailboard on root causes of events and new corrective action program; Contributing cause is Standard-Policy Conflict - cannot implement 5/20 | Transmission | #REF! | Yes | no |  | ACE
Near Hit | 154513 | O50_PT0001 OES_PT0002 | East Bay | 2013-03-16 10:37 | 148.497 | 150 | -1.503 | -1.002% | HF/WPE - Field O&M |  |  |  |  | Transmission | Near Hit | No | No
Near Hit | 154665 7000027 | OPB_PT0001 OCQ_PT0002 | East Bay | 2013-03-20 09:30 | 143.612 | 150 | -6.388 | -4.259% | HF/WPE - Field O&M |  |  |  | • Require Local Trans & Distr Planning to review all Gas Transmission clearances (pending SAP program to correct this issue) • Coordinate (No additional info) | Transmission | Near Hit | No | No
OP | 159616 7000026 | Gauge | Mission | 2013-03-30 10:30 | 310 | 250 | 60 | 24% | Maintenance Operations Quality | HU | P50.2 | Potentially missed clearance steps. | leak survey performed. L105N pressure reduced to 230 psig. DRs closed again. Engineering evaluating if further actions required. | Transmission | Large OP Event | no | no |  | ACE |  | H-14 | GT.STAT.MISC |  | H14
OP | 159789 7000135 | SFR_PT0001 | Sacramento | 2013-04-11 01:28 | 151.175 | 150 | 1.175 | 0.7833% | Gas Contaminants - Debris | EQ |  | Reg failed lock up and debris was found in the pilot cartridge which caused the reg failure. | T&R completed inspection of reg and monitors - pilot cartridges rebuilt and reg is functioning properly. | Transmission | #REF! | Yes | no |  | ACE |  | CAT B | GT.STAT.MISC.FLORINMNSN | 0811584.pdf
OP | 160282 | KE_RGC_R522 FRN_PT0002 | Kern | 2013-04-16 04:23 | 56.2 | 55 | 1.2 | 2.182% | Maintenance Operations Quality |  |  | Performing lock-up test |  | HP Distribution | #REF! | no | no |  | ACE |  | H14 | GD.STAT.DIST.00619
OP | 160527 7000132 | RCC_PT0002 | Humboldt | 2013-04-26 00:08 | 376.3 | 370 | 6.3 | 1.703% | Gas Control Center Operations | HU |  |  | Local T&R swapped regulation to a 1/4 turn plug valve controlled by a Becker Controller at Cummings Creek, as it has shown to not react to reduced flow as does the Mooney. Planning allowed T&R to reduce regulation down to 360 psig for the duration of the TROP (and OPP set to MOP). | Transmission | #REF! | Yes | no |  | ACE |  | CAT A | GT.STAT.MISC.CUMMINGSCK | 082474.pdf
OP | 160574 250904 7000131 | Chart Recorder | Yosemite | 2013-04-30 | 101 | 60 | 41 | 68.33% | Failure - Equipment | EQ | P5 | Leaking bypass valve | Leak survey performed on the system and lowered system pressure to 50 psig. Determined regulator stn by-pass valve was leaking by. Valve was greased and a small H202 blow-off valve was installed and set for 60 psig. | HP Distribution | Large OP Event | no | no |  | ACE |  | H-14 | GD.STAT.DIST
OP | 245926 | SF_SF_R090 | San Francisco | 2013-05-15 09:29 | 10.5552 | 10.5 | 0.0552 | 0.5257% | Maintenance Operations Quality | HU |  |  | T&R checked LP system after pressure fluctuation due to bagging | LP Distribution | Small OP Event | no | no |  | ACE |  |  | GD.STAT.LPRS.00031
OP | 250145 | Chart Recorder | Sierra | 2013-05-28 | 52 | 50 | 2 | 4% | Failure - Equipment | EQ |  | Regulator failed to lock up | T&R rebuilt the pilot on the regulator due to wear on the stem and checked the monitor, relief and backflow regulator. The station was operating normally upon departure. | HP Distribution | #REF! | no | no |  | ACE |  |  | 0
OP | 250214 | RNW_PT0005 | North Bay | 2013-06-06 16:52 | 450.685 | 450 | 0.685 | 0.1522% | Failure - Equipment |  |  |  | Work on clearance then preceded after checking with engineering. | Transmission | #REF! | Yes | no |  | ACE |  | CAT A | GT.STAT.MISC.NAPAYREGST | 385170.pdf
Near Hit | 7001173 | EB_CRK_EX25_PT1 | East Bay | 2013-06-11 17:35 | 46.76 | 400 | -353.24 | -88.31% | HF/WPE - Field O&M |  |  |  | Opened valve 23 to release pressure (valve should be normally open). No corrective actions taken beyond the intitial corrective actions taken during the event. | Transmission | Near Hit | No | No
OP | 257843 | KEK_PT0002 | Fresno | 2013-06-12 20:36 | 658.19 | 650 | 8.19 | 1.26% | Maintenance Operations Quality |  |  |  |  | Transmission | #REF! | Yes | no |  | ACE |  | CAT A | GT.STAT.MISC.ELKHORNSTA | 085549.pdf
Near Hit | 258110 7000105 | K4B_PT0004 | Kettleman District | 2013-06-30 | 746.2 | 754 | -7.8 | -1.034% | HF/WPE - Gas Control |  |  |  | • Controls engineering to look into implementing a valve max control scheme similar to PLS3 to prevent this type of event • Implement a better control scheme using “Valve Max” and pressure setpoint control algorithm similar to PLS 1, 2, and 3 RTUs. • Review the possibility that similar problem could occur on other PLS stations that don’t have the PLS 3 type RTU ramp program applied • Investigate Relief V-A | Transmission | Near Hit | No | No
Near Hit | 7001247 | NLP_PT0101 | San Francisco | 2013-07-19 01:48 | 144.866 | 145 | -0.134 | -0.09241% | HF/WPE - Field O&M |  |  |  |  | Transmission | Near Hit | No | No
Near Hit | 7001248 | OES_PT0002 | East Bay | 2013-07-25 09:42 | 121.03 | 121 | 0.03 | 0.02479% | Equipment - Other |  |  |  | • Review operating diagram and the location of the pressure gauges. • 0.5 psig may be the tolerance for not calling and event an OP vs Near hit | Transmission | Near Hit | Yes | No
OP | 263063 | SAE_PT0002 | Sacramento | 2013-08-07 22:47 | 175.76 | 175 | 0.76 | 0.4343% | Failure - Equipment |  |  |  | T&R reduced pressure by station blow-off valve and then switched district reg to feed on isolated section of DFM 0618-02 to help draw away leaking gas. This DFM section was deactivated and not returned to service as part of system uprate on 8/14/2013. | Transmission | #REF! | Yes | no |  | ACE |  | CAT B | GT.STAT.MISC.ANTELOPERM | 081623.pdf
OP | 279057 7000038 | Gauge | North Valley | 2013-08-08 11:00 | 80 | 60 | 20 | 33.33% | Gas Contaminants - Debris | EQ | P5 | Metallic particle contamination debris | 1) Set point lowered to from 57 psig to 40 psig 2) A Fisher H202 RV was added to the station as OPP 3) Both Runs have been cleared of debris contamination 4) Mains leak survey August 8th – no issues found | HP Distribution | Large OP Event | no | no |  | ACE |  | H-14 | GD.STAT.DIST.01439 |  | H14
Near Hit | 263026 7000103 | SHS_PT0004 SBV_PT0001 SWG_PT0002 | Willows District | 2013-08-12 05:12 | 679.6 | 708 | -28.4 | -4.011% | Equipment - Other |  |  |  | Completed | Transmission | Near Hit | No | No
Near Hit | 7001253 | AAN_PT0114S BRT_PT0114S | Los Medanos District | 2013-08-12 15:40 | 370 | 368 | 2 | 0.5435% | HF/WPE - Gas Control |  |  |  |  | Transmission | Near Hit | No | No
OP | 263301 263249 7000101 | SYC_PT0007 | Sierra | 2013-08-17 00:15 | 531.4 | 525 | 6.4 | 1.219% | Design Issue |  |  |  | More closely monitor Mooney performance when supply pressures decrease | Transmission | #REF! | Yes | no |  | ACE |  | CAT A | GT.STAT.MISC.YUBACITYUH | 284091.pdf
OP | 263371 263713 7000371 | Chart Recorder | North Valley | 2013-08-19 13:39 | 650 | 469 | 181 | 38.59% | Design Issue | EQ | P5 | Regulation failed to lockup. | At Grape Way the regulation station lead run was isolated on Monday (8/19) and the standby run was put into service at the new reduced pressure for TROP from engineering. The failed run was rebuilt and placed back in service on Thursday (8/22). We will be maintain flow out of the downstream district regulator station at Kennedy, to allow for more flow to be drawn from Grape Way Regulation Station until L-177B is tied back in (tentatively scheduled for 8/29). We set a portable ERX to monitor pressure. | Transmission | Large OP Event | no | no |  | ACE |  | H-19 | GT.STAT.MISC.GRAPEWAYRG | 086447.pdf
OP | 271642 7000090 | SJ_SJ_RF55 | San Jose | 2013-09-10 12:38 | 29.98 | 10.5 | 19.48 | 185.5% | Maintenance Operations Quality | HU | P50.2 | Valve inadvertently operated beyond its stops. | Need to install stops on valve and relocate chain to eliminate interference with valve operation. | LP Distribution | Large OP Event | no | no |  | ACE |  | H-14 | GD.STAT.LPRS.00138
OP | 7000491 | JRR_PT0003 JRR_PT0005 | Central Coast | 2013-09-18 10:09 | 312.882 | 303 | 9.882 | 3.261% | Maintenance Operations Quality |  |  |  | Verify pressure regulator secure closed before performing future work. See design criteria….PSRS No. 31891 Job Order No. 31062960 Document No. 0806325 | Transmission | #REF! | Yes | no |  | ACE |  | CAT A | GT.STAT.MISC.ROBROYREGS | 0811609.pdf
Near Hit | 7001195 | EB_RCH_RH02_PT3 | East Bay | 2013-09-18 11:29 | 14.2 | 10.5 | 3.7 | 35.24% | HF/WPE - Field O&M |  |  |  | • Need to contact codes and standards group to check on this maintenance practice. Ensure Gas Control is aware of work. | LP Distribution | Near Hit | No | No
OP | 278087 7000240 | RNV_PT0001 | North Bay | 2013-10-08 19:30 | 153 | 150 | 3 | 2% | Design Issue |  |  |  | 1) Install sulfagon filters at station 2) Review current clearance and three upcoming clearances and change clearances to address risk of OP due to regulation operating outside of design range 3) Create more reliable notification of ERX alarm to on-call supervisor to improve response to OP events in-lieu of 2014 replacement of ERXs. 4) After validation of planning model for system (utilizing ERX data), consider implementation of 5/20 rule. | Transmission | #REF! | Yes | no |  | ACE |  |  | GT.STAT.MISC.DIABLONOVA | 0800128.pdf
OP | 7009239 | Gauge | Mission | 2013-11-01 | 200 | 175 | 25 | 14.29% | Maintenance Operations Quality | HU | P50.2 | Pressure reduction was inadvertently missed per clearance specifications. | Upon discovery in February 18th 2014 – I&R supervisor worked with Control Center and PLE in the set point change order. And the reg set point at Smith Street Station was lowered below the new MAOP of 175 psig. Regulator on the primary run was lowered from 200 psig to 155 psig and secondary run from 190 psig and 145 psig. Both monitors were lowered from 209 psig to 170 psig. | Transmission | Large OP Event | Yes | No | No | ACE | No | H-14 | GT.STAT.MISC.SMITHLN153 | 0800292.pdf
OP | 7000484 | FR_FRE_EX04 | Fresno | 2013-11-04 | 12.4 | 12 | 0.4 | 3.333% | Maintenance Operations Quality | HU |  |  | Future corrective actions might include working on clearance after checking with engineering. Also additional training is suggested | LP Distribution | Small OP Event | no | no |  | ACE |  |  | GD.STAT.LPRS.00257
Near Hit | 7001211 / 7000597 | FST_PT043 | Stockton | 2013-11-18 13:22 | 10.5919 | 10.5 | 0.0919 | 0.8752% | HF/WPE - Field O&M |  |  |  | • Review design standards and work procedures and update if necessary. | LP Distribution | Near Hit | No | No
Near Hit | 7001196 | FST_PT0061 | Stockton | 2013-11-19 12:51 | 12.0111 | 10.5 | 1.5111 | 14.39% | Design Issue - Other |  |  |  | • Review design and work procedures and update if necessary. | LP Distribution | Near Hit | No | No
Near Hit | 7001250 | SHS_PT0026A | Willows District | 2013-11-20 04:43 | 959.257 | 965 | -5.743 | -0.5951% | Equipment - Other |  |  |  | V-8 setpoint raised to 660# to relieve pressure. scheduled valve maintenance in DEC 2013 | Transmission | Near Hit | Yes | No
OP | 7001256 | OCM_PT0002 | Diablo | 2013-11-20 16:24 | 173.345 | 170 | 3.345 | 1.968% | Maintenance Operations Quality |  |  |  | TBD | Transmission | #REF! | yes | No |  | ACE |  |  | GT.STAT.MISC.CONCORDMTR | 0811631.pdf
Near Hit | 7001544 | OC2_PT2109 EB_OAK_RA58_PT3 | East Bay | 2013-11-21 | 14.3 | 10.5 | 3.8 | 36.19% | Communication |  |  |  | • Corrective Actions see CAP ID#7000330 • see 7003570 | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00096
OP | 7001681 | FFN_PT0013 | Fresno | 2013-11-21 05:55 | 414.409 | 400 | 14.409 | 3.602% | Design Issue |  |  |  | • Enter the Nov. 21, 2013 OP event at Fresno GLC into the Corrective Action Program • Ensure that PSEP designs/works are reviewed by Pipeline Engineering & Design • Lower the regulator and monitor set points • There is no sign of a bypass across monitor (V-107) and regulator (V-108). Determine the safety risk of a single run without a bypass for Fresno GLC and the feasibility of installing a bypass run | Transmission | Small Excursion | no | No |  | ACE |  |  | GT.STAT.MISC.FRESNOLOAD | 3808517.pdf
Near Hit | 7001197 | SGZ_PT0001 | Meridian | 2013-12-11 13:05 | 800.38 | 800 | 0.38 | 0.0475% | Communication |  |  |  | Reset RV to 800 psig Notified Engineering to confirm Relief valve was sized properly Notified Engineering to contact producer for better controls on their system | Transmission | Near Hit | No | No
Near Hit | 7000937 | SHS_PT0026A | Willows District | 2013-12-12 06:58 | 900.272 | 890 | 10.272 | 1.154% | Equipment - Other |  |  |  | • Buckeye V-8 was closed. Tech sent out to gauge L302W; field pressure was the same as citect pressure • Some corrective actions that might prevent a near hit or over pressure event from occurring similar to this in the future are to use a ramp timer valve on crossover valves, or a valve that will allow for % open basis. Allowing some insight into the regulator position (opening %) might also assist. But mostly it should be noted that a full open full closed valve (as is valve 8) is the culprit of this. Design criteria to add ramp timer and ramp open function capabilities seems like the best solution for resolving an issue like this. • Clearance to perform valve maintenance and repairs to take place in December as scheduled • Full open/closed valves are the culprit - Consider using ramp-timer or % openvalves if they are RCVs in the crossover position. • Consider allowing some insight into the regulator position (%opening) in future designs. | Transmission | Near Hit | yes | No
Near Hit | 7001210 | KPF_PT0008 | Yosemite | 2013-12-27 10:15 | 452.78 | 500 | -47.22 | -9.444% | Equipment - Other |  |  |  | • Tech brought the pressure down to 430 psig and Gill Ranch asked Paramount Farms to close one of their station block valve due to the pigging job being done at Gill Ranch. Station engineering confirmed that the Paramount Farms line qualified to 500 psig. The documentation is being submitted to change the operating diagram from 450 to 500 psig. • Advise Paramount Farms to inspect their block valve for possible leakage • Review Set points of monitor & regs | Transmission | Near Hit | No | No
Near Hit | 7001547 | SA_IST_RR01_PT03 | Sacramento | 2013-12-28 | 44 | 42 | 2 | 4.762% | Equipment - Other |  |  |  | • Tech gauge tested the line and compared it to SCADA reading • Determine when was the chart calibrated and further inspect the instrument for possible error (suggestion) • Perform a dead weight on both devices with the same tester and to confirm the differential is repeatable (suggestion) | HP Distribution | Near Hit | Yes | No
Near Hit | 7001574 | SJ_SJ_EX05_PT1 | San Jose | 2014-01-06 23:40 | 57.05 | 60 | -2.95 | -4.917% | SP Too Close to MOP/HiHi |  |  |  | • Monitor point, call back if it reaches 58 psig. MOP is 60 psig. | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
OP | 7001252 | NV_RBL_R125 | North Valley | 2014-01-07 10:32 | 66.9871 | 60 | 6.9871 | 11.65% | Gas Contaminants - Liquids | EQ | P5 | A slug of pipeline liquids and sludge from past hydrotesting flooded regulator station. | • Immediate action to respolve over pressure: T&R switched runs and lowered the pressure to 55 PSIG. • B inspection will take place for further investigation. • Equipment was saturated with large amounts of pipeline liquid - attempt to locate source of liquids. The filters were coated and sense lines to the pilot were dripping upon disassembly. More information to come as the investigation continues. ' Brad Spainhower - to explain more - Liquids moved from the line - multiple times | HP Distribution | Large OP Event | yes | No |  | ACE |  | H-14 | GD.STAT.DIST.00921 |  | GQ
OP | 7001315 7003563 | KT2_PT0100B | Topock District | 2014-01-10 17:44 | 699 | 660 | 39 | 5.909% | Maintenance Operations Quality | HU | P50.2 | Two OP Events: (1) A split station operating mode combined with antiquted equipment resulted in excessive risk of station shutdown and OP. (2) TCS Operator opened valve to reinitiate L-300B, however; he/she did not check pressure upstream and downtream as they were trained to do and actions resulted in second OP. | awaiting confirmation of corrective actions from issue owners to be recorded in SAP/CAP | Transmission | Large OP Event | no | Yes |  | ACE |  | H-19 | GT.STAT.COMP.TOPOCK____ | 383655.pdf | H19
OP | 7001312 | NV_RBL_R125 | North Valley | 2014-01-13 07:52 | 89 | 60 | 29 | 48.33% | Gas Contaminants - Liquids | EQ | P5 | A slug of pipeline liquids and sludge from past hydrotesting flooded regulator station. | • Repeat B inspection • and repairs on affected equipment • Leak Survey on system see 1252 | HP Distribution | Large OP Event | yes | No |  | ACE |  | H-14 | GD.STAT.DIST.00921 |  | GQ
OP | 7001340 | HU_EUR_EX01_PT1 | Eureka | 2014-01-15 05:50 | 11.3 | 10.5 | 0.8 | 7.619% | Failure - Equipment |  |  | Monitor and regulator set points were to close together – this caused equipment to interact in a manner that created control instability and the over pressure event. | • Immediate action was lowering regulator set-point to 8 in-WC. • Daily monitoring of chart will take place during cold weather, high gas demand conditions. Notifications were made as required. • Increase MAOP to 14 in | LP Distribution | Small OP Event | no | No |  | ACE |  |  | GD.STAT.LPRS.00243
Near Hit | 7001571 | HU_ARC_RR09_PT3 | Humboldt | 2014-01-17 11:29 | 60.279 | 60 | 0.279 | 0.465% | SP Too Close to MOP/HiHi |  |  |  | • Investigate accuracy with deadweight test on both devices with same tester • Rebuild station to alter from two elbows to an inline tee | HP Distribution | Near Hit | Yes | No
Near Hit | 7001545 | EB_OAK_RA58_PT3 | East Bay | 2014-01-20 06:48 | 14.3 | 10.5 | 3.8 | 36.19% | Communication |  |  |  | • Additional research may be required. • Corrective Actions see CAP ID#7000330 • see 7003570 | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00096
Near Hit | 7001546 | BRT_PT0010 | Diablo | 2014-01-23 15:49 | 832 | 867 | -35 | -4.037% | HF/WPE - Field O&M |  |  |  | (email sent 2/5 & 2/11 for more info) • Crew was throttling V-42 in order to reduce the pressure and was left open to displace any future leakage • Crew also greased V-2 and V-65 to help reduce leakage • Update the Operating Diagram to reflect the latest MAOP and MOP • Monitor | Transmission | Near Hit | No | No |  |  |  |  | #N/A
Near Hit | 7001720 | SJ_SJ_RG55_PT3 | San Jose | 2014-01-28 23:25 | 55.45 | 60 | -4.55 | -7.583% | SP Too Close to MOP/HiHi |  |  |  | • Continue to Monitor • Send tech out in the morning | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7001745 | CC_CML_RM27_PT3 | Central Coast | 2014-01-29 01:01 | 50.0095 | 52 | -1.9905 | -3.828% | SP Too Close to MOP/HiHi |  |  |  | • Continue to Monitor • Send tech out in the morning | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7001442 | SSW_PT0007 | Sacramento | 2014-01-29 23:00 | 551 | 800 | -249 | -31.13% | HF/WPE - Field O&M |  |  |  | After the GSO got in touch with Oscar Martinez, it was decided that instead of using V-58 to pack L172 out of Swingle Junction, he should have instead used V-54 which would have given him direct control of the pressure entering L172 through V-58. After L172 reached approximately 470#, V-56/V-57 were closed | Transmission | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7001721 | SJ_SJ_RG55_PT3 | San Jose | 2014-01-30 00:20 | 55.11 | 60 | -4.89 | -8.15% | SP Too Close to MOP/HiHi |  |  |  | • Continue to Monitor • Send tech out in the morning | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
OP | 7001532 | OC1_PT0024 | Mission | 2014-02-02 14:00 | 163 | 160 | 3 | 1.875% | Clearance Preparation | HU |  | Clearance set up for ILI did not anticipate regulators would be set outside of prescribed optimum control range. | • Immediate action was to set regulator down to 150 psig. • Consider installing pressure indication & flow metering at A & Yolo (if this reoccurs) • Needs confirmation about a system wide evaluation of regulation where SCADA is not at the deliver point - see notes in Reminders. | Transmission | Small OP Event | yes | No |  | ACE |  |  | #N/A
Near Hit | 7002025 | YO_LBN_RC06_PT3 | Yosemite | 2014-02-12 23:09 | 43.1348 | 44 | -0.8652 | -1.966% | SP Too Close to MOP/HiHi |  |  |  | • Field to address calibration issues • GDCC to monitor pressure, and report • Task: Ask if the calibration cleared the issue: Sheryl Phillips & Sup • Request if the operating point can be reduced so it won't be operating to close to MOP/HiHi | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002021 | SA_WSA_RWS3_PT3 | Sacramento | 2014-02-13 16:25 | 87.77 | 50 | 37.77 | 75.54% | Communication |  |  |  | • Install a New/Repair the RTU at West Capital and 5th Street • Continue to Monitor, see 70000136 | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002027 | YO_LBN_RC06_PT3 | Yosemite | 2014-02-14 01:30 | 43.27 | 44 | -0.73 | -1.659% | SP Too Close to MOP/HiHi |  |  |  | • Field to address calibration issues • GDCC to monitor pressure, and report • Task is to ask if the calibration cleared the issue: Sheryl Phillips & Sup | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002029 | ST_TRA_RT32_PT3 | Stockton | 2014-02-14 01:49 | 26.02 | 28 | -1.98 | -7.071% | SP Too Close to MOP/HiHi |  |  |  | • Task: Does the pressure approach 26 psig on other dates during the cold weather? - no • Task: Alert the field to consider reducing the operating pressure of these regulators down from its current setting at 25 psig, so its not operating so close to the hihi alarm (26 psig). | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002028 | YO_LBN_RC06_PT3 | Yosemite | 2014-02-14 23:12 | 43.12 | 44 | -0.88 | -2% | SP Too Close to MOP/HiHi |  |  |  | • Field to address calibration issues • GDCC to monitor pressure, and report • Task is to ask if the calibration cleared the issue: Sheryl Phillips & Sup | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002024 | KE_RGC_R522_PT3 | Kern | 2014-02-16 23:27 | 52.02 | 55 | -2.98 | -5.418% | SP Too Close to MOP/HiHi |  |  |  | • Review calibration and set points, consider reducing operating set points using 5/20 | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7001900 | KT2_PT0106 | Kern | 2014-02-19 20:30 | 205.2 | 250 | -44.8 | -17.92% | HF/WPE - Field O&M |  |  |  | CAP team has established corrective actions - and non relate to GCSS… this will be tracked by another team. | Transmission | Near Hit | Yes | No |  |  |  |  | #N/A
OP | 7001977 | NLP_PT0101 | Milpitas District | 2014-02-22 14:27 | 151 | 145 | 6 | 4.138% | Clearance Preparation |  |  | The monitor and regulator valves had relatively the same set point to which they interacted in a manner that created control instability, when the operation called adjust set points. Clearance did not provide enough information. | Rebuild station | Transmission | Small OP Event | yes | No |  | ACE |  |  | GT.STAT.MISC.LOMTPKPLS_
Near Hit | 7002048 | EB_OAK_RA58_PT3 | East Bay | 2014-02-24 11:45 | 14.5 | 14 | 0.5 | 3.571% | Communication |  |  |  | • Continue to Monitor • Tech sent on site to confirm pressure - 9.3 in w.c. • Refer to 7000330 to replace the RTU at this location • Corrective Actions see CAP ID#7000330 • see 7003570 | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00096
Near Hit | 7002072 | SA_SAC_RD08_PT3 | Sacramento | 2014-02-26 23:12 | 17.1754 | 14 | 3.1754 | 22.68% | Communication |  |  |  | • send the tech out to gauge the pressure • monitor pressures in the control room • isolated incident - no corrective actions at this time, will review upon repetition | LP Distribution | Near Hit | No | No |  |  |  |  | #N/A
Near Hit | 7002166 | YO_LBN_RC06_PT3 | Yosemite | 2014-03-04 01:18 | 43.02 | 44 | -0.98 | -2.227% | SP Too Close to MOP/HiHi |  |  |  | • Send the tech out to gauge the pressure • Monitor pressures in the control room • This is the 4th hihi event at that same location - it will be suggested to confirm calibration of the gauge, and additionally reduce the regulator set pressure by 1-2 psig in an attempt to reduce hihi breaching alarms | HP Distribution | Near Hit | No | No |  |  |  |  | #N/A
Near Hit | 7002301 | JAW_PT0001 | San Jose | 2014-03-05 00:13 | 323.831 | 330 | -6.169 | -1.869% | Design Issue - Other |  |  |  |  | Transmission | Near Hit | No | No |  |  |  |  | #N/A
Near Hit | 7002204 | ST_TRA_RT32_PT3 | Stockton | 2014-03-05 12:24 | 26.1 | 28 | -1.9 | -6.786% | SP Too Close to MOP/HiHi |  |  |  | • Task: breaching hihi alarm may lead to over pressure event in the future - Field needs to make adjustments on regulator to adjust set points. | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002300 | ALM_PT1004 | Diablo | 2014-03-05 19:52 | 399.296 | 590 | -190.704 | -32.32% | Design Issue - Other |  |  |  |  | Transmission | Near Hit | No | Yes |  |  |  |  | #N/A
Near Hit | 7002205 | YO_LBN_RC06_PT3 | Yosemite | 2014-03-05 22:31 | 43.4 | 44 | -0.6 | -1.364% | SP Too Close to MOP/HiHi |  |  |  | • Corrective actions addressed by 7002116 | HP Distribution | Near Hit | No | No |  |  |  |  | #N/A
Near Hit | 7002167 | SA_SAC_R003_PT3 | Sacramento | 2014-03-06 12:56 | 49.0413 | 50 | -0.9587 | -1.917% | SP Too Close to MOP/HiHi |  |  |  | • This appears to be an isolated incident and immediate corrective actions were to replace the transducer • As a precautionary, the hihi alarm sits very close to the MOP alarm for this district. | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002461 | CC_SCR_RJ03_PT3 | Sacramento | 2014-03-08 19:48 | 47.1864 | 50 | -2.8136 | -5.627% | SP Too Close to MOP/HiHi |  |  |  | Immediate actions were taken following the HIHI alarm breached - GDCC notified on call personnel, a tech was sent out to Felton Reg Station, and the reg set point was lowered to 46 psig (Based on Gas Log - 22:03 Sat. Mar 08) | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002464 | SJ_SJ_RG55_PT3 | San Jose | 2014-03-09 23:44 | 55.94 | 60 | -4.06 | -6.767% | SP Too Close to MOP/HiHi |  |  |  | The local T&R Sup and planner was contacted to discuss the possibility of lowering the reg & monitor set points and other possible CA's. Waiting for response 70002454 for CA | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002465 | SA_CLK_RCL2_PT3 | Sacramento | 2014-03-10 01:00 | 59.48 | 60 | -0.52 | -0.8667% | SP Too Close to MOP/HiHi |  |  |  | Contacted the T&R Sup on 03/12/14 at 09:28 AM but unable to talk to him so left a voice message regarding Clarksburg Prim HIHI breach. Waiting for response | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002466 | BRT_PT0066D | Diablo | 2014-03-12 09:36 | 509 | 722 | -213 | -29.5% | HF/WPE - Manual Operations |  |  |  | Immediate actions were done following the HIHI breach - GTCC contacted Clearance and GT M&C supervisors, clearance was placed on hold and conducted valve position check, found V-42 not fully closed and corrected, updated GTCC and resumed clearance | Transmission | Near Hit | No | No |  |  |  |  | #N/A
Near Hit | 7002401 | SI_ROC_R406_PT3 | Sierra | 2014-03-12 10:32 | 62.41 | 60 | 2.41 | 4.017% | SP Too Close to MOP/HiHi |  |  |  | remove pipe, and tailboard, this is complete | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002457 | ART_PT0002 | North Valley | 2014-03-13 23:05 | 593.336 | 600 | -6.664 | -0.011107 | Design Issue - Other |  |  |  |  | Transmission | Near Hit |  | No |  |  |  |  | #N/A
Near Hit | 7002454 | SJ_SJ_RG55_PT3 | San Jose | 2014-03-16 00:01 | 55.7245 | 60 | -4.2755 | -7.126% | SP Too Close to MOP/HiHi |  |  |  | refer to 70002454 for CA | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002456 | DI_PLH_RC16_PT3 | Diablo | 2014-03-16 00:18 | 57.1 | 60 | -2.9 | -4.833% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002455 | SJ_SJ_RG55_PT3 | San Jose | 2014-03-16 23:42 | 55.6864 | 60 | -4.3136 | -7.189% | SP Too Close to MOP/HiHi |  |  |  | see 7002454 for CA | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002458 | ALM_PT1004 | Diablo | 2014-03-19 23:37 | 408 | 590 | -182 | -0.30847 | Design Issue - Other |  |  |  |  | Transmission | Near Hit | Yes | Yes |  |  |  |  | #N/A
Near Hit | 7002587 | ALM_PT1004 | Diablo | 2014-03-22 00:28 | 397.682 | 590 | -192.318 | -0.32596 | Design Issue - Other |  |  |  |  | Transmission | Near Hit | Yes | Yes |  |  |  |  | #N/A
Near Hit | 7002823 | SA_SAC_R003_PT3 | Sacramento | 2014-03-27 12:18 | 46 | 50 | -4 | -0.08 | Communication |  |  |  | • Follow up with T&R Supervisor to determine if transducer replacement was completed | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002936 7002955 | SF_SF_R037_PT2 | San Francisco | 2014-04-08 23:52 | 52.2528 | 60 | -7.7472 | -0.12912 | SP Too Close to MOP/HiHi |  |  |  | • Follow up with T&R Supervisor - emails have been sent on 4/9 & 4/15 to Mitchell Pena | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7002952 | ST_STK_RR09_PT3 | Stockton | 2014-04-09 02:25 | 10.3172 | 14 | -3.6828 | -0.26306 | SP Too Close to MOP/HiHi |  |  |  | • GDCC will contact planning regarding Harding and Hunter LP set points • Planning group determine appropriate set points for summer operation email sent to GDCC requesting additional information 4.15.14 Update: a follow up email was sent to GDCC on 10/23/14 and responded it was "Completed" | LP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7003207 | SF_SF_R037_PT2 | San Francisco | 2014-04-11 01:06 | 52.0544 | 60 | -7.9456 | -0.13243 | SP Too Close to MOP/HiHi |  |  |  | • Follow up with T&R Supervisor | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7003089 | FFC_PT0002 | Stockton | 2014-04-15 02:37 | 403.43 | 410 | -6.57 | -0.016024 | HF/WPE - Eng Review |  |  |  | • Immediate response | Transmission | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7003181 | EB_OAK_EX07_PT1 | East Bay | 2014-04-16 11:49 | 47.1 | 54 | -6.9 | -0.12778 | Communication |  |  |  | No C/A | HP Distribution | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7003538 | ART_PT0002 | North Valley | 2014-04-30 01:13 | 593.885 | 600 | -6.115 | -0.010192 | Design Issue - Other |  |  |  | Reduced set point pressure to 585 psig | Transmission | Near Hit | Yes | No |  |  |  |  | #N/A
Near Hit | 7003679 | M6A_PT0003 | Central Coast | 2014-05-01 11:45 | 607.3 | 630 | -22.7 | -0.036032 | Equipment - Other |  |  |  | Immediate response: Replace transmitter, check SP of RV on annual VMR inspection | Transmission | Near Hit | Yes | No |  |  |  |  | #N/A
OP | 7003511 | Chart Recorder | San Francisco | 2014-05-06 10:00 | 15 | 12 | 3 | 25% | Maintenance Operations Quality | HU |  | The bagging procedure was performed too fast, destabilizing the regs before they had to take control again. This in addition to GC's deactivation job being performed too close caused the OP event. | Immediate action followed after the incident - M&C crew was sent to stabilize the station CAP 7004145 CAP 7004164 | LP Distribution | Small OP Event | yes | No |  | ACE |  |  | GD.STAT.LPRS.00053
Near Hit | 7003730 | SSA_PT0009 | Sacramento | 2014-05-08 01:45 | 259.011 | 260 | -0.989 | -0.0038038 | Equipment - Sulfur |  |  |  | • Local Sup sent out a Tech to the location first thing in the morning • Tech/Crew installed and completed Sulfagon filters at Sac GLC • Analyze to institute the 5/20 rule if possible. | Transmission | Near Hit | Yes | No |  |  |  |  | GD.STAT.DIST.01090 | \\fairfield07\gis\giswebMiscFiles\GasStations\385186.pdf
Near Hit | 7003680 | BWL_PT0001 | Stockton | 2014-05-12 01:26 | 403.202 | 410 | -6.798 | -0.01658 | HF/WPE - Manual Operations |  |  |  | N/A | Transmission | Near Hit | Yes | No
Near Hit | 7003871 | MMT_PT1112B | Milpitas District | 2014-05-17 08:15 | 530 | 590 | -60 | -0.10169 | Communication |  |  |  | N/A - this can be closed once it has been risk ranked | Transmission | Near Hit | Yes | No
Near Hit | 7003794 | BWL_PT001 | Stockton | 2014-05-21 02:29 | 403.1 | 410 | -6.9 | -0.016829 | SP Too Close to MOP/HiHi |  |  |  | N/A | Transmission | Near Hit | Yes | No
OP | 7004510 | Chart Recorder | Sierra | 2014-06-16 15:00 | 53 | 50 | 3 | 6% | Failure - Equipment | EQ | P5 | Historical lock up issues on Mooney Regulator coupled with Low Flow/No Flow conditions allowed the pressure to creep up and eventually pack the line. | Engineering Review of Station Configuration Immediate actions following the incident were the Reg and Monitor pressure set points were adjusted below the MAOP of 50 psig and the pressure recorder was reset. A review and update of the M-01 American Rice District Reg Data Sheet should be performed so that it accurately shows valid set points and information. | HP Distribution | Small OP Event | Yes | No | No | ACE |  | LVCR | 0 | 0804366 | 46 | 55 | 52
OP | 7004358 | SCX_PT0001 | Sacramento | 2014-06-21 01:38 | 710.387 | 708 | 2.387 | 0.3371% | Design Issue |  |  | Low demand north of the station and inadequate regulation from the California Production Wells caused the rise in pressure on L-172, L-169, L-167 | L-172, 167, and 169 are currently under a CROP of 708 psig. The removal of the CROP would potential restores the MAOP/MOP of 800 psig that provides additional flexibility in avoiding OP Events or near hits. | Transmission | Small OP Event | No | No |  | ACE |  |  | GT.STAT.MISC.HERJCTPLS_
Near Hit | 7004414 | KHJ_PT0005 | Fresno | 2014-06-21 17:17 | 644.7 | 650 | -5.3 | -0.0081538 | Equipment - Other |  |  |  | Have repair kit onhand | Transmission | Near Hit | No | No
Near Hit | 7004563 | MMT_PT00087 | Milpitas District | 2014-06-26 12:35 | 302 | 720 | -418 | -0.58056 | HF/WPE - Gas Control |  |  |  | Sherkan to deliver MAOP of Milpitas Terminal Reiteration to GSO to confirm valve operation completion | Transmission | Near Hit | No | No
Near Hit | 7004562 | M17_PT0001 | Kettleman District | 2014-06-29 06:01 | 803.317 | 839 | -35.683 | -0.04253 | SP Too Close to MOP/HiHi |  |  |  | Corrective Actions: GTCC is in the process of conversing Lesson Learns from this OP near hit with Gas System Operator, Transmission Coordinator, Supervisor, and Manager | Transmission | Near Hit | No | No
OP | 7004583 | RHN_PT0005 | North Bay | 2014-06-30 19:25 | 407 | 400 | 7 | 1.75% | Gas Control Center Operations |  |  | Power outages at the station caused actuator malfunctions. Pressure drop and dead band pressure during valve out of range alarm also contributed to OP event. | Rebuild Station | Transmission | Small OP Event | No | No |  | ACE |  |  | GT.STAT.MISC.HERMANSTAT | 082454.pdf
Near Hit | 7004755 | MIR_PT0012 | Mission | 2014-07-09 05:02 | 336.7 | 420 | -83.3 | -0.19833 | HF/WPE - Manual Operations |  |  |  | N/A | Transmission | Near Hit | No | No
Near Hit | 7004884 | SI_ROC_R406_PT3 | Sierra | 2014-07-15 22:05 | 59.46 | 60 | -0.54 | -0.009 | Equipment - Other |  |  |  | N/A | HP Distribution | Near Hit | No | No
Near Hit | 7004892 | SA_CLK_RCL2_PT3 | Sacramento | 2014-07-16 15:08 | 62.94 | 60 | 2.94 | 4.9% | Communication |  |  |  | N/A as this appears to have been a comm issue, there are not corrective actions in terms of pressure | HP Distribution | Near Hit | No | No
Near Hit | 7004896 | FHE_PT0001 | Fresno | 2014-07-18 10:16 | 403.42 | 500 | -96.58 | -19.32% | Equipment - Other |  |  |  | Immediate actions followed that included the following: • GTCC contacted the I&R Supervisor when it received a HIHI alarm at Herndon Junction • GTCC contacted the M&C Mechanic when the MOP of 400 psig was breach at 400.83 psig; in addition, the I&R Supervisor was also contacted about the MOP breach and opening of V-3 • Revision was done to Clearance 80001866 instead of closing V-10 and V-3 to isolate pressure between L-134A and L-118A. The isolation point was changed to V-1. • GTCC also contacted the Pipeline Engineer regarding the MOP breach at Herndon Junction. And the local engineer will be conducting and investigate/research of MAOP. - In station MAOP has been determined to be 500 psig | Transmission | Near Hit | No | No
Near Hit | 7004934 | Gauge | Kern | 2014-07-18 17:00 | 311 | 335 | -24 | -7.164% | HF/WPE - Field O&M |  |  |  | CA: OP diagram needs to be updated to show MAOP from SCG at 335 psig. | Transmission | Near Hit | No | No
OP | 7005061 | ALM_PT1703 | Los Medanos District | 2014-07-20 14:37 | 400.5 | 400 | 0.5 | 0.125% | Failure - Equipment |  |  | OP event caused by a malfunction of the positioner transducer. | Replace transducer | Transmission | Small OP Event | No | No |  | ACE |  |  | GT.STAT.STOR.LOSMEDANOS | 3807802.pdf
Near Hit | 7005066 | FR_FRE_RB01_PT3 | Fresno | 2014-07-29 09:27 | 60.6293 | 60 | 0.6293 | 1.049% | HF/WPE - Eng Review |  |  |  | • need to be released 1. Short term – Ensure that the following procedure is use for checking pressure at this station a. Check running reg and adjust pressure using the standard short line method. b. Switch the running reg and the standby reg by lowering the running reg set point to the standby reg set point. Then raise the standby reg to the normal running set point. c. Check the new running reg and adjust pressure using the short line method. 2. Long term – Move the tap for SCADA to a location on the outlet pipe that is well downstream of the sense lines and outlet valves. | HP Distribution | Near Hit | No | No | [5 empty] | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\3807802.pdf
OP | 7005059 | EB_ALA_S020 | East Bay | 2014-07-30 04:22 | 15.14 | 15 | 0.14 | 0.9333% | Failure - Equipment |  |  | Pressure set point was not originally adjusted down for summer operations and thus was too close to MOP | •awaiting addiitonal information - potential close out Division will review the system, and see if pressure should be lowered on other stations to prevent future alarming. | HP Distribution | Small OP Event | No | No |  | ACE |  | H14 | GD.STAT.DIST.00329
Near Hit | 7005158 | ST_LOD_EX02_PT1 | Stockton | 2014-08-01 04:29 | 59.5611 | 60 | -0.4389 | -0.7315% | Equipment - Other |  |  |  | Supervisor indicated rebuilt the pilot | HP Distribution | Near Hit
OP | 7005140 | JDL_PT0002 | Hollister District | 2014-08-04 02:02 | 472.6 | 408 | 64.6 | 15.83% | Clearance Preparation | HU | P50.2 | Clearance writers did not take into account that the pressure would equalize across the regulation when they closed valve V-0.01 and caused an OP event. | • Immediate response • Integrity Management to conduct a condition assessment • Hydrotest piping to confirm it is sufficient for the MAOP (advised) : >>>>>>>Option 2 – Expand scope of PSRS 28501 Dolan Rd Station Rebuild project scheduled for 2015 to include strength testing of this section of L-301B. Current scope is limited to repair of valve extensions/gauge tap lines and atmospheric corrosion. The current job is scheduled for 2015 construction; I would say this expansion of the scope will make this a late 2015 project, possibly 2016. | Transmission | Large OP Event | No | No |  | ACE |  | H-14 | GT.STAT.MISC.DOLNRDPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\083812.pdf | H14
Near Hit | 7005190 | MMT_PT3030 | Milpitas District | 2014-08-05 06:33 | 296 | 300 | -4 | -1.333% | HF/WPE - Gas Control |  |  |  | Corrective Actions have been entered into CAP | Transmission | Near Hit | No | No
Near Hit | 7005258 | SSW_PT0004 | Sacramento | 2014-08-10 16:22 | 629.585 | 639 | -9.415 | -1.473% | HF/WPE - Manual Operations |  |  |  | Immediate corrective actions have been entered Mention in the next 5MM - caution when hand throttling valves | Transmission | Near Hit | Yes | No
Near Hit | 7005290 | M6A_PT0003 | Hollister District | 2014-08-11 11:08 | 615.539 | 630 | -14.461 | -2.295% | HF/WPE - Gas Control |  |  |  | After noticing the set point at PLS-6A was entered incorrectly, the operator immediately lowered the set point to 500 psig and the pressure started to reduced after the set point was corrected. At 11:15 AM, the Senior Transmission Coordinator and GT Manager were in discussion of the incident. Overall, the following the incident immediate actions were done in order to correct the inadvertently wrong set point. This event is a lesson learned for CC and operators. | Transmission | Near Hit | Yes | No
Near Hit | 7005263 | SF_SF_S027 | San Francisco | 2014-08-11 15:51 | 49.2 | 60 | -10.8 | -18% | HF/WPE - Eng Review |  |  |  | New ERX location to be established | HP Distribution | Near Hit | Yes | No
Near Hit | 7005527 | SF_SF_S026 | San Francisco | 2014-08-11 17:30 | 49.26 | 60 | -10.74 | -17.9% | HF/WPE - Eng Review |  |  |  | New ERX location to be established | HP Distribution | Near Hit | Yes | No
Near Hit | 7005396 | SO_PET_R495_PT3 | Sonoma | 2014-08-15 00:34 | 49.0337 | 50 | -0.9663 | -1.933% | SP Too Close to MOP/HiHi |  |  |  | Immediate actions followed during the HIHI alarm at Peteluma Dist that included the following: • GDCC acknowledge the HIHI alarm at Peteluma Dist D/S pressure (SO_PET_R495_PT3) • GDCC contacted the on call Tech regarding the HIHI alarm. GDCC was unable to reach the on call so their left a message regarding Peteluma HIHI. A second call was made a few minutes after the initial call • GDCC also contacted the I&R Supervisor after attempting to reach the on call Tech • At about 01:31 AM, a Tech was sent out to Peteluma in order to investigate the HIHI incident. | HP Distribution | Near Hit | Yes | No
OP | 7005431 7005698 | FAI_PT0002 | Stockton | 2014-08-16 08:50 | 116.424 | 90 | 26.424 | 29.36% | Maintenance Operations Quality | HU | P50.2 | Due to poor station design the distance between THYP-31 and THYP-32 was insufficient for the installed equipment to react quickly enough in the event of quick valve closures. | See CAP 7005698 for RCA analysis by the CAP group | Transmission | Large OP Event | No | No |  | ACE |  | H-14 | #N/A | 082229.pdf | H14
Near Hit | 7005525 | ST_TRA_RT32_PT3 | Stockton | 2014-08-16 12:47 | 26.0585 | 28 | -1.9415 | -6.934% | SP Too Close to MOP/HiHi |  |  |  | Please refer to CAP 7005431 – Acacia Station OP Event on Aug 16, 2014 for Corrective Actions. | HP Distribution | Near Hit | Yes | No
Near Hit | 7005470 | FAI_PT0002 | Stockton | 2014-08-20 09:31 | 71.3145 | 72 | -0.6855 | -0.9521% | HF/WPE - Field O&M |  |  |  | Please refer to CAP 7005431 – Acacia Station OP Event on Aug 16, 2014 for Corrective Actions. | Transmission | Near Hit | Yes | No
Near Hit | 7005524 | OMZ_PT0002 | Diablo | 2014-08-20 11:26 | 262.42 | 268 | -5.58 | -2.082% | HF/WPE - Field O&M |  |  |  | Improve training and clearance instructions to advise caution when setting regulation on active flowing system. Update OP diagram analyze system reguator and monitor set points | Transmission | Near Hit | Yes | No
Near Hit | 7005529 | SA_WDL_S028 | Sacramento | 2014-08-26 00:01 | 9.99 | 14 | -4.01 | -28.64% | SP Too Close to MOP/HiHi |  |  |  | Immediate actions following the incident are considered adequate for this event. No further corrective actions are required. | LP Distribution | Near Hit | No | No
Near Hit | 7005556 | SF_SF_S0004_PT1 | San Francisco | 2014-08-29 01:03 | 10.63 | 14 | -3.37 | -24.07% | SP Too Close to MOP/HiHi |  |  |  | Work to obtain approval for alarm limits to be increased at SCADA sites of higher elevation | LP Distribution | Near Hit | Yes | No
Near Hit | 7005720 | SA_ESP_S045_PT1 | Sacramento | 2014-08-29 02:25 | 53.01 | 55 | -1.99 | -3.618% | SP Too Close to MOP/HiHi |  |  |  | isolated incident, probably no corrective actions will come of this… await thrusday meeting | HP Distribution | Near Hit | Yes | No
Near Hit | 7005721 | KKT_PT0001 | Kettleman District | 2014-08-31 05:29 | 664 | 669 | -5 | -0.7474% | HF/WPE - Gas Control |  |  |  | Supervisor to address training in concerining this operating situation in the future with GSO | Transmission | Near Hit | No | Yes
Near Hit | 7005832 | SA_SAC_S026_PT1 | Sacramento | 2014-09-10 02:30 | 9.5 | 14 | -4.5 | -32.14% | SP Too Close to MOP/HiHi |  |  |  | N/A - isolated can be closed out after risk ranking no response from I&R supervisor | LP Distribution | Near Hit | No | No
Near Hit | 7006071 | Gauge | Hinkley District | 2014-09-10 20:25 | 73 | 720 | -647 | -89.86% | Equipment - Other |  |  |  | Update drawing with MAOP/MOP of L314 and downstream | Transmission | Near Hit | No | No
Near Hit | 7005830 | SA_WIN_S042 | Sacramento | 2014-09-10 23:29 | 56.03 | 60 | -3.97 | -6.617% | SP Too Close to MOP/HiHi |  |  |  | N/A - isolated can be closed out after risk ranking | HP Distribution | Near Hit | Yes | No
Near Hit | 7005831 | SA_SAC_S014_PT1 | Sacramento | 2014-09-11 02:29 | 46.99 | 50 | -3.01 | -6.02% | SP Too Close to MOP/HiHi |  |  |  | N/A - isolated can be closed out after risk ranking | HP Distribution | Near Hit | Yes | No
Near Hit | 7005922 | PN_SM_PA65_PT3 | Peninsula | 2014-09-13 00:22 | 32.23 | 34 | -1.77 | -5.206% | SP Too Close to MOP/HiHi |  |  |  | if no C/A close upon risk rank | HP Distribution | Near Hit | Yes | No
Near Hit | 7005924 | SA_SAC_S014_PT1 | Sacramento | 2014-09-13 01:22 | 47.13 | 50 | -2.87 | -5.74% | SP Too Close to MOP/HiHi |  |  |  | if no C/A close upon risk rank | HP Distribution | Near Hit | Yes | No
Near Hit | 7005923 | SA_SAC_S026_PT1 | Sacramento | 2014-09-13 01:46 | 9.44 | 12 | -2.56 | -21.33% | SP Too Close to MOP/HiHi |  |  |  | Address the low setting of the hihi alarm – should this hihi alarm be set to 10.5 in-w.c.? | LP Distribution | Near Hit | No | No
Near Hit | 7005868 | OES_PT0002 | East Bay | 2014-09-13 14:09 | 124.07 | 150 | -25.93 | -17.29% | Equipment - Other |  |  |  | Immediate Actions Followed the event that included: - GTCC contacted the local T&R Sup regarding the HIHI and MOP breach at Enrico - Local T&R Sup sent out a Tech to Enrico - Tech arrived at Enrico and didn’t find anything wrong at the station and "Everything looked normal". The Tech also gauged the line, and a 0.2 psig difference was observed Additional CA: L105N has an MOP/MAOP 150/198 psig respectively. It is currently being held down by a CROP to a MOP of 121 psig. This CROP/TROP was issued in 2011 due to unscheduled crane movement along 105A on Hollis St. Emeryville. Requesting Engineering to review and determine if the CROP on 105N is still validate at this point | Transmission | Near Hit | Yes | No
Near Hit | 7005925 | SA_SAC_S014_PT1 | Sacramento | 2014-09-14 01:43 | 47.14 | 50 | -2.86 | -5.72% | SP Too Close to MOP/HiHi |  |  |  | if no C/A close upon risk rank | HP Distribution | Near Hit | Yes | No
Near Hit | 7005926 | SA_SAC_RD25_PT3 | Sacramento | 2014-09-16 23:12 | 11.44 | 12 | -0.56 | -4.667% | SP Too Close to MOP/HiHi |  |  |  | • Immediate Response o Various calls made to get field technician out to the field Lowered set point pressure of regulation 1 in-w.c. reading 8.4 in-w.c. Call to confirm questions | LP Distribution | Near Hit | No | No
Near Hit | 7005927 | YO_HUS_S034 | Yosemite | 2014-09-18 02:43 | 48.13 | 52 | -3.87 | -7.442% | SP Too Close to MOP/HiHi |  |  |  | if no C/A close upon risk rank | HP Distribution | Near Hit | Yes | No
Near Hit | 7005932 | KE_RGC_R522_PT3 | Kern | 2014-09-19 07:12 | 52.01 | 55 | -2.99 | -5.436% | Equipment - Other |  |  |  | replace transducer | HP Distribution | Near Hit | Yes | No
Near Hit | 7006075 | SA_SAC_S013 | Sacramento | 2014-09-24 00:53 | 55.06 | 60 | -4.94 | -8.233% | SP Too Close to MOP/HiHi |  |  |  | Corrected HIS- isolated incident. | HP Distribution | Near Hit | Yes | No
Near Hit | 7006073 | SA_SAC_S012 | Sacramento | 2014-09-24 00:27 | 48.03 | 50 | -1.97 | -3.94% | SP Too Close to MOP/HiHi |  |  |  | immediate response - tech out to field, awaiting additional repsonse form Todd/Tim from email | HP Distribution | Near Hit | No | No
Near Hit | 7006074 | RHN_PT0005 | North Bay | 2014-09-24 03:20 | 620 | 675 | -55 | -8.148% | HF/WPE - Eng Review |  |  |  | Corrective action on 7004583 to rebuild station | Transmission | Near Hit | Yes | No
Near Hit | 7006072 | EB_CRK_EX25_PT1 | East Bay | 2014-09-24 12:04 | 58.8 | 500 | -441.2 | -88.24% | Design Issue - Other |  |  |  | see report | Transmission | Near Hit | No | No
Near Hit | 7006143 | M19_PT0106 | Central Coast | 2014-09-26 16:27 | 493.5 | 500 | -6.5 | -1.3% | Equipment - Other |  |  |  | Immediate actions followed the MOP breach that included: • GTCC contacted the Clearance Supervisor about the HIHI and MOP alarm at Hollister Station • The on-call CPUC liaison was also contacted regarding the MOP excursion at Hollister by GTCC. The on-call liaison determined that this event was not a CPUC reportable and no external notifications were required. • In addition, the on-call Pipeline Engineer was also contacted regarding the incident at Hollister Station. • The Clearance Supervisor reported back that the cause of the MOP excursion was due to a deteriorating o-ring on V-30 and repairs were being done to V-30. Clearance was completed and closed out on the same day (September 26, 2014) at 19:00 | Transmission | Near Hit | Yes | No
Near Hit | 7006220 | ALM_PT1004 | Diablo | 2014-09-26 21:23 | 473 | 590 | -117 | -19.83% | Design Issue - Other |  |  |  | typical operations | Transmission | Near Hit | Yes | Yes
Near Hit | 7006241 | NV_RBL_R125_PT3 | North Valley | 2014-10-04 21:50 | 55.4 | 60 | -4.6 | -7.667% | SP Too Close to MOP/HiHi |  |  |  | Immediate response - investigate station, and lower set points by 2 psig. It might be valuable to put MAOP separation lines (especially since its 3 stages), and annotate pressure breaks on the OP diagram | HP Distribution | Near Hit | Yes | No
Near Hit | 7006311 | PN_SM_PA72_PT3 | Peninsula | 2014-10-09 00:27 | 32.0025 | 32 | 0.0025 | 0.007812% | SP Too Close to MOP/HiHi |  |  |  | isolated incident Close after risk ranking | HP Distribution | Near Hit | No | No
Near Hit | 7006396 | FR_FRE_RJ36_PT3 | Fresno | 2014-10-12 00:40 | 57.0128 | 60 | -2.9872 | -4.979% | SP Too Close to MOP/HiHi |  |  |  | isolated incident Close after risk ranking | HP Distribution | Near Hit | Yes | No
Near Hit | 7006393 | KE_BKD_R405_PT3 | Kern | 2014-10-13 01:17 | 50.1011 | 51 | -0.8989 | -1.763% | SP Too Close to MOP/HiHi |  |  |  | isolated incident Close after risk ranking | HP Distribution | Near Hit | Yes | No
Near Hit | 7006488 | SA_SAC_RA44_PT3 | Sacramento | 2014-10-22 22:54 | 49.28 | 50 | -0.72 | -1.44% | Equipment - Sulfur |  |  |  | Immediate & GDCC to determine if associated regulator station is available | HP Distribution | Near Hit | Yes | No
Near Hit | 7006612 | PN_SM_PB09_PT3 | Central Coast | 2014-10-24 00:53 | 32.0152 | 34 | -1.9848 | -5.838% | SP Too Close to MOP/HiHi |  |  |  | Request for Distribution Planning to review the current PN_SM_PB09_PT09’s HIHI alarm limit to potential increase to 33 psig instead of 32 psig. | HP Distribution | Near Hit | Yes | No
Near Hit | 7006762 | RNW_PT0001 | North Bay | 2014-10-29 16:35 | 333.732 | 450 | -116.268 | -25.84% | Equipment - Other |  |  |  | isolated incident Close after risk ranking | Transmission | Near Hit | No | No
Near Hit | 7006990 | YO_FRB_S031_PT1 | Yosemite | 2014-11-07 00:03 | 40.3 | 45 | -4.7 | -10.44% | SP Too Close to MOP/HiHi |  |  |  | additional information requested | HP Distribution | Near Hit | Yes | No
Near Hit | 7006929 | YO_ATW_S027_PT1 | Yosemite | 2014-11-07 15:49 | 44.25 | 45 | -0.75 | -1.667% | Equipment - Sulfur |  |  |  | additional information requested | HP Distribution | Near Hit | Yes | No
OP | 7008497 | Gauge | North Valley | 2014-11-08 05:00 | 182 | 60 | 122 | 203.3% | Gas Contaminants - Liquids | EQ | P5 | Unknown fluids passing the filters and entering the regulator and monitor prevented proper station operation. | • T&R mechanic took steps to alleviate pressure excursion by bleeding pressure to normal NOP and returning station to service • Evaluating distribution main for damage • Leak survey to be completed • T&R to shut-in station, and replace rubber goods in the station • Replacement of main and service piping | HP Distribution | Large OP Event | No | No | No |  | No | LVCR | 0 | 0800189 | 40 | 48
Near Hit | 7007131 | DA_LGS_RD24_PT3 | San Jose | 2014-11-13 00:52 | 59.0207 | 60 | -0.9793 | -1.632% | SP Too Close to MOP/HiHi |  |  |  | call Morris white and Oscar Garcia emailed Jason Bright to consider set point reduction | HP Distribution | Near Hit | Yes | No
Near Hit | 7007130 | BRT_PT0131S | Diablo | 2014-11-18 19:24 | 414 | 525 | -111 | -21.14% | HF/WPE - Gas Control |  |  |  | o Event did not require additional mitigative actions | Transmission | Near Hit | No | No
Near Hit | 7007172 | KKT_PT0001 | Kettleman District | 2014-11-20 04:39 | 665 | 669 | -4 | -0.5979% | HF/WPE - Gas Control |  |  |  | • Immediate action was followed by GTCC to address the situation in order to prevent further over pressuring of the suction head piping. • For future compression operation at Kettleman, it’s suggested that the Main Line Valve (V-354.02B) is fully closed before compression is started in the station (A. Wenzel) • For long term – develop and provide a logical procedure of compressing (A. Wenzel) • Wenzel & Grandmont – 5MM review with GTCC procedure that spill valves will be used – reference 7005721 C/A, what are you doing to address this moving forward? | Transmission | Near Hit | No | No
Near Hit | 7007262 | BRT_PT0131 | Diablo | 2014-11-20 10:21 | 468 | 867 | -399 | -46.02% | HF/WPE - Manual Operations |  |  |  | Close upon risk rank CAP item 7007264 entered to address transmission gauging intervals | Transmission | Near Hit | No | No
Near Hit | 7007173 | ALM_PT1703 | Diablo | 2014-11-20 19:34 | 393 | 590 | -197 | -33.39% | Design Issue - Other |  |  |  | Back power question needs to be addressed | Transmission | Near Hit | No | Yes
Near Hit | 7007260 | SA_WDL_S044 | Sacramento | 2014-11-21 00:52 | 48 | 50 | -2 | -4% | SP Too Close to MOP/HiHi |  |  |  | isolated incident Close after risk ranking | HP Distribution | Near Hit | Yes | No
Near Hit | 7007346 | K15_PT0035 | Yosemite | 2014-11-21 04:32 | 844 | 890 | -46 | -5.169% | Equipment - Other |  |  |  | Techs were sent out to Panoche Station to investigate the swinging valves Per discussion with CAP Specialist, this could have been prevented if the valves were set to manual after the oscillation started (Lesson Learnd - mentioned to GTCC Sup). | Transmission | Near Hit | No | No
Near Hit | 7007226 | K4B_PT0004 | Kern | 2014-11-22 16:40 | 723 | 754 | -31 | -4.111% | HF/WPE - Manual Operations |  |  |  | PLS 4 relief valve incident has been assigned to Bruce Riggs as the CAP Notification Owner. A copy of the 48 hour report has been attached to the CAP Notification (CAP # 7007226) | Transmission | Near Hit | No | No
Near Hit | 7007261 | KE_RGC_R522_PT3 | Kern | 2014-11-24 01:23 | 52.02 | 55 | -2.98 | -5.418% | Equipment - Other |  |  |  | confirm transducer was replaced from previous CAP item 7005932 | HP Distribution | Near Hit | Yes | No
OP | 7016776 | Gauge | Sierra | 2014-11-24 13:30 | 122 | 60 | 62 | 103.3% | Clearance Preparation | HU | P50.2 | A dead-end system was created at an abandoned prune dryer when the connected bypass valve was not fully closed after a clearance. | Deactiveate service, and review decommissioning procedures | HP Distribution | Large OP Event | No | No |  | ACE |  | LVCR | 0
Near Hit | 7007333 | EB_ALA_EX14_PT1 | East Bay | 2014-11-30 00:36 | 10.6 | 12 | -1.4 | -11.67% | SP Too Close to MOP/HiHi |  |  |  | isolated incident Close after risk ranking | LP Distribution | Near Hit | No | No
Near Hit | 7007332 | MI_UNC_S019_PT1 | East Bay | 2014-11-30 02:47 | 50.2 | 58 | -7.8 | -13.45% | SP Too Close to MOP/HiHi |  |  |  | isolated incident Close after risk ranking | HP Distribution | Near Hit | Yes | No
Near Hit | 7007456 | EB_RCH_S019_PT1 | East Bay | 2014-12-01 04:00 | 4 | 5 | -1 | -20% | SP Too Close to MOP/HiHi |  |  |  | isolated incident Close after risk ranking | HP Distribution | Near Hit | No | No
Near Hit | 7007337 | SA_WDL_S044 | Sacramento | 2014-12-03 00:39 | 48.08 | 50 | -1.92 | -3.84% | Equipment - Sulfur |  |  |  | immediate response, sulfagon filter? | HP Distribution | Near Hit | Yes | No
Near Hit | 7007491 | EB_RCH_S019_PT1 | East Bay | 2014-12-04 00:35 | 4.03 | 5 | -0.97 | -19.4% | SP Too Close to MOP/HiHi |  |  |  | Close after risk ranking | HP Distribution | Near Hit | No | No
Near Hit | 7007431 | MI_UNC_S019_PT1 | East Bay | 2014-12-07 02:47 | 50.14 | 58 | -7.86 | -13.55% | SP Too Close to MOP/HiHi |  |  |  | not an isolated incident see previous 7007332 | HP Distribution | Near Hit | Yes | No
OP | 7007543 | SYC_PT0007 | Sierra | 2014-12-08 04:50 | 528 | 525 | 3 | 0.5714% | Gas Contaminants - Debris | EQ |  | Debris in the regs and monitors are the most probable cause for this OP event. | Existing corrective actions still outstanding in CAP # 7000101 and additional suggested CA's TBD | Transmission | Small OP Event | No | Yes |  | ACE |  |  | GT.STAT.MISC.YUBACITYUH
Near Hit | 7007625 | M19_PT0105 | Hollister District | 2014-12-10 08:00 | 391.1 | 396 | -4.9 | -1.237% | Design Issue - Other |  |  |  | Close upon risk rank | Transmission | Near Hit | No | No
Near Hit | 7007811 | ALM_PT1004 | Diablo | 2014-12-16 13:06 | 393 | 590 | -197 | -33.39% | Design Issue - Other |  |  |  | Replace UPS - There is currently a project initiated for the replacement of the UPS (see PSRS 36970). It is also mentioned in CAP # 7007173 | Transmission | Near Hit | No | Yes
Near Hit | 7007813 | EB_BER_EX05_PT1 | East Bay | 2014-12-17 02:13 | 97.2 | 60 | 37.2 | 62% | Communication |  |  |  | - There is currently a project initiated for the replacement of the UPS (see PSRS 36970) – and CAP 7007173 | HP Distribution | Near Hit | No | No
Near Hit | 7009733 | SF_SF_S037 | San Francisco | 2014-12-18 12:29 | 10.46 | 12 | -1.54 | -12.83% | SP Too Close to MOP/HiHi |  |  |  | Adjustment of local reg station | LP Distribution | Near Hit | No | No
Near Hit | 7007943 | YO_MER_S016 | Yosemite | 2014-12-18 13:13 | 47.7 | 50 | -2.3 | -4.6% | SP Too Close to MOP/HiHi |  |  |  | ERX alarm limited adjusted | HP Distribution | Near Hit | No | No
Near Hit | 7009736 | SF_SF_S037 | San Francisco | 2014-12-19 02:41 | 10.59 | 12 | -1.41 | -11.75% | SP Too Close to MOP/HiHi |  |  |  | Adjustment of local reg station | LP Distribution | Near Hit | No | No
Near Hit | 7007881 | SJ_SJ_RG83_PT3 | San Jose | 2014-12-21 02:43 | 10.55 | 12 | -1.45 | -12.08% | Equipment - Other |  |  |  | Regulator to be replaced | LP Distribution | Near Hit | No | No
Near Hit | 7007988 | ATN_PT0002 | Burney District | 2014-12-22 03:12 | 899 | 905 | -6 | -0.663% | Design Issue - Other |  |  |  | awaiting CAP meeting | Transmission | Near Hit | No | Yes
OP | 7007915 | KAM_PT0001 | Fresno | 2014-12-25 03:47 | 503.1 | 498 | 5.1 | 1.024% | Gas Contaminants - Debris | EQ |  | The regulation U/S of the station wasn't locking up properly due to grease/residue discovered in the reg. | Immediate actions followed: • GTCC received a MOP/HIHI alarm at Amador Station and contacted on call supervisor • On call supervisor sent out Techs to Coalinga Tap (U/S of Amador Station) • Regulation at Coalinga Tap wasn’t locking up properly and service was done on regulation (the reg’s internal components was replaced and rechecked) • The reg set points were readjusted to the 5/20 rule. The monitors were left at 493 psig, the reg for the primary run was set to 478 psig, and the secondary run at 468 psig. | Transmission | Small OP Event | Yes | No |  | ACE |  |  | GT.STAT.MISC.AMADORSTAT | 085551.pdf
Near Hit | 7008033 | NV_CHC_RL14_PT3 | North Valley | 2014-12-29 06:46 | 8.9 | 12 | -3.1 | -25.83% | Equipment - Other |  |  |  | Immediate Actions followed: • GDCC contacted on-call personnel, GDCC planner, Sup Local Gas Engineer, and I&R Sup • I&R discovered that the slam shut was triggered and the slam shut device was reset to 14” W.C. | LP Distribution | Near Hit | No | No | [5 empty] | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\085551.pdf
Near Hit | 7008032 | Relief Valve | Stockton | 2014-12-29 12:23 | 60 | 500 | -440 | -88% | Equipment - Other |  |  |  | Immediate Actions followed: • GDCC identified incident was GTCC responsibility and was handled over to the Transmission Operator. Prior to GDCC handling over the incident to GTCC, GRS and FD were notified and on site. • GTCC contacted and sent out a I&R Tech to the location • I&R Tech discovered that a relief valve was triggered and it was close after discovery. The regs were inspected, and sulfur build up was found on the regs. | Transmission | Near Hit | Yes | Yes
Near Hit | 7008031 | OPP_PT0001 | Diablo | 2014-12-30 06:40 | 336.2 | 338 | -1.8 | -0.5325% | HF/WPE - Gas Control |  |  |  | • GTCC contacted the local supervisor about the HIHI breach at Pittsburg Power Station and requested for a crew to be sent out to validate reading and inspect the regs U/S of Pittsburg Power Station. No signs of irregularities were found. • Per Gas Log, it was suggested to raise set points in small increments (less than 5 psig) Lesson Learned: When remote set points are changed during operation, it is suggested to raise set points in small increment to allow adequate time for reg to fully control. | Transmission | Near Hit | No | No
Near Hit | 7008073 | AIP_PT0002B | North Valley | 2014-12-31 13:10 | 753.4 | 911 | -157.6 | -17.3% | HF/WPE - Field O&M |  |  |  | Immediate Actions followed: • GTCC contacted the field regarding the MOP/HIHI alarm limit at Indian Spring • Field closed the valve to stop flow through V-48.65 • GTCC contacted Planning about the MOP/HIHI at Indian Spring. The MOP alarm was due to a CROP/TROP and this instance doesn’t apply. • GTCC contacted the Pipeline Engineer and was advised that this was a near miss/ near hit | Transmission | Near Hit | No | No
OP | 7008090 | FR_FRE_EX11 | Fresno | 2015-01-03 20:32 | 70.6 | 60 | 10.6 | 17.67% | Failure - Equipment | EQ | P5 | Technicians discovered a damaged equipment (pilot plug), plus found weld slag in regulator body and ice in pilot. | • C/A inventory control on sulfur-gon filters in storage; given direction to supplier quality, working with supplier to address packaging - M. Rossi o Recommended shelf life? o Moisture sensing materials? • C/A identify stations with similar work where there may be weld slag in the pipeline between regulator and monitor - Construction Superintendent/Management | HP Distribution | Large OP Event | Yes | No |  | ACE |  | H-14 | GD.STAT.DIST.01424 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Fre\Tif\Gas\RegStation\0806679.PDF | H14
Near Hit | 7008153 | Relief Valve | Hinkley District | 2015-01-06 09:45 | 70 | 720 | -650 | -90.28% | Facility Design |  |  |  | • Relief valve (OPP) set point should be reviewed by D. Yorke’s group | Transmission | Near Hit | Yes | No
Near Hit | 7008165 | AIP_PT0002B | North Valley | 2015-01-06 23:10 | 744.1 | 911 | -166.9 | -18.32% | Failure - Equipment |  |  |  | Replace fault parts in V-12 (regulator valve that failed) | Transmission | Near Hit | No | No
OP | 7008166 | KGF_PT0002 | Kern | 2015-01-07 07:51 | 486.2 | 478 | 8.2 | 1.715% | Clearance Execution |  |  | Clearance lacked detail, steps not followed, reg was failed open to place monitor in control causing overshoot. | • Immediate response o Field took immediate action to reduce pressure under MAOP o DOT protocol o Event did not require additional mitigative actions | Transmission | Small OP Event | Yes | No |  | ACE |  |  | GT.STAT.MISC.GOSFORDRDM | 083802.pdf
Near Hit | 7008167 | K4B_PT0004 | Kern | 2015-01-07 17:02 | 720 | 754 | -34 | -4.509% | Failure - Equipment |  |  |  | Further Corrective Actions: (Reference CAP # 7008296) • Engineering to address Relief Valve Set points (Jonathan Lo) • A new pilot has been ordered for replacement (Jonathan Lo) • Update on Citect Screen for valve J (Jordan Blanco) | Transmission | Near Hit | No | No | [5 empty] | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\083802.pdf
Near Hit | 7009014 | SA_DVS_S021 | Sacramento | 2015-01-08 23:10 | 55.19 | 60 | -4.81 | -8.017% | SP Too Close to MOP/HiHi |  |  |  | Request to increase hihi alarm setting | HP Distribution | Near Hit | Yes | No
Near Hit | 7009015 | EB_RCH_S014 | East Bay | 2015-01-09 09:15 | 4.39 | 5 | -0.61 | -12.2% | SP Too Close to MOP/HiHi |  |  |  | No further corrective actions | HP Distribution | Near Hit | No | No
Near Hit | 7009014 | SA_DVS_S021 | Sacramento | 2015-01-09 22:35 | 55.13 | 60 | -4.87 | -8.117% | SP Too Close to MOP/HiHi |  |  |  | Request to increase hihi alarm setting | HP Distribution | Near Hit | Yes | No
Near Hit | 7009149 | ST_TRA_RT72_PT3 | Stockton | 2015-01-10 00:45 | 57.05 | 60 | -2.95 | -4.917% | SP Too Close to MOP/HiHi |  |  |  | Tech responded to site (on-site 07:35 AM), and lowered pressure slightly . | HP Distribution | Near Hit | Yes | No
Near Hit | 7008493 | ST_STK_RR13_PT3 | Stockton | 2015-01-10 12:33 | 10.552 | 12 | -1.448 | -12.07% | SP Too Close to MOP/HiHi |  |  |  | Stakeholders are searching for possible short/long term solutions to the HIHI alarm (See CAP # 7008542 for updates) | LP Distribution | Near Hit | No | No
Near Hit | 7009014 | SA_DVS_S021. | Sacramento | 2015-01-12 11:39 | 55.19 | 60 | -4.81 | -8.017% | SP Too Close to MOP/HiHi |  |  |  | Request to increase hihi alarm setting | HP Distribution | Near Hit | Yes | No
OP | 7008412 | Gauge | East Bay | 2015-01-12 11:00 | 609.4 | 12 | 597.4 | 4978% | Gas Contaminants - Debris | EQ | P95.8 | Using temporary bypass reg w/no filter or OPP, weld slag failed regulator. | • Check hospital for leaks • Ensure appliance regs get replaced • Develop by-pass standard | LP Distribution | Large OP Event | No | No | No | ACE |  | H-14 | 0 | 0808679.PDF | GQ
Near Hit | 7009162 | SA_EMC_S022 | Sacramento | 2015-01-12 13:32 | 56 | 60 | -4 | -6.667% | SP Too Close to MOP/HiHi |  |  |  | Comments from SRDC Daily Report: Called on-call, they are aware that this is coming in due to need for an alarm setpoint chance. Will notify on-call if pressure exceeds 57 PSIG | HP Distribution | Near Hit | Yes | No
Near Hit | 7008494 | AIP_PT0002B | North Valley | 2015-01-14 09:32 | 740.4 | 911 | -170.6 | -18.73% | Failure - Equipment |  |  |  |  | Transmission | Near Hit | No | No
Near Hit | 7008493 | ST_STK_RR13_PT3 | Stockton | 2015-01-17 01:07 | 10.51 | 12 | -1.49 | -12.42% | SP Too Close to MOP/HiHi |  |  |  | Stakeholders are searching for possible short/long term solutions to the HIHI alarm (See CAP # 7008542 for updates) | LP Distribution | Near Hit | No | No
Near Hit | 7014895 | ST_STK_S008 | Stockton | 2015-01-19 01:18 | 10.57 | 12 | -1.43 | -11.92% | SP Too Close to MOP/HiHi |  |  |  |  | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00208
Near Hit | 7014944 | EB_OAK_RA64_PT3 | East Bay | 2015-01-20 10:48 | 8.4 | 12 | -3.6 | -30% | Failure - Contaminants |  |  |  |  | LP Distribution | Near Hit | No | No
Near Hit | 7009016 | RMO_PT0002 | North Bay | 2015-01-22 09:32 | 197.2 | 200 | -2.8 | -1.4% | Maintenance Operations Quality |  |  |  |  | Transmission | Near Hit | Yes | No |  |  |  | H-14 | GT.STAT.MISC.MONROEREGS
Near Hit | 7008493 | ST_STK_RR13_PT3 | Stockton | 2015-01-27 00:43 | 10.66 | 12 | -1.34 | -11.17% | SP Too Close to MOP/HiHi |  |  |  | Stakeholders are searching for possible short/long term solutions to the HIHI alarm (See CAP # 7008542 for updates) | LP Distribution | Near Hit | No | No
Near Hit | 7008807 | K4B_PT0004 | Kern | 2015-01-28 03:48 | 720 | 754 | -34 | -4.509% | Failure - Equipment |  |  |  | Further Corrective Actions: (Reference CAP # 7008296) • Engineering to address Relief Valve Set points (Jonathan Lo) • A new pilot has been ordered for replacement (Jonathan Lo) • Update on Citect Screen for valve J (Jordan Blanco) | Transmission | Near Hit | No | No
Near Hit | 7009013 | KKT_PT0004 | Kern | 2015-01-31 09:32 | 812 | 840 | -28 | -4.509% | Failure - Equipment |  |  |  |  | Transmission | Near Hit | No | Yes |  |  |  |  | GT.STAT.COMP.KETTLEMAN_
Near Hit | 7009011 | KE_TRO_S005 | Kern | 2015-02-03 16:30 | 63.91 | 55 | 8.91 | 16.2% | Failure - Equipment |  |  |  | Immediate Response: • GDCC contacted the I&R Supervisor and I&R crew was sent out to the District Reg Station and ERX • I&R crew rebuilt the regulators (replaced internal components) and installed new pilots. The pressure was found at 45.8 psig and as left at 45 psig. o Old pilots were removed intact and will be sent to the Concord Test Lab for further analysis – M. Pace • ~1150 services are being leak surveyed – 1 grade one leak was found on the evening of February 4th (this may not be related to the overpressure event). Leak survey will continue its surveying into February 5th 2015. | HP Distribution | Near Hit | No | No
Near Hit | 7009012 | SJ_SJS_RG05_PT3 | San Jose | 2015-02-04 00:50 | 10.56 | 12 | -1.44 | -4.509% | Failure - Equipment |  |  |  | None | LP Distribution | Near Hit | No | No
Near Hit | 7009006 | SMS_PT0005 | Sacramento | 2015-02-06 14:00 | 73 | 95.4 | -22.4 | -23.48% | Facility Design |  |  | No documentation of houseline MAOP or STPR for meter set. Likely Near Hit, MAOP houseline is 95 psig per ASME B31.3 | Immediate response: • Field took immediate action to reduce pressure under MAOP Long Term: • Permanent valve tag attached to Single feed large customers that indicates houseline MAOP (similar to valve tags) • Evaluate customer accounts with delivery pressure and houseline MAOP | Transmission | Near Hit | Yes | No |  |  |  |  | GT.STAT.LVCR.0000000523
Near Hit | 7009377 | SA_SAC_S013 | Sacramento | 2015-02-07 00:26 | 55.03 | 60 | -4.97 | -8.283% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014945 | SJ_SJS_RF19_PT3 | San Jose | 2015-02-10 15:17 | 59.0055 | 60 | -0.9945 | -1.658% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7009160 | EB_OAK_RA64_PT3 | East Bay | 2015-02-11 15:24 | 11.01 | 12 | -0.99 | -8.25% | SP Too Close to MOP/HiHi |  |  |  |  | LP Distribution | Near Hit | No | No
Near Hit | 7009163 | SJ_SJS_RF19_PT3 | San Jose | 2015-02-11 15:24 | 59.07 | 60 | -0.93 | -1.55% | Maintenance Operations Quality |  |  |  | Immediate actions were taken – the transducer was recalibrated by I&R Tech | HP Distribution | Near Hit | Yes | No
OP | 7009056 | MMT_PT0083 | Milpitas District | 2015-02-11 17:20 | 306 | 300 | 6 | 2% | Clearance Preparation |  |  | PLC uploading error, Regulating Valves not in manual control. | Pressure subsided below MOP Request TIMP Engineering to assist with the Engineering Critical Analysis (ECA) to verify any threat activations/mitigations required Pressure reduction and leak survey is not required per PLE | Transmission | Small OP Event | No | No |  | RCE |  |  | GT.STAT.MISC.MLPTSTPLM_ | 383510.pdf
Near Hit | 7009377 | SA_SAC_S013 | Sacramento | 2015-02-14 00:27 | 54.93 | 60 | -5.07 | -8.45% | Failure - Contaminants |  |  |  | • Inspection was conducted and rubber goods & pilot cartridge were replaced • The reg was also lowered by 0.5 psig | HP Distribution | Near Hit | Yes | No
Near Hit | 7009301 | SJ_SJS_RG05 | San Jose | 2015-02-14 01:31 | 10.55 | 12 | -1.45 | -12.08% | SP Too Close to MOP/HIHI |  |  |  | To be further monitored | LP Distribution | Near Hit | No | No
Near Hit | 7009300 | EB_OAK_RA63_PT3 | East Bay | 2015-02-14 01:48 | 10.54 | 12 | -1.46 | -12.17% | SP Too Close to MOP/HiHi |  |  |  | I&R Tech was sent out to calibrate the transducer and adjust the regulation | LP Distribution | Near Hit | No | No
Near Hit | 7009304 | SJ_SJS_RF83 | San Jose | 2015-02-14 02:16 | 10.59 | 12 | -1.41 | -11.75% | SP Too Close to MOP/HIHI |  |  |  | Further monitor per on call supervisor request | LP Distribution | Near Hit | No | No
Near Hit | 7009495 | EB_BER_RE09 | East Bay | 2015-02-14 02:17 | 14.03 | 15 | -0.97 | -6.467% | SP Too Close to MOP/HIHI |  |  |  | Tech was sent out to Thousand Oaks & Carmel – recalibration was conducted and corrected the 0.2 psig pressure difference | HP Distribution | Near Hit | No | No
Near Hit | 7009493 | KE_TRO_S005 | Kern | 2015-02-18 19:15 | 45 | 55 | -10 | -18.18% | Failure - Equipment |  |  |  | Technicians will be replacing the ERX at Hemlock, and send it to CTL for further testing | HP Distribution | Near Hit | No | No
Near Hit | 7009494 | EB_OAK_EX21_PT1 | East Bay | 2015-02-23 10:10 | 10.8 | 12 | -1.2 | -10% | Maintenance Operations Quality |  |  |  | Immediate Response – field check the reg for lock up and reg returned to normal operation | LP Distribution | Near Hit | No | No
OP | 7009775 | JHK_PT0003 | Central Coast | 2015-02-24 08:51 | 329.2 | 313 | 16.2 | 5.176% | Failure - Equipment | EQ |  | Antiquated equipment, undetermined equipment problem. | • Upon technician arrival • Full ‘in-the-case’ inspection was done • Regulator/monitor set points were reduced • Air supply was checked and found within acceptable range • Slight oil in upstream strainer – not enough to cause event • Moisture was not found in air supply • RTU transducer set point was validated • Replacing Bristol Controller with Becker SB CH pilots | Transmission | Small OP Event | No | No |  | ACE |  | H-19 | GT.STAT.MISC.HARKINSROD | 082856.pdf
Near Hit | 7009732 | AAN_PT298A | Diablo | 2015-02-24 15:51 | 585.9 | 720 | -134.1 | -18.63% | Failure - Equipment |  |  |  | Immediate action followed - Set point adjusted to 575 psig | Transmission | Near Hit | No | No | No | No | No |  | GT.STAT.MISC.ANTGSTPLS_
Near Hit | 7009513 | AAN_PT298A | Diablo | 2015-02-25 09:50 | 592.9 | 720 | -127.1 | -17.65% | Clearance Execution |  |  |  | Caution when closing MLV-298.87 | Transmission | Near Hit | No | No | No | No | No |  | GT.STAT.MISC.ANTGSTPLS_
Near Hit | 7009540 | CC_SAL_RS38_PT3 | Central Coast | 2015-02-27 00:28 | 59.8 | 60 | -0.2 | -0.3333% | Maintenance Operations Quality |  |  |  | Immediate action followed – reduced the pressure after HIHI alarm and maintenance work was completed | HP Distribution | Near Hit | No | No
Near Hit | 7009586 | K15_PT0035 | Yosemite | 2015-02-28 04:09 | 839 | 890 | -51 | -5.73% | Failure - Equipment |  |  |  | Immediate action followed: • GTCC notified station engineer • Regulation stabilized after MOP of 838 psig was breached at ~805 psig | Transmission | Near Hit | No | No
Near Hit | 7014946 | CC_MON_RM17_PT3 | Central Coast | 2015-02-28 21:42 | 50.8 | 51 | -0.2 | -0.3922% | Failure - Equipment |  |  |  |  | HP Distribution | Near Hit | No | No
Near Hit | 7009770 | CC_MON_RM17_PT3 | Central Coast | 2015-03-01 06:59 | 50.8 | 51 | -0.2 | -0.3922% | Emergency Response |  |  |  | GDCC notified the I&R Supervisor regarding the HIHI alarm, and Supervisor informed his crew to stay below the MOP limit during the response to the Monterey dig in – CNG injection was commenced | HP Distribution | Near Hit | No | No
Near Hit | 7014947 | CC_SCR_RJ03_PT3 | Central Coast | 2015-03-05 12:21 | 47 | 50 | -3 | -6% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014948 | DI_ORI_RW28_PT3 | Diablo | 2015-03-06 11:22 | 59.14 | 60 | -0.86 | -1.433% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014949 | SA_WDL_S043 | Sacramento | 2015-03-07 12:31 | 48.01 | 50 | -1.99 | -3.98% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014960 | ST_STK_RR33_PT3 | Stockton | 2015-03-08 00:26 | 10.67 | 12 | -1.33 | -11.08% | SP Too Close to MOP/HIHI |  |  |  |  | LP Distribution | Near Hit | No | No
Near Hit | 7014961 | EB_OAK_RA59_PT3 | East Bay | 2015-03-08 01:21 | 10.5 | 12 | -1.5 | -12.5% | SP Too Close to MOP/HIHI |  |  |  |  | LP Distribution | Near Hit | No | No
Near Hit | 7014962 | SJ_SJS_RG05_PT3 | San Jose | 2015-03-08 01:49 | 10.58 | 12 | -1.42 | -11.83% | SP Too Close to MOP/HIHI |  |  |  |  | LP Distribution | Near Hit | No | No
Near Hit | 7014963 | SJ_SJS_RF83_PT3 | San Jose | 2015-03-08 01:54 | 10.55 | 12 | -1.45 | -12.08% | SP Too Close to MOP/HIHI |  |  |  |  | LP Distribution | Near Hit | No | No
Near Hit | 7014964 | YO_NEW_S025 | Yosemite | 2015-03-08 03:16 | 45.42 | 50 | -4.58 | -9.16% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014972 | SA_WIN_S042_PT1 | Sacramento | 2015-03-09 01:53 | 55.9 | 60 | -4.1 | -6.833% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014965 | YO_NEW_S025 | Yosemite | 2015-03-10 22:47 | 45.97 | 50 | -4.03 | -8.06% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014973 | EB_ALA_RC07_PT3 | East Bay | 2015-03-13 02:32 | 10.31 | 12 | -1.69 | -14.08% | SP Too Close to MOP/HIHI |  |  |  | Corrective actions taken were to immediately notify the filed and request tech sent out to investigate issue. | LP Distribution | Near Hit | No | No
Near Hit | 7014967 | EB_BER_RE09 | East Bay | 2015-03-14 01:05 | 14.14 | 15 | -0.86 | -5.733% | SP Too Close to MOP/HIHI |  |  |  | Epage was sent out - this was first thought to be low pressure - but discovery uncovered it was SHP | HP Distribution | Near Hit | No | No
Near Hit | 7014975 | SJ_GIL_RH83_PT3 | San Jose | 2015-03-15 00:01 | 54.13 | 55 | -0.87 | -1.582% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | No | No
Near Hit | 7014976 | PN_SM_PA65_PT3 | Peninsula | 2015-03-15 01:25 | 33.01 | 34 | -0.99 | -2.912% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014977 | DA_SUN_RC28_PT1 | DeAnza | 2015-03-15 01:44 | 59.04 | 60 | -0.96 | -1.6% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014978 | ST_TRA_RT72_PT3 | Stockton | 2015-03-15 02:10 | 57.01 | 60 | -2.99 | -4.983% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014974 | EB_OAK_EX23_PT3 | East Bay | 2015-03-15 02:38 | 10.6 | 12 | -1.4 | -11.67% | SP Too Close to MOP/HIHI |  |  |  |  | LP Distribution | Near Hit | No | No
Near Hit | 7014979 | YO_RVB_S038_PT1 | Yosemite | 2015-03-16 01:53 | 55.58 | 60 | -4.42 | -7.367% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7014980 | EB_OAK_EX23_PT1 | East Bay | 2015-03-17 00:53 | 10.6 | 12 | -1.4 | -11.67% | SP Too Close to MOP/HIHI |  |  |  | On call was notified and he will be sending a tech out to inspect today as dayshift will follow up to make sure this is completed. | LP Distribution | Near Hit | No | No
Near Hit | 7010085 | M6A_ZS000J M6A_PT0001 | Central Coast | 2015-03-17 06:22 | 520 | 631 | -111 | -17.59% | Failure - Equipment |  |  |  | Immediate Action were taken: • Control Center contacted on-call supervisor and Tech was sent out to PLS-6 • Tech reported that power was still down at the station and the blow off cap was still intact. In addition, the OIT (similar reading to SCADA) was normal at 520 psig. • Tech recharged the backup battery until power was restored to the station • Tech remained at the station until power was restored to normal | Transmission | Near Hit | No | No
Near Hit | 7014981 | HU_EUR_RP02_PT3 | Humboldt | 2015-03-19 23:46 | 57 | 60 | -3 | -5% | SP Too Close to MOP/HIHI |  |  |  | ADJUSTED REG DOWN 0.5 PSIG. THERE IS ALSO A LARGE CUSTOMER ON THAT SYSTEM THAT WENT OFFLINE CAUSING A PRESSURE SPIKE. | HP Distribution | Near Hit | Yes | No
Near Hit | 7014968 | EB_BER_RE09 | East Bay | 2015-03-20 00:55 | 14 | 15 | -1 | -6.667% | SP Too Close to MOP/HIHI |  |  |  | REBUILT PILOT AND REG. ADJUSTED REG DOWN .5 PSIG. | HP Distribution | Near Hit | No | No
Near Hit | 7014969 | EB_BER_RE09 | East Bay | 2015-03-21 01:26 | 14 | 15 | -1 | -6.667% | SP Too Close to MOP/HIHI |  |  |  | REBUILT PILOT AND REG. ADJUSTED REG DOWN .5 PSIG. | HP Distribution | Near Hit | No | No
OP | 7010357 | DI_PIT_S028_PT1 | Diablo | 2015-03-24 10:29 | 24.1 | 17 | 7.1 | 41.76% | Maintenance Operations Quality | HU | P50.2 | Technicians performed maintenance by opening an incorrect valve, and did not fully return it to the closed postion. | Immediate Action Followed: - Techs were sent out to Pittsburg and confirm lock up at Pittsburg Town Station. Other associated stations and MAOP valve in Pittsburg are were checked by the Techs. -MAOP valve was found open and immediately closed by the Techs upon discovery - Leak survey was coordinated and scheduled Future CAs: - Removal of MAOP valve or further secure MAOP valve - Ernest Muse - Tailboard to all I&R - Jody Garcia RCE investigation requested 7010600 MAOP Separation Valves 7004171 | HP Distribution | Large OP Event | No | No |  | RCE |  | H-14 | 0 |  | H14
Near Hit | 7014982 | SJ_SJS_RF27_PT3 | San Jose | 2015-03-24 17:08 | 10.7 | 12 | -1.3 | -10.83% | SP Too Close to MOP/HIHI |  |  |  | working with engineer to change NOP. Tech in the field stated that calibrated gauges read ~1 "wc lower than SCADA. Needs to be calibrated, will address Wednesday | LP Distribution | Near Hit | No | No
Near Hit | 7014970 | EB_BER_RE09 | East Bay | 2015-03-27 02:12 | 14 | 15 | -1 | -6.667% | Failure - Contaminants |  |  |  | Pilot entirely replaced by crew | HP Distribution | Near Hit | No | No
OP | 7010548 | FFN_PT0009 | Fresno | 2015-03-27 20:05 | 418.3 | 400 | 18.3 | 4.575% | Clearance Execution |  |  | Performing work with verbal permission but no clearance, work steps caused loss and then surge of gas u/s reg, reg unable to handle. | More closely monitor Mooney performance when supply pressures decrease | Transmission | Small OP Event | No | No |  | ACE |  | H-14 | GT.STAT.MISC.FRESNOLOAD | 3808517.pdf
Near Hit | 7014983 | YO_LVT_S035 | Yosemite | 2015-03-30 23:41 | 38.2 | 42 | -3.8 | -9.048% | SP Too Close to MOP/HIHI |  |  |  | Called the field | HP Distribution | Near Hit | No | No
Near Hit | 7014966 | YO_NEW_S025 | Yosemite | 2015-04-01 01:47 | 45.4 | 50 | -4.6 | -9.2% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | No | No
Near Hit | 7014984 | SI_MVL_EX02 | Sierra | 2015-04-01 14:18 | 10.63 | 12 | -1.37 | -11.42% | SP Too Close to MOP/HIHI |  |  |  | Immediate Notification | LP Distribution | Near Hit | No | No
Near Hit | 7014985 | SJ_SJS_RF27_PT3 | San Jose | 2015-04-02 16:07 | 9.1 | 12 | -2.9 | -24.17% | SP Too Close to MOP/HIHI |  |  |  | according to the log, actial pressrue was 9.1 in-w.c. - (SCADA reading measure pressure too high according to gauge; recalibrate | LP Distribution | Near Hit | No | No
Near Hit | 7014986 | SA_SAC_S026 | Sacramento | 2015-04-04 00:12 | 9.56 | 12 | -2.44 | -20.33% | SP Too Close to MOP/HiHi |  |  |  | Continued to monitor pressure trends | LP Distribution | Near Hit | No | No
Near Hit | 7014987 | SA_SAC_S026 | Sacramento | 2015-04-06 13:03 | 9.5 | 12 | -2.5 | -20.83% | SP Too Close to MOP/HiHi |  |  |  | M&C Mech Robert Murphy reporting on to address HighHigh alarm for erx SA_SAC_S026 (5073 10th ave., Sac.) states feeding station DR-C02 is running fine and should not be adjusted. Local Planning advised him High High set point is low based on new standards. High High set at 9.5 inwc andbased on gdcc guidelines should be 10.5 high-high and 10.0 high | LP Distribution | Near Hit | No | No
Near Hit | 7015000 | ASL_PT0002 | North Valley | 2015-04-07 21:21 | 770.6 | 911 | -140.4 | -15.41% | SP Too Close to MOP/HiHi |  |  |  | Immediate actions – GTCC lowered discharge pressure at Burney Compressor Station in order to alleviate pressure at Shingle Town Station On April 10th 2015, alarm limits D/S of L-400 at Shingle Town Station was restored to normal with a MOP of 865 psig. | Transmission | Near Hit | No | No
Near Hit | 7011537 | MMT_PT3838A | San Jose | 2015-04-08 08:20 | 294 | 300 | -6 | -2% | Failure - Equipment |  |  |  | Evaluate if replacement of pressure transducer is needed – Matt McLaughlin | Transmission | Near Hit | No | No
Near Hit | 7015001 | K15_PT0032 | Yosemite | 2015-04-09 21:25 | 838 | 1040 | -202 | -19.42% | Failure - Equipment |  |  |  | Immediate actions followed: • Set point was lowered to 800 psig on V-32 • I&R Supervisor was notified by GTCC • Techs were sent out to check V-32/V-32R. No evidence of issues was found. | Transmission | Near Hit | No | No
Near Hit | 7014989 | SIL_PT0003 | Sacramento | 2015-04-10 11:13 | 466.2 | 720 | -253.8 | -35.25% | Clearance Execution |  |  |  | Immediate actions following - GTCC contacted the field regarding the spike in pressure of 466.2 psig, and PLE determined that Isleton Town station piping was rated for 720 psig. | Transmission | Near Hit | No | No
Near Hit | 7014988 | NB_SRF_EX06_PT1 | North Bay | 2015-04-12 03:30 | 55 | 60 | -5 | -8.333% | Failure - Equipment |  |  |  | Confirmed - and paper chart did not show a breach | HP Distribution | Near Hit | Yes | No
OP | 7011503 | SA_SAC_RA44 | Sacramento | 2015-04-23 10:31 | 51.7 | 50 | 1.7 | 3.4% | Maintenance Operations Quality | HU |  | Suspected HPE in performing "A" inspection, but could not be confirmed. | Immediate actions followed: - GDCC contacted the local Supervisor and field personnel regarding the MOP - Tech inspected the SCADA unit and found no issues with the unit. In addition, the field and SCADA reading were confirmed similar. Tasks/Corrective Actions: - Review and confirm SA_SAC_RA44_PT3 location and if its correct in SCADA | HP Distribution | Small OP Event | No | No |  | ACE |  | H-14 | GD.STAT.DIST.01007 | file://fairfield07/gis/giswebMiscFiles/GasStations/MET/0804238.PDF
Near Hit | 7014971 | EB_BER_RE09 | East Bay | 2015-05-01 01:00 | 14 | 15 | -1 | -6.667% | SP Too Close to MOP/HiHi |  |  |  | Continued to monitor pressure trends | HP Distribution | Near Hit | No | No
Near Hit | 7015122 | PN_BUR_S024 | Peninsula | 2015-05-01 01:26 | 33 | 34 | -1 | -2.941% | SP Too Close to MOP/HiHi |  |  |  | Tech would be sent out in the morning, per on call and GDCC decision | HP Distribution | Near Hit | No | No
OP | 7011650 | EB_BER_RE09 | East Bay | 2015-05-01 01:59 | 15.3 | 15 | 0.3 | 2% | Design Issue |  |  | Albany system fed by multiple reg stations, appears to be a negative interaction b/w regs at nearby stations. |  | HP Distribution | Small OP Event | No | No |  | ACE |  | H-14 | GD.STAT.DIST.00351 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Rch\Tif\Gas\RegStation\0804753.PDF
Near Hit | 7015121 | SA_SAC_S013 | Sacramento | 2015-05-01 23:55 | 55.22 | 60 | -4.78 | -7.967% | SP Too Close to MOP/HiHi |  |  |  | Continued to monitor pressure trends | HP Distribution | Near Hit | No | No
Near Hit | 7015123 | SA_SAC_S013 | Sacramento | 2015-05-02 00:05 | 55.22 | 60 | -4.78 | -7.967% | SP Too Close to MOP/HiHi |  |  |  | Tech was not sent out that evening | HP Distribution | Near Hit | No | No
Near Hit | 7015129 | NB_NAP_I006 | North Bay | 2015-05-02 01:19 | 144 | 150 | -6 | -4% | Failure - Contaminants |  |  |  | I&R Tech inspected the pilot and found evidence of sulfur build up. A sulfur filter/trimmer was installed on the Mooney pilot. | Transmission | Near Hit | No | No
Near Hit | 7015124 | FR_FRE_RA18 | Fresno | 2015-05-03 01:30 | 57.1 | 60 | -2.9 | -4.833% | Failure - Contaminants |  |  |  | Tech Rebuilt regulator, as left pressure 54.6 PSIG | HP Distribution | Near Hit | No | No
Near Hit | 7015125 | SA_SAC_S013 | Sacramento | 2015-05-04 23:09 | 55 | 60 | -5 | -8.333% | SP Too Close to MOP/HiHi |  |  |  | Alarm set points need to be adjusted | HP Distribution | Near Hit | No | No
Near Hit | 7015126 | SA_SAC_S013 | Sacramento | 2015-05-05 22:37 | 55 | 60 | -5 | -8.333% | SP Too Close to MOP/HiHi |  |  |  | Alarm set points need to be adjusted | HP Distribution | Near Hit | No | No
Near Hit | 7015127 | SA_SAC_S013 | Sacramento | 2015-05-06 22:36 | 55 | 60 | -5 | -8.333% | SP Too Close to MOP/HiHi |  |  |  | Alarm set points need to be adjusted | HP Distribution | Near Hit | No | No
Near Hit | 7015128 | YO_ATW_S018 | Yosemite | 2015-05-08 23:51 | 40.2 | 45 | -4.8 | -10.67% | SP Too Close to MOP/HiHi |  |  |  | Immediate Actions - I&R will be working with Planning in the next course of action in revolving the set points issue | HP Distribution | Near Hit | No | No
Near Hit | 7015140 | YO_ATW_S018 | Yosemite | 2015-05-11 23:49 | 40.59 | 45 | -4.41 | -9.8% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7015141 | YO_ATW_S018 | Yosemite | 2015-05-12 23:49 | 40.59 | 45 | -4.41 | -9.8% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7015142 | YO_ATW_S019 | Yosemite | 2015-05-13 23:49 | 40.59 | 45 | -4.41 | -9.8% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7012110 | BRT_PT16_58U | Diablo | 2015-05-16 17:39 | 483 | 497 | -14 | -2.817% | Failure - Equipment |  |  |  | Immediate Actions: • Tech was sent out to Brentwood Terminal and V-60 was manually closed (Temporary) • In the process of ordering new mother board V-60. Arrival is approximately 3 to 5 business days. Future and suggested CAs/Tasks: • Per FIMP e-mail, discussion has been initiated to review failure modes of regulation and monitor. (Terry W. and William M.) | Transmission | Near Hit | No | No
Near Hit | 7015143 | FLB_PT0001 | Tracy District | 2015-05-18 01:00 | 385.75 | 394 | -8.25 | -2.094% | Failure - Contaminants |  |  |  | Technician took immediate actions to reduce pressure and remedy the situation. This was done by shutting in the lead run and rebuilding the regulator set up. Future corrective actions are to install sulfur-gon filters has begun. Work in stages has been ongoing project 183521. | Transmission | Near Hit | No | No
Near Hit | 7012104 | MIS_PT0045 | Mission | 2015-05-18 12:15 | 271 | 500 | -229 | -45.8% | Failure - Equipment |  |  |  | Kelly Jones currently performing sassessment | Transmission | Near Hit | No | No
Near Hit | 7015145 | SF_SF_S037 | Peninsula | 2015-05-19 15:04 | 10.5 | 12 | -1.5 | -12.5% | SP Too Close to MOP/HiHi |  |  |  | Immediate respnse - called to the field, regs need to be adjusted | LP Distribution | Near Hit | No | No
OP | 7012117 | KE_BKD_R143 | Kern | 2015-05-21 11:55 | 52.7 | 51 | 1.7 | 3.333% | Maintenance Operations Quality | HU |  | Wrong steps in performing lockup test, used outlet fire valve over-pressuring pipe b/w reg run block valve and outlet valve. | Immediate Actions: • Another crew was dispatched to the site and proceeds with C-Inspection. Crew completed the C-Inspection and reg lock up set and checked to 47 psig. | HP Distribution | Small OP Event | No | No | No | ACE |  | H-14 | GD.STAT.DIST.01475 | file://utility.pge.com/projects/metcat/metcatprd-fs01/COMP_PUB/Bkd/Tif/Gas/RegStation/0807465.PDF
Near Hit | 7015147 | SMS_PT0005 | Sacramento | 2015-06-01 09:35 | 95 | 95.4 | -0.4 | -0.4193% | Failure - Equipment |  |  |  | Immediate actions followed – rubber goods were replaced and lock up checked | Transmission | Near Hit | No | No |  |  |  |  | 0
Near Hit | 7015146 | SF_SF_S037 | Peninsula | 2015-06-02 00:58 | 10.5 | 12 | -1.5 | -12.5% | SP Too Close to MOP/HiHi |  |  |  | Immediate response - Tech sent out to inspect, guaged pressure, and point was trending down. On call advised GDCC to continue to monitor and call back if the HIHI is breached | LP Distribution | Near Hit | No | No
Near Hit | 7015148 | SMS_PT0005 | Sacramento | 2015-06-05 17:27 | 91.1 | 95.4 | -4.3 | -4.507% | Failure - Equipment |  |  |  | Tech rebuiltt reg V-13 and set at 75 psig, and fixef leak on senseline to v-12 | Transmission | Near Hit | Yes | No |  |  |  |  | GT.STAT.LVCR.0000000523
Near Hit | 7015149 | KE_BKD_R118 | Kern | 2015-06-07 18:52 | 8.8 | 12 | -3.2 | -26.67% | SP Too Close to MOP/HIHI |  |  |  | Immediate Notification - alarm pressure not recorded in daily, reported max value was NOP, actual pressure reading per scada is 8.82 psig | LP Distribution | Near Hit | No | No
Near Hit | 7015150 | K15_PT0032 | Yosemite | 2015-06-11 09:22 | 771 | 890 | -119 | -13.37% | Failure - Equipment |  |  |  | Immediate actions - valve was closed by GTCC and D/S pressure stabilized and returned to normal | Transmission | Near Hit | No | No
Near Hit | 7015151 | ST_LOD_RL43 | Stockton | 2015-06-15 02:32 | 54 | 60 | -6 | -10% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7015152 | SI_RSC_S001 | Sierra | 2015-06-17 02:24 | 58.1 | 60 | -1.9 | -3.167% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7015156 | SI_RSC_S001 | Sierra | 2015-06-18 00:39 | 58.1 | 60 | -1.9 | -3.167% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7015157 | SI_RSC_S001 | Sierra | 2015-06-19 02:40 | 58.1 | 60 | -1.9 | -3.167% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7015158 | SI_RSV_S001 | Sierra | 2015-06-20 00:29 | 58.1 | 60 | -1.9 | -3.167% | SP Too Close to MOP/HiHi |  |  |  | Tech went out to Reg Station 406 and adjusted the set point | HP Distribution | Near Hit | No | No
Near Hit | 7015161 | SI_RSV_S003 | Sierra | 2015-06-20 01:53 | 58.1 | 60 | -1.9 | -3.167% | SP Too Close to MOP/HiHi |  |  |  | Tech went out to Reg Station 406 and adjusted the set point | HP Distribution | Near Hit | No | No
Near Hit | 7015162 | SI_RSV_R619 | Sierra | 2015-06-20 02:07 | 58.1 | 60 | -1.9 | -3.167% | SP Too Close to MOP/HiHi |  |  |  | Tech went out to Reg Station 406 and adjusted the set point | HP Distribution | Near Hit | No | No
Near Hit | 7015159 | SI_RSV_S002 | Sierra | 2015-06-20 02:16 | 58.1 | 60 | -1.9 | -3.167% | SP Too Close to MOP/HiHi |  |  |  | Tech went out to Reg Station 406 and adjusted the set point | HP Distribution | Near Hit | No | No
Near Hit | 7015163 | SF_SF_S037 | San Francisco | 2015-06-22 13:49 | 10.83 | 12 | -1.17 | -9.75% | SP Too Close to MOP/HiHi |  |  |  | Immediate notification of I&R and GDCC will continue to monitor if its reach 11" W.C. | LP Distribution | Near Hit | No | No
Near Hit | 7013423 | SF_SF_S037 | San Francisco | 2015-06-23 10:48 | 10.6 | 12 | -1.4 | -11.67% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification to I&R | LP Distribution | Near Hit | No | No
Near Hit | 7015165 | SO_PET_R495_PT3 | Sonoma | 2015-06-24 12:46 | 49.03 | 50 | -0.97 | -1.94% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7015164 | SA_FAO_S011 | Sacramento | 2015-06-24 23:52 | 48.21 | 60 | -11.79 | -19.65% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7015166 | SF_SF_S037 | San Francisco | 2015-06-25 13:22 | 10.54 | 12 | -1.46 | -12.17% | SP Too Close to MOP/HiHi |  |  |  | Low demand | LP Distribution | Near Hit | No | No
Near Hit | 7015168 | SI_AUB_S008 | Sierra | 2015-06-25 23:20 | 59.26 | 60 | -0.74 | -1.233% | SP Too Close to MOP/HiHi |  |  |  | Reg running high. Hotter | HP Distribution | Near Hit | No | No
Near Hit | 7015169 | SI_AUB_S007 | Sierra | 2015-06-25 23:20 | 59.07 | 60 | -0.93 | -1.55% | SP Too Close to MOP/HiHi |  |  |  | Reg running high. Hotter | HP Distribution | Near Hit | No | No
Near Hit | 7015170 | SI_AUB_R234 | Sierra | 2015-06-25 23:20 | 59.07 | 60 | -0.93 | -1.55% | SP Too Close to MOP/HiHi |  |  |  | Reg running high. Hotter | HP Distribution | Near Hit | No | No
Near Hit | 7015173 | SF_SF_S037 | San Francisco | 2015-06-26 13:22 | 10.54 | 12 | -1.46 | -12.17% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notificaton | LP Distribution | Near Hit | No | No
Near Hit | 7015174 | SI_AUB_S008 | Sierra | 2015-06-26 23:20 | 59.26 | 60 | -0.74 | -1.233% | SP Too Close to MOP/HiHi |  |  |  | Tech responded and lowered reg set point | HP Distribution | Near Hit | No | No
Near Hit | 7015175 | SI_AUB_R234 | Sierra | 2015-06-26 23:20 | 59 | 60 | -1 | -1.667% | SP Too Close to MOP/HiHi |  |  |  | Tech responded and lowered reg set point | HP Distribution | Near Hit | No | No
Near Hit | 7015176 | SI_AUB_S007 | Sierra | 2015-06-26 23:20 | 59.07 | 60 | -0.93 | -1.55% | SP Too Close to MOP/HiHi |  |  |  | Tech responded and lowered reg set point | HP Distribution | Near Hit | No | No
Near Hit | 7015172 | SF_SF_S037 | San Francisco | 2015-06-27 14:00 | 10.8 | 12 | -1.2 | -10% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification and e-mail has been sent to GDCC supervisor regarding the repeating incident | LP Distribution | Near Hit | No | No
Near Hit | 7015178 | SF_SF_S037 | San Francisco | 2015-07-01 01:11 | 10.8 | 12 | -1.2 | -10% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notificaton | LP Distribution | Near Hit | No | No
Near Hit | 7013750 | DA_SUN_RC30_PT1 | DeAnza | 2015-06-30 06:12 | 178.4 | 180 | -1.2 | -10% | SP Too Close to MOP/HiHi |  |  |  | Immediate Action Followed - • GTCC contacted Clearance Supervisor regarding the HIHI alarm • Supervisor mentioned that Field Techs were on site performing a Clearance • Techs gauge the pipeline to verify the SCADA reading and a 0.3 psig difference was reported | Transmission | Near Hit | Yes | No
OP | 7013743 | EB_BER_RE09 | East Bay | 2015-06-09 02:19 | 15.2 | 15 | 0.2 | 1.333% | Design Issue |  |  | Albany system fed by multiple reg stations, appears to be a negative interaction b/w regs at nearby stations. | Tech onsite found the reg at Scenic and Virginia in Berkeley was feeding very heavily. When he shut in the reg, system pressure recovered below MOP almost immediately. Tech found debris in the boot, currently investigating why monitor didn't take control. | HP Distribution | Small OP Event | No | No |  | ACE |  | H-14 | GD.STAT.DIST.00343
Near Hit | 7015180 | SF_SF_S037 | San Francisco | 2015-07-03 02:15 | 10.8 | 12 | -1.2 | -10% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notificaton | LP Distribution | Near Hit | Yes | No
Near Hit | 7015181 | SF_SF_S037 | San Francisco | 2015-07-07 01:28 | 10.97 | 12 | -1.03 | -8.583% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | LP Distribution | Near Hit | Yes | No
Near Hit | 7015182 | SA_SAC_S014_PT1 | Sacramento | 2015-07-08 02:06 | 47.03 | 50 | -2.97 | -5.94% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7015183 | JLL_PT0003 | DeAnza | 2015-07-07 01:12 | 185 | 400 | -215 | -53.75% | Clearance Preparation |  |  |  |  | Transmission | Near Hit | Yes | No
Near Hit | 7015184 | JWF_PT0002 | Central Coast | 2015-07-06 10:00 | 383.3 | 400 | -16.7 | -4.175% | Clearance execution |  |  |  | Immediate action was taken to prevent overpressure | Transmission | Near Hit | Yes | No
Near Hit | 7015185 | MMT_PT1314 | Milpitas District | 2015-07-03 08:44 | 407 | 477 | -70 | -14.68% | Maintenance Operations Quality |  |  |  | RCV 66/67 were shut to isolate and work was stopped until an investigation could be performed. | Transmission | Near Hit | No | No
Near Hit | 7015187 | Gauge | Central Coast | 2015-07-02 11:25 | 383.27 | 400 | -16.73 | -4.183% | Maintenance Operations Quality |  |  |  |  | Transmission | Near Hit | No | No
Near Hit | 7015188 | FCY_PT0003 | Fresno | 2015-07-02 13:06 | 202.7 | 204 | -1.3 | -0.6373% | Maintenance Operations Quality |  |  |  |  | Transmission | Near Hit | Yes | No
Near Hit | 7015189 | SF_SF_S021 | San Francisco | 2015-07-12 03:50 | 13.5 | 15 | -1.5 | -10% | Calibration |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7015190 | SJ_SJS_RF13 | San Jose | 2015-07-13 16:00 | 330 | 60 | 270 | 450% | Clearance Execution |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7015191 | ST_LOD_RL43_PT3 | Stockton | 2015-07-16 01:08 | 57.7 | 60 | -2.3 | -3.833% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7015192 | FR_KMN_S011_PS1_HI | Fresno | 2015-07-15 12:22 | 52.2 | 53 | -0.8 | -1.509% | Calibration |  |  |  |  | HP Distribution | Near Hit | Yes | No
OP | 7013997 | SNH_PT0011 | Sacramento | 2015-07-08 09:55 | 183.6 | 180 | 3.6 | 2% | Clearance Execution |  |  | Clearance procedure not followed, opened valve instead of throttling through valve. Throttling SP was also too close to MAOP. | Immediate Actions Followed: • GTCC contacted Clearance Supervisor • V-1 was closed at 275.8 psig on L-119C and V-B at NSUH was blew down instead of drafting from V-1 | Transmission | Small OP Event | Yes | No |  | ACE |  |  | GT.STAT.MISC.NSACHOLDER | 382860.pdf
OP | 7014357 | SMS_PT0005 | Sacramento | 2015-07-16 14:10 | 128.7 | 95.4 | 33.3 | 34.91% | Design Issue | EQ | P5 | Failure mode analysis not completed on losing flow signal during engineering review. Software problem in meter controller. | • I&R crew verified regulation lock up – no indications of lock up • A 20% reduction in pressure was ordered • Leak survey was performed • A Root Cause Analysis task force has been initiated | Transmission | Large OP Event | Yes | No |  | ACE |  | LVCR | GT.STAT.LVCR.0000000523 |  | LVC
Near Hit | 7015193 | SF_SF_S021 | San Francisco | 2015-07-19 03:40 | 12.9 | 15 | -2.1 | -14% | Calibration |  |  |  | Not enough information | HP Distribution | Near Hit | Yes | No
Near Hit | 7015194 | SF_SF_S021 | San Francisco | 2015-07-20 04:24 | 12.9 | 15 | -2.1 | -14% | Calibration |  |  |  | Not enough information | HP Distribution | Near Hit | Yes | No
OP | 7019938 | AAN_PTCCPP | Los Medanos District | 2015-07-24 15:53 | 196.5 | 195 | 1.5 | 0.7692% | Maintenance Operations Quality |  |  | Technician rebuilt monitor pilot improperly, regulation significantly oversized for load. | Line is scheduled to be converted to distribution and returned coming out Antioch Terminal in Late 2015. Due to the fact this is a dead-end system; a corrective action to complete this work will be submitted into the CAP Notification. Training and tailboard to be given to the crew to emphasize importance of following procedures and attention to detail. | Transmission | Small OP Event | Yes | Yes |  | ACE |  |  | GT.STAT.MISC.ANTGSTPLS_ | 4807103.pdf
Near Hit | 7015341 | EB_HER_S024 | East Bay | 2015-07-30 03:04 | 44 | 45 | -1 | -2.222% | SP Too Close to MOP/HIHI |  |  |  |  | HP Distribution | Near Hit | Yes | Yes
Near Hit | 7015333 | NB_RBL_R125 | North Valley | 2015-07-30 23:09 | 55 | 60 | -5 | -8.333% | SP Too Close to MOP/HiHi |  |  |  | GDCC will continue to monitor and if the HIHI alarm limit is triggered again to contact I&R Supervisor | HP Distribution | Near Hit | No | No
Near Hit | 7015831 | SI_AUB_R234_PT3 | Sierra | 2015-07-30 23:25 | 59 | 60 | -1 | -1.667% | SP Too Close to MOP/HiHi |  |  |  | Tech will return to ERX site (10570 Kay Les Lane) during daylight hours because the ERX is located in the bushes. | HP Distribution | Near Hit | Yes | No
Near Hit | 7015334 | SI_AUB_S008 | Sierra | 2015-07-30 23:25 | 59 | 60 | -1 | -1.667% | SP Too Close to MOP/HiHi |  |  |  | Tech will return to ERX site (10570 Kay Les Lane) during daylight hours because the ERX is located in the bushes. | HP Distribution | Near Hit | Yes | No
Near Hit | 7015335 | EB_HER_S024 | East Bay | 2015-07-31 00:58 | 44 | 45 | -1 | -2.222% | Calibration |  |  |  | Tech determined 10 psig differences between the field reading and SCADA. The Tech calibrated the ERX unit. | HP Distribution | Near Hit | No | No
Near Hit | 7015336 | YO_DEL_S029 | Yosemite | 2015-07-31 01:09 | 53 | 60 | -7 | -11.67% | SP Too Close to MOP/HiHi |  |  |  | N/A | HP Distribution | Near Hit | Yes | No
Near Hit | 7015422 | JLL_PT0003 | DeAnza | 2015-07-30 21:45 | 230 | 400 | -170 | -42.5% | Failure - Equipment |  |  |  | Course of action for V-A and V-B (Replacement and/or separate vent stack) by Pipeline Engineering | Transmission | Near Hit | Yes | No
Near Hit | 7015480 | YO_OKD_RP03 | Yosemite | 2015-08-02 01:39 | 47 | 50 | -3 | -6% | SP Too Close to MOP/HiHi |  |  |  | On call was notified and requested for Operator to continue to monitor | HP Distribution | Near Hit | No | No
Near Hit | 7015481 | YO_OKD_RP03 | Yosemite | 2015-08-03 01:04 | 47 | 50 | -3 | -6% | SP Too Close to MOP/HiHi |  |  |  | On call was notified and requested for Operator to continue to monitor | HP Distribution | Near Hit | No | No
OP | 7015601 | BMD_PT0020 | McDonald Island District | 2015-08-03 09:00 | 1211 | 1025 | 186 | 18.15% | Maintenance Operations Quality | HU | P50.2 | Improper clearance steps, inadequate review of clearance changes . | • A Safety Stand Down to be facilitated by management regarding the Over Pressurization at McDonald Island (Jody Garcia and Louis Krannich). Currently, the Safety Stand Down Meetings are conducted at 7:00 AM by Louis K. that discuss past OP Events and the findings. • Affected segment of pipe has been depressurized at this moment, and there is plan for deactivation in the near future • Per discussion with Station Services, there is a in process Over Pressure Protection project that includes the following:  V-38 is being automated to close at 1020 psig  Relief has also been added that will be set at 1025 psig | Transmission | Large OP Event | Yes | Yes |  | ACE |  | H-19 | GT.STAT.COMP.MCDONLDISL | 385179.pdf
OP | 7015706 | Gauge | San Jose | 2015-08-06 10:49 | 154 | 38 | 116 | 305.3% | Clearance Preparation | HU | P95.8 | The purging process created high flows, when station was disassembled metal debris was discovered in the regulator and monitor. | Crew took immediate steps to reduce overpressure by switching runs. Leak survey was conducted – no leaks were found, customer regulators were replaced, equipment was taken apart, and GDED was contacted to conduct necessary analysis. | HP Distribution | Large OP Event | No | No | No | ACE |  | H-14 | GD.STAT.DIST.00445 | file://utility.pge.com/projects/metcat/metcatprd-fs01/comp_pub/Cuo/Tif/Gas/regstation/0808087.PDF | H10
Near Hit | 7015832 | SA_VAC_S052 | Sacramento | 2015-08-10 03:17 | 58.41 | 60 | -1.59 | -2.65% | SP Too Close to MOP/HiHi |  |  |  | Further monitor per on call supervisor request | HP Distribution | Near Hit | Yes | No
Near Hit | 7015982 | M19_PT0105 | Hollister District | 2015-08-07 14:15 | 388.1 | 396 | -7.9 | -1.995% | Maintenance Operations Quality |  |  |  |  | Transmission | Near Hit | Yes | No
Near Hit | 7016255 | SA_TAB_S048 | Sacramento | 2015-08-18 23:04 | 37.9 | 40 | -2.1 | -5.25% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7015652 | Gauge | Sacramento | 2015-07-29 09:00 | 567 | 720 | -153 | -21.25% | Failure - Equipment |  |  |  | Crew shut in the meter set and pressure was relieved on the meter set piping. | HP Distribution | Near Hit | No | No
Near Hit | 7016420 | YO_MAD_RB41 | Yosemite | 2015-08-23 01:37 | 39 | 42 | -3 | -7.143% | Unknown/ Not Recorded |  |  |  | Pressure steadied out and began to decline. Pheng Ly state would send someone in morning to investigate unless continues to rise. | HP Distribution | Near Hit | Yes | No
OP | 7016683 | YO_TUR_S042 | Yosemite | 2015-08-28 11:23 | 16 | 12 | 4 | 33.33% | Maintenance Operations Quality | HU | P50.2 | Firefighting water runoff filled up the regulating vault and submerged vent lines. Technican did not return vent lines to top of vault. | Leak survey using picarro, | LP Distribution | Large OP Event | No | No |  | ACE |  | H-14 | GD.STAT.LPRS.00183 | 0808759.PDF | H10
Near Hit | 7016803 | YO_MAD_RB41 | Yosemite | 2015-08-31 06:56 | 39.06 | 42 | -2.94 | -7% | Failure - Equipment |  |  |  | reduced set point pressure | HP Distribution | Near Hit | Yes | No
Near Hit | 7016777 | MI_FMT_RF59 | Mission | 2015-09-02 00:51 | 434 | 477 | -43 | -9.015% | Failure - Equipment |  |  |  | Tech out to field - PT 2 will probably be disconnected. | Transmission | Near Hit | No | No
Near Hit | 7017105 | YO_NEW_S025 | Yosemite | 2015-09-06 02:50 | 45.86 | 50 | -4.14 | -8.28% | SP Too Close to MOP/HiHi |  |  |  | keep monitoring | HP Distribution | Near Hit | No | No
OP | 7017104 | Gauge | Kern | 2015-09-08 14:40 | 35 | 32 | 3 | 9.375% | Maintenance Operations Quality |  |  | Technician failed to gauge pressure prior to and during return to service. Reg failured to hold set point due to rusted component. | Immediately reduce pressure, replace regulator, and leak survey service. | HP Distribution | Small OP Event | No | No | No | ACE |  | H-10 | 0
Near Hit | 7017228 | PN_SM_PA65 | Peninsula | 2015-09-15 04:34 | 33.9 | 34 | -0.1 | -0.2941% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | No | No
Near Hit | 7017229 | PN_SM_PA55 | Peninsula | 2015-09-15 04:39 | 32.9 | 34 | -1.1 | -3.235% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | No | No
Near Hit | 7017275 | YO_NEW_S025 | Yosemite | 2015-09-16 03:50 | 45.9 | 50 | -4.1 | -8.2% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | No | No
Near Hit | 7017601 | BRT_PT0057A | Diablo | 2015-09-22 19:39 | 531 | 536 | -5 | -0.9328% | Failure - Equipment |  |  |  | Configure valve operations to reduce pressure and bleed into L-131 Grease offending valve WR216437 has been submitted to investigate other leaking valves at Brentwood Terminal near L-57A. | Transmission | Near Hit | No | No
OP | 7017564 | SLC_PT0004 | Sierra | 2015-09-23 11:47 | 502.6 | 500 | 2.6 | 0.52% | Failure - Equipment | EQ |  | Mechanical damage of the Becker pilot diaphragm. | replace/rebuild pilot, MPR report monitor station | Transmission | Small OP Event | Yes | No |  | ACE |  |  | GT.STAT.MISC.LINCOLNJUC | 0811591.pdf
Near Hit | 7017787 | SF_SF_S037_PT1_HI | San Francisco | 2015-09-25 01:11 | 10.64 | 12 | -1.36 | -11.33% | Inspection Related |  |  |  | Possibly due to an A inspection. Recent maintenance-field anticipated pressure increase. Will investigate today. SF pressure increase was simply a result of known elevation changed in the Mt Davidson system. Anytime we perform station maintenance, we interrupt this happy system and redo set points until system balance is restored. We adjusted set points on Friday last week to address the pressure problem. | LP Distribution | Near Hit | Yes | No
Near Hit | 7017788 | YO_DEL_S029 | Yosemite | 2015-09-25 23:34 | 51.53 | 60 | -8.47 | -14.12% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7017789 | ST_LOD_RL43 | Stockton | 2015-09-26 01:41 | 57 | 60 | -3 | -5% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7017790 | FR_FRE_RJ36_PT3 | Fresno | 2015-09-26 19:30 | 57 | 60 | -3 | -5% | SP Too Close to MOP/HiHi |  |  |  | Tech lowered set point | HP Distribution | Near Hit | Yes | No
Near Hit | 7017791 | YO_NEW_S025 | Yosemite | 2015-09-27 06:33 | 45.82 | 50 | -4.18 | -8.36% | SP Too Close to MOP/HiHi |  |  |  | Tech lowered set point | HP Distribution | Near Hit | Yes | No
OP | 7017769 | Gauge | North Valley | 2015-09-29 18:45 | 42 | 40 | 2 | 5% | Gas Contaminants - Debris | EQ |  | Weld slag from first stage construction entrained into downstream stages of regulation. | Start-up check list for regulator stations | HP Distribution | Small OP Event | Yes | No | No | ACE |  | H-14 | GD.STAT.DIST.01514 | file://utility.pge.com/projects/metcat/metcatprd-fs01/COMP_PUB/Rdg/Tif/Gas/REGSTATION/0807101.PDF
Near Hit | 7017974 | SA_DVS_S021 | Sacramento | 2015-10-01 03:17 | 55.09 | 60 | -4.91 | -8.183% | SP Too Close to MOP/HiHi |  |  |  | Increased alarem set point | HP Distribution | Near Hit | Yes | No
Near Hit | 7017975 | FR_FOW_RL51 | Fresno | 2015-10-01 22:44 | 49.3 | 52 | -2.7 | -5.192% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7017976 | FR_FOW_RL52 | Fresno | 2015-10-01 22:44 | 49.3 | 52 | -2.7 | -5.192% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7017977 | SA_DVS_S021 | Sacramento | 2015-10-02 02:48 | 55.08 | 60 | -4.92 | -8.2% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7018252 | SA_DVS_S021 | Sacramento | 2015-10-05 01:01 | 55 | 60 | -5 | -8.333% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7018253 | YO_DEL_S029 | Yosemite | 2015-10-06 18:18 | 51.75 | 60 | -8.25 | -13.75% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7018161 | RKS_PT0002 | Santa Rosa | 2015-10-07 10:26 | 642 | 720 | -78 | -10.83% | Failure - Equipment |  |  |  | Immediate action – crew reopened control valve and stabilized the pressure below the MOP limit. | Transmission | Near Hit | No | Yes
OP | 7018290 | NV_BIG_S028 | North Valley | 2015-10-09 04:45 | 61.24 | 60 | 1.24 | 2.067% | Gas Contaminants - Debris | EQ |  | Weld slag post construction entrained into downstream stages of regulation. | Pressure reduced to 53 psig | HP Distribution | Small OP Event | Yes | No |  | ACE |  | H-14 | GD.STAT.DIST.01303 | file://utility.pge.com/projects/metcat/metcatprd-fs01/comp_pub/Chi/Tif/Gas/REGSTATION/0806950.PDF
Near Hit | 7018802 | SO_HLB_R52_PT3 | Sonoma | 2015-10-10 03:40 | 47.03 | 50 | -2.97 | -5.94% | SP Too Close to MOP/HiHi |  |  |  | will call back | HP Distribution | Near Hit | Yes | No
OP | 7018460 | Gauge | San Jose | 2015-10-12 10:56 | 60.8 | 60 | 0.8 | 1.333% | Clearance Preparation |  |  | Clearance steps to replace fire valve did not shut-in regulator station prior to d/s isolation, and created dead-end system. |  | HP Distribution | Small OP Event | Yes | No | No | ACE |  | H-14 | GD.STAT.DIST.00450
Near Hit | 7018802 | SO_HLB_RR52_PT3 | Sonoma | 2015-10-16 | 47.06 | 50 | -2.94 | -5.88% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7019449 | DA_LGS_RD24_PT3 | DeAnza | 2015-10-27 22:05 | 59 | 60 | -1 | -1.667% | SP Too Close to MOP/HiHi |  |  |  | Continued to monitor pressure trends | HP Distribution | Near Hit | Yes | No
Near Hit | 7019511 | DI_OKL_S015 | Diablo | 2015-10-28 01:05 | 58 | 60 | -2 | -3.333% | SP Too Close to MOP/HiHi |  |  |  | Continued to monitor pressure trends | HP Distribution | Near Hit | Yes | No
OP | 7019514 | EB_RCH_RG06 | East Bay | 2015-10-27 10:42 | 13.68 | 12 | 1.68 | 14% | Maintenance Operations Quality | HU |  | During inspection technician overshot regulator set point on LP station fed directly from TP. |  | LP Distribution | Small OP Event | No | No |  | ACE |  | 1 | GD.STAT.LPRS.00128 | file://utility.pge.com/projects/metcat/metcatprd-fs01/comp_pub/RCH/Tif/Gas/REGSTATION/0804766.pdf
Near Hit | 7019752 | DI_OKL_S015 | Diablo | 2015-10-29 01:25 | 58 | 60 | -2 | -3.333% | SP Too Close to MOP/HiHi |  |  |  | Continued to monitor pressure trends | HP Distribution | Near Hit | Yes | No
Near Hit | 7019750 | DI_OKL_S015 | Diablo | 2015-10-31 00:38 | 58 | 60 | -2 | -3.333% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7020003 | HU_FTA_S009 | Humboldt | 2015-11-03 23:21 | 53 | 55 | -2 | -3.636% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
OP | 7019878 | OFW_PT0007 | East Bay | 2015-11-03 16:53 | 258.6 | 246 | 12.6 | 5.122% | Construction Quality |  |  | Water intruded an unsealed fitting which led to a short and malfunction causing the regulator to fail (open). | Extent of Condition Review – How many regulator valves do we have throughout the system that fail open on loss of a control input? These need an engineering review for what can be done so that these valves don’t quickly fail open increasing the likelihood and impact of an OP event. This is at least the 3rd OP Event we’ve had related to this type of failure in the past couple years. Also, we have a POD remedy to address this type of failure on PLC controlled valves, does this need to be expanded to all electronic controlled valves? Was the monitor versus regulator speeds set correctly? What type of validation have we done systemwide related to controller operated equipment and the speeds of monitor versus regulator valves? | Transmission | Small OP Event | No | No |  | ACE |  |  | GT.STAT.MISC.FAIRWAY153 | 082424.pdf
Near Hit | 7020227 | SI_MVL_EX02 | Sierra | 2015-10-29 15:45 |  | 53 | -53 | -100% | Clearance execution |  |  |  | Immediate corrective actions - Reset slam shut at regulator station - Complete uprate of LP distribution system | HP Distribution | Near Hit | No | No
Near Hit | 7020004 | NV_RBL_R125_PT3 | North Valley | 2015-11-04 23:32 | 55 | 60 | -5 | -8.333% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7020049 | DA_LGS_RD24 | Diablo | 2015-11-05 21:03 | 59 | 60 | -1 | -1.667% | Failure - Equipment |  |  |  | Transducer calibrated | HP Distribution | Near Hit | Yes | No
Near Hit | 7020228 | YO_HUS_S034 | Yosemite | 2015-11-11 13:06 | 51 | 52 | -1 | -1.923% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7020229 | YO_HUS_S034 | Yosemite | 2015-11-12 11:54 | 51 | 52 | -1 | -1.923% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7020193 | Gauge | North Valley | 2015-10-30 09:00 | 50 | 53 | -3 | -5.66% | Maintenance Operations Quality |  |  |  |  | HP Distribution | Near Hit | No | No
Near Hit | 7020440 | EB_OAK_RB82_PT3 | East Bay | 2015-11-13 12:27 | 11.05 | 12 | -0.95 | -7.917% | Clearance Preparation |  |  |  | an alarm of this nature it is either because 1. They are taking the line or reg station out of service and therefore point will drop to zero or 2. They are removing the point to reinstall at another location. | LP Distribution | Near Hit | No | No
Near Hit | 7020441 | ST_STK_RR28 | Stockton | 2015-11-13 10:14 | 10.5 | 12 | -1.5 | -12.5% | Clearance Preparation |  |  |  | an alarm of this nature it is either because 1. They are taking the line or reg station out of service and therefore point will drop to zero or 2. They are removing the point to reinstall at another location. | LP Distribution | Near Hit | No | No
Near Hit | 7020634 | YO_ATW_S028 | Yosemite | 2015-11-21 16:42 | 43.1 | 45 | -1.9 | -4.222% | SP Too Close to MOP/HiHi |  |  |  | No further corrective actions | HP Distribution | Near Hit | No | No
Near Hit | 7020635 | DI_LFY_S007 | Diablo | 2015-11-21 22:05 | 56 | 60 | -4 | -6.667% | SP Too Close to MOP/HiHi |  |  |  | Per morning brief, alarm set points were correctly changed during the winter clearance | HP Distribution | Near Hit | No | No
Near Hit | 7020741 | DA_MVW_RB38_PT1 | San Jose | 2015-11-22 13:25 | 178.2 | 180 | -1.8 | -1% | SP Too Close to MOP/HiHi |  |  |  | see abnormal incident report for more details ​South GSO Barabad received a Hi alarm on SCAD, he trended the pressure, made call out to crew working in field to make them aware of the rising pressure in the line. He was successful in preventing the crew from going any higher than they did. | Transmission | Near Hit | Yes | No
Near Hit | 7020742 | ATN_PT0002 | Burney District | 2015-11-20 01:15 | 899 | 905 | -6 | -0.663% | Gas Control Center Operations |  |  |  | see abnormal incident report for more details | Transmission | Near Hit | No | No
Near Hit | 7020743 | SSA_PT0009 | Sacramento | 2015-10-27 00:50 | 259.1 | 260 | -0.9 | -0.3462% | Gas Control Center Operations |  |  |  | see abnormal incident report for more details | Transmission | Near Hit | No | No |  |  |  | H-14 | GD.STAT.DIST.01090 | \\fairfield07\gis\giswebMiscFiles\GasStations\385186.pdf
OP | 7020781 | NLP_PT0007 | Peninsula | 2015-11-26 10:22 | 158.1 | 145 | 13.1 | 9.034% | Failure - Equipment |  |  | Incorrectly sized restrictor contributed to freezing and intermittent failure of the DNGP resulted in the valve swinging open. |  | Transmission | Small OP Event | No | No |  | ACE |  |  | GT.STAT.MISC.LOMTPKPLS_ | 081519.pdf
Near Hit | 7021195 | YO_ATW_S028 | Yosemite | 2015-12-01 19:54 | 43.1 | 45 | -1.9 | -4.222% | Low Demand |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7021196 | YO_ATW_S028 | Yosemite | 2015-12-05 18:24 | 43.56 | 45 | -1.44 | -3.2% | SP Too Close to MOP/HiHi |  |  |  | Immediate Notification | HP Distribution | Near Hit | No | No
Near Hit | 7020994 | AAN_PT0114S | Tracy District | 2015-12-05 09:20 | 514.5 | 720 | -205.5 | -28.54% | Clearance Execution |  |  | Gas control operations did not follow special instructions - clearance assumed high level of facility knowledge. | ▪ Review standard clearances to implement appropriate preventive measurements when dead-end systems are created ▪ Investigate and fix SAP administration rights that allow changes and bypass approval process | Transmission | Near Hit | No | No
Near Hit | 7021462 | EB_OAK_R100 | East Bay | 2015-12-10 03:46 | 9 | 12 | -3 | -25% | SP Too Close to MOP/HiHi |  |  |  |  | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.01480
OP | 7021385 | JSJ_PT0012 | San Jose | 2015-12-11 10:55 | 251.1 | 250 | 1.1 | 0.44% | Clearance Preparation |  |  | Shut-in block valve for reg lock-up test did not account for back up in pressure, and SP too close to MOP. | Publish TD-4125P-07 | Transmission | Small OP Event | Yes | No |  | ACE |  |  | GT.STAT.MISC.DIANALRCV_ | 082126.pdf
Near Hit | 7021386 | BRT_PT0065 | Diablo | 2015-12-11 10:18 | 727.7 | 867 | -139.3 | -16.07% | Gas Control Center Operations |  |  |  | Gas control operatios ndid not anticiipate spike in pressure upon valve operations | Transmission | Near Hit | No | No
Near Hit | 7021697 | HU_EUR_RP01 | Humboldt | 2015-12-16 00:36 | 47 | 50 | -3 | -6% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7021552 | MMT_PT1721 | Milpitas District | 2015-12-15 08:30 | 334 | 720 | -386 | -53.61% | Gas Control Center Operations |  |  |  |  | Transmission | Near Hit | Yes | No
OP | 7022303 7022242 | Chart Recorder | Yosemite | 2015-12-16 09:00 | 64 | 60 | 4 | 6.667% | Failure - Equipment | EQ |  | Unknown cause at the processing plant resulted in multiple pressure spikes. Update 2016 - suspected hot shutdown of customer equipment. See 2016 Cause - customer hot shutdown created overpressure event. Failure Equipment. |  | HP Distribution | Small OP Event | No | No | No | ACE |  | H-14 | GT.STAT.LVCR.0000000218 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Mer\Tif\Gas\REGSTATION\0805090.PDF
OP | 7021631 | YO_HLM_S041 | Yosemite | 2015-12-17 03:12 | 62.81 | 60 | 2.81 | 4.683% | Gas Contaminants - Liquids | EQ |  | Stand-by regulator partially failed open due to pilot icing causing a negative interaction between monitor and regulator. |  | HP Distribution | Small OP Event | Yes | No |  | ACE |  | H-14 | GD.STAT.DIST.00881
Near Hit | 7021615 7021714 | MMT_PT1721 | Milpitas District | 2015-12-16 15:35 | 332 | 720 | -388 | -53.89% | Gas Control Center Operations |  |  |  | see abnormal incident report for more details | Transmission | Near Hit | Yes | No
Near Hit | 7021549 | OOA_PT0002 | East Bay | 2015-12-17 11:06 | 183.8 | 275 | -91.2 | -33.16% | Maintenance Operations Quality |  |  | Regulator trimmer & load valve lock-up/leak caused pressure to increase downstream in the dead-end system created to isolate piping for valve removal. |  | Transmission | Near Hit | Yes | No
Near Hit | 7021715 | OFW_PT0007 | East Bay | 2015-12-18 16:07 | 235.6 | 246 | -10.4 | -4.228% | Failure - Equipment |  |  |  | see abnormal incident report for more details | Transmission | Near Hit | Yes | No
Near Hit | 7021721 | ACD_PT0007B | Sacramento | 2015-12-21 14:21 | 650.7 | 650 | 0.7 | 0.1077% | HF/WPE - Manual Operations |  |  |  |  | Transmission | Near Hit | No | No
OP | 7021967 | BMD_PT0043 | McDonald Island District | 2015-12-26 07:59 | 1043 | 1025 | 18 | 1.756% | Design Issue |  |  | Malfunctioned valve actuator allowed withdrawal gas to enter the suction piping and relief valve did not limit pressure to below MAOP levels. | V-53 was grease and under observation by local crew | Transmission | Small OP Event | No | No |  | ACE |  |  | GT.STAT.COMP.MCDONLDISL | 385179.pdf
Near Hit | 7022027 | SJ_SJS_RF31 | San Jose | 2015-12-29 11:32 | 11.43 | 12 | -0.57 | -4.75% | Failure - Equipment |  |  |  | Tech adjusted regulator to 9.6" WC (AL) | LP Distribution | Near Hit | No | No
Near Hit | 7022181 | ST_STK_RR32 | Stockton | 2015-12-30 10:00 | 11.19 | 12 | -0.81 | -6.75% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7022182 | ST_STK_RR46_PT3 | Stockton | 2016-01-05 22:25 | 11.08 | 12 | -0.92 | -7.667% | Failure - Equipment | EQ |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7022183 | ST_STK_S009 | Stockton | 2016-01-05 22:45 | 10.7 | 12 | -1.3 | -10.83% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00209
Near Hit | 7022184 | ST_STK_S008 | Stockton | 2016-01-05 22:45 | 10.7 | 12 | -1.3 | -10.83% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00208
Near Hit | 7022284 | EB_RCH_S014 | East Bay | 2016-01-06 06:46 | 7.92 | 5 | 2.92 | 58.4% | Failure - Equipment | EQ |  |  | site specific | HP Distribution | Near Hit | No | No
Near Hit | 7022444 | SO_UKI_S024 | Sonoma | 2016-01-11 23:30 | 23.04 | 25 | -1.96 | -7.84% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7022445 | SO_UKI_S023 | Sonoma | 2016-01-11 00:33 | 23.04 | 25 | -1.96 | -7.84% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7022446 | EB_BER_RB05_PT3 | East Bay | 2016-01-13 01:05 | 10.52 | 12 | -1.48 | -12.33% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7022470 | ABY_PT0003 | Burney District | 2016-01-12 04:30 | 803 | 1000 | -197 | -19.7% | Maintenance Operations Quality | HU |  |  | Immediate actions were done - GTCC relieve pressure on the suction header side at Burney Station and stabilize the system | Transmission | Near Hit | No | Yes
Near Hit | 7022397 | K3B_PT0004 | Kern | 2016-01-12 08:09 | 766.6 | 803 | -36.4 | -4.533% | Failure - Equipment | EQ |  |  | CAP Notifications have been submitted for the issues at PLS 3 and PLS 4. These notifications are 7022433 and 7022434, respectively. | Transmission | Near Hit | No | No
Near Hit | 7022447 | ST_STK_RR46_PT3 | Stockton | 2016-01-13 11:52 | 10.55 | 12 | -1.45 | -12.08% | SP Too Close to MOP/HiHi |  |  |  | SRDR - see 7008493 from 2015 | LP Distribution | Near Hit | No | No
Near Hit | 7022448 | ST_STK_RR13_PT3 | Stockton | 2016-01-13 14:10 | 10.55 | 12 | -1.45 | -12.08% | SP Too Close to MOP/HiHi |  |  |  | SRDR - see 7008493 from 2015 | LP Distribution | Near Hit | No | No
Near Hit | 7022513 | SO_UKI_S024 | Sonoma | 2016-01-14 22:03 | 23.4 | 25 | -1.6 | -6.4% | SP Too Close to MOP/HiHi |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7022514 | SO_UKI_S023 | Sonoma | 2016-01-14 22:41 | 23.1 | 25 | -1.9 | -7.6% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7022578 | PN_SM_PA55 | Peninsula | 2016-01-16 00:30 | 33 | 34 | -1 | -2.941% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 9001972 | SO_UKI_S024 | Sonoma | 2016-01-17 00:37 | 23.4 | 25 | -1.6 | -6.4% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
OP | 9002063 | EB_OAK_RA16 | East Bay | 2016-01-18 01:00 | 13.19 | 12 | 1.19 | 9.917% | Maintenance Operations Quality | HU |  | Technician did not return vent lines to top of vault and during inclement weather water runoff filled up the regulating vault and submerged vent lines. |  | LP Distribution | Small OP Event | No | No | No | ACE |  | 1 | GD.STAT.LPRS.00072 | file://utility.pge.com/projects/metcat/metcatprd-fs01/comp_pub/Oak/Tif/Gas/RegStation/DRA16.PDF | 9 | 10.2 | 14
Near Hit | 7022585 | ST_STK_S008 | Stockton | 2016-01-18 03:30 | 10.68 | 12 | -1.32 | -11% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00208
Near Hit | 7022586 | ST_STK_S009 | Stockton | 2016-01-18 03:30 | 10.61 | 12 | -1.39 | -11.58% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00209
Near Hit | 7022587 | ST_STK_RR13_PT3 | Stockton | 2016-01-18 00:05 | 11.88 | 12 | -0.12 | -1% | Flooding |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
OP | 7022635 | ST_STK_RR46 | Stockton | 2016-01-18 05:32 | 12.25 | 12 | 0.25 | 2.083% | Failure - Equipment | EQ |  | Increased winter set points with low demand, poor lock-up issues and station interactions led to the overpressure event. |  | LP Distribution | Small OP Event | No | No | No | ACE |  | 1 | GD.STAT.LPRS.00226 | file://utility.pge.com/projects/metcat/metcatprd-fs01/COMP_PUB/Stk/Tif/Gas/REGSTATION/0804932.PDF | 9 | 10.2
Near Hit | 7022588 | YO_HUS_S034 | Yosemite | 2016-01-18 14:16 | 47.8 | 52 | -4.2 | -8.077% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7022610 | SA_SAC_RB37_PT3 | Sacramento | 2016-01-18 23:56 | 59 | 60 | -1 | -1.667% | Gas Contaminants | EQ |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7022611 | SA_EMC_S022 | Sacramento | 2016-01-19 00:07 | 56.3 | 60 | -3.7 | -6.167% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7022613 | SA_SAC_S067 | Sacramento | 2016-01-19 02:36 | 11 | 12 | -1 | -8.333% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7022611 | SA_EMC_S022 | Sacramento | 2016-01-19 14:52 | 56.13 | 60 | -3.87 | -6.45% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7022636 | ST_STK_S008 | Stockton | 2016-01-20 14:16 | 11 | 12 | -1 | -8.333% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00208
Near Hit | 7022637 | ST_STK_S009 | Stockton | 2016-01-20 14:18 | 10.8 | 12 | -1.2 | -10% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00209
Near Hit | 7022638 | ST_STK_RR46_PT3 | Stockton | 2016-01-20 14:18 | 11.1 | 12 | -0.9 | -7.5% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7022639 | ST_STK_S009 | Stockton | 2016-01-21 11:37 | 10.57 | 12 | -1.43 | -11.92% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00209
Near Hit | 7022690 | ST_STK_S008 | Stockton | 2016-01-21 11:39 | 10.57 | 12 | -1.43 | -11.92% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00208
Near Hit | 7022634 | ST_STK_RR46_PT3 | Stockton | 2016-01-21 11:37 | 11.01 | 12 | -0.99 | -8.25% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7022692 | ST_STK_RR13_PT3 | Stockton | 2016-01-21 11:37 | 11.01 | 12 | -0.99 | -8.25% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7022875 | SA_EMC_S022 | Sacramento | 2016-01-26 14:30 | 56 | 60 | -4 | -6.667% | SP Too Close to MOP/HiHi |  |  |  | This alarm limit was reviewed by the local engineer and it was decided that we would raise the limit to 59 PSIG. This alarm limit change was made today. This change to 1 psig below MOP is within the guidelines of the latest standard. | HP Distribution | Near Hit | Yes | No
Near Hit | 7022793 | SSW_PT0007 | Sacramento | 2016-01-24 05:49 | 511 | 520 | -9 | -1.731% | Failure - Equipment | EQ |  | Brief mechanical malfunction resulted in improper regulator operation. | Replacement of Meco Reg & Becker Pilots | Transmission | Near Hit | No | No
Near Hit | 7023105 | JAV_PT0001 | Mission | 2016-01-29 04:57 | 331.1 | 336 | -4.9 | -1.458% | Failure - Equipment | EQ |  | Brief power loss to the regulator required the monitor to take control. | • Crew responded and discovered power outage at Irvington Station • Crew identified that the monitors took control during the power lost and regulating below the MOP limits • Crew continued to monitor the station • Power has been restored at Irvington Station | Transmission | Near Hit | No | No
Near Hit | 7023500 | SJ_SJS_RG53 | San Jose | 2016-02-03 01:36 | 59.03 | 60 | -0.97 | -1.617% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023501 | SF_SF_S037 | San Francisco | 2016-02-05 15:37 | 10.5 | 12 | -1.5 | -12.5% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7023502 | SO_UKI_S024 | Sonoma | 2016-02-07 14:32 | 23 | 25 | -2 | -8% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7023503 | SJ_SJS_RG53 | San Jose | 2016-02-07 23:38 | 59.06 | 60 | -0.94 | -1.567% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023504 | SF_SF_S037 | San Francisco | 2016-02-07 23:55 | 10.51 | 12 | -1.49 | -12.42% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7023554 | DI_DNV_SO33 | DIablo | 2016-02-08 13:54 | 58 | 60 | -2 | -3.333% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023555 | ST_STK_RR32_PT3 | Stockton | 2016-02-08 23:31 | 11.13 | 12 | -0.87 | -7.25% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7023556 | SF_SF_S012 | San Francisco | 2016-02-09 01:48 | 7.98 | 9.2 | -1.22 | -13.26% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7023557 | ST_STK_S018 | Stockton | 2016-02-09 00:25 | 10.36 | 12 | -1.64 | -13.67% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7023558 | PN_PFA_S016 | Peninsula | 2016-02-09 01:18 | 47.03 | 50 | -2.97 | -5.94% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023559 | SA_ELK_SO64 | Sacramento | 2016-02-09 14:25 | 58 | 60 | -2 | -3.333% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023610 | SF_SF_S012 | San Francisco | 2016-02-10 01:48 | 7.98 | 9.2 | -1.22 | -13.26% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7023761 | SA_ELK_SO64 | Sacramento | 2016-02-11 15:11 | 58 | 60 | -2 | -3.333% | SP Too Close to MOP/HiHi |  |  |  | GDCC contacted local I&R | HP Distribution | Near Hit | Yes | No
Near Hit | 7023869 | ST_STK_RR32_PT3 | Stockton | 2016-02-14 23:12 | 11.12 | 12 | -0.88 | -7.333% | Low Demand |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7023930 | DI_MTZ_S031_PT1 | Diablo | 2016-02-15 00:04 | 58 | 60 | -2 | -3.333% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023931 | DI_OKL_S004 | Diablo | 2016-02-15 01:01 | 57 | 60 | -3 | -5% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023932 | DI_OKL_S015 | Diablo | 2016-02-15 01:21 | 57.04 | 60 | -2.96 | -4.933% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023933 | DI_MTZ_S031_PT1 | Diablo | 2016-02-15 23:41 | 58.1 | 60 | -1.9 | -3.167% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023934 | DI_DNV_RW13_PT3 | Diablo | 2016-02-16 00:24 | 59 | 60 | -1 | -1.667% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023935 | SF_SF_S012 | San Francisco | 2016-02-16 01:00 | 8.1 | 9.2 | -1.1 | -11.96% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7023936 | EB_RCH_S012 | East Bay | 2016-02-16 01:06 | 48.1 | 50 | -1.9 | -3.8% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023899 | DI_DNV_RW13 | Diablo | 2016-02-17 23:59 | 59.13 | 60 | -0.87 | -1.45% | Low Demand |  |  |  | GCSS notified control room about alarm consistency, and to provide caution to the field. CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023970 | DI_MTZ_S031 | Diablo | 2016-02-17 00:09 | 58.21 | 60 | -1.79 | -2.983% | Low Demand |  |  |  | GCSS notified control room about alarm consistency, and to provide caution to the field. CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7023972 | SF_SF_S012 | San Francisco | 2016-02-17 00:52 | 8 | 9.2 | -1.2 | -13.04% | Low Demand |  |  |  | GCSS notified control room about alarm consistency, and to provide caution to the field. CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7023973 | EB_RCH_S012 | East Bay | 2016-02-17 02:33 | 48.1 | 50 | -1.9 | -3.8% | Low Demand |  |  |  | GCSS notified control room about alarm consistency, and to provide caution to the field. CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7024458 | SO_HLB_RR52_PT2 | Sonoma | 2016-02-26 23:20 | 165 | 720 | -555 | -77.08% | SP Too Close to MOP/HiHi |  |  |  | Tech adjusted intermediate reg set point from ~164 psig to 155 psig | HP Distribution | Near Hit | No | No
Near Hit | 7024459 | YO_DEL_S029 | Yosemite | 2016-02-26 00:01 | 51.5 | 60 | -8.5 | -14.17% | SP Too Close to MOP/HiHi |  |  |  |  | HP Distribution | Near Hit | Yes | No
Near Hit | 7024480 | SF_SF_S012 | San Francisco | 2016-02-26 01:07 | 8 | 9.2 | -1.2 | -13.04% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7024481 | KE_BKD_S004 | Kern | 2016-02-26 02:17 | 10.5 | 12 | -1.5 | -12.5% | SP Too Close to MOP/HiHi |  |  |  |  | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00151
Near Hit | 7024552 | SA_CHT_S059 | Sacramento | 2016-02-27 00:05 | 58 | 60 | -2 | -3.333% | SP Too Close to MOP/HiHi |  |  |  | Regulator set point was adjusted | HP Distribution | Near Hit | Yes | No
Near Hit | 7024672 | SA_CHT_S059 | Sacramento | 2016-02-29 12:59 | 58 | 60 | -2 | -3.333% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7024671 | SF_SF_S012 | San Francisco | 2016-03-01 01:50 | 8 | 9.2 | -1.2 | -13.04% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7024719 | SA_CHT_S059 | Sacramento | 2016-03-01 12:58 | 58 | 60 | -2 | -3.333% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7024740 | SI_ELD_S011 | Sierra | 2016-03-02 00:13 | 58.01 | 60 | -1.99 | -3.317% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7024741 | SF_SF_S012 | San Francisco | 2016-03-02 02:37 | 8 | 9.2 | -1.2 | -13.04% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7024811 | SA_CHT_S059 | Sacramento | 2016-03-03 12:58 | 58 | 60 | -2 | -3.333% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7024928 | SJ_SJS_RG53 | San Jose | 2016-03-04 05:00 | 59.03 | 60 | -0.97 | -1.617% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7025862 | SSD_PT0003 | Sacramento | 2016-03-05 01:47 | 693.8 | 700 | -6.2 | -0.8857% | Design Issue - Other |  |  |  | Tech disassembled the regulator and replaced all rubber goods. After the inspection, the regulator was returned to operation and no further lock up issues were observed. | Transmission | Near Hit | No | No
Near Hit | 7024992 | ST_STK_RR46_PT3 | Stockton | 2016-03-06 13:19 | 11.1 | 12 | -0.9 | -7.5% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7024995 | ST_STK_RR13_PT3 | Stockton | 2016-03-06 13:19 | 11.03 | 12 | -0.97 | -8.083% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00208
Near Hit | 7024994 | ST_STK_RR46_PT3 | Stockton | 2016-03-07 13:19 | 11.1 | 12 | -0.9 | -7.5% | SP Too Close to MOP/HiHi |  |  |  | Bsaed on the frequency of nearhits in the area it has been deemed necessary to perform a B-inspection at this site. Consider replacing regulator for longer term solution. | LP Distribution | Near Hit | No | No
Near Hit | 7024996 | ST_STK_RR13_PT3 | Stockton | 2016-03-07 13:19 | 11.03 | 12 | -0.97 | -8.083% | SP Too Close to MOP/HiHi |  |  |  | Bsaed on the frequency of nearhits in the area it has been deemed necessary to perform a B-inspection at this site. Consider replacing regulator for longer term solution. | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00208
Near Hit | 7025654 | MSH_PT0003 | Mission | 2016-03-08 04:30 | 579.8 | 583 | -3.2 | -0.5489% | Gas Contaminants - Moisture |  |  |  | We found that the gas rack for V-3 is icing up due to cold weather condition which may have produce un-reliable control signal gas to V-3 positioner causing operational issues. We just warm up and remove the icing on the gas rack and since V-3 is not accessible by that time due to station upgrade construction, we just wait until the sun warm it up. And true enough, V-3 started to work properly on its own without us doing anything on it. So we come up with the conclusion that the cold weather and gas rack icing up is the cause of the problem. | Transmission | Near Hit | No | No
Near Hit | 7026451 | ALM_PT1004 | Diablo | 2016-03-11 14:46 | 401.36 | 405 | -3.64 | -0.8988% | Design Issue - Other |  |  |  | The high back pressure on the branch line will trip V1 at the inter connect, which requires a local reset. | Transmission | Near Hit | No | No
Near Hit | 7025934 | HU_FTA_S006 | Humboldt | 2016-03-18 00:10 | 44 | 45 | -1 | -2.222% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7025936 | YO_ATW_RA20 | Yosemite | 2016-03-18 01:23 | 42.1 | 43 | -0.9 | -2.093% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7025935 | YO_ATW_RA13 | Yosemite | 2016-03-18 01:28 | 42.1 | 43 | -0.9 | -2.093% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7025937 | YO_ATW_RA20 | Yosemite | 2016-03-21 01:23 | 42.6 | 43 | -0.4 | -0.9302% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7025938 | YO_ATW_RA13 | Yosemite | 2016-03-21 01:28 | 42.6 | 43 | -0.4 | -0.9302% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7025939 | YO_ATW_S018 | Yosemite | 2016-03-21 01:35 | 42.4 | 45 | -2.6 | -5.778% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7025946 | KT2_PT0_10U | Kern | 2016-03-23 08:15 | 663.6 | 700 | -36.4 | -5.2% | Clearance Execution | HU |  |  | In order to alleviate pressure at this location V-0.10A was throttled to reduce pressure. | Transmission | Near Hit | No | Yes
Near Hit | 7026117 | SSD_PT0003 | Sacramento | 2016-03-24 01:34 | 691.3 | 700 | -8.7 | -1.243% | Failure - Equipment | EQ |  |  | The tech switched to the secondary run to diagnose potential issues with the primary run. | Transmission | Near Hit | No | No
Near Hit | 7026272 | FR_FRE_RL08_PT3 | Fresno | 2016-03-26 07:51 | 11.1 | 12 | -0.9 | -7.5% | Failure - Equipment | EQ |  |  | Immediate notification to the field. | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00154
Near Hit | 7026779 | KE_TAF_S016 | Kern | 2016-04-02 15:27 | 41.1 | 42 | -0.9 | -2.143% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7027378 | SO_COT_R378 | Sonoma | 2016-04-07 01:31 | 49.02 | 50 | -0.98 | -1.96% | Low Demand |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7027136 | FHE_PT0001 | Yosemite | 2016-04-06 16:47 | 403.9 | 500 | -96.1 | -19.22% | Failure - Equipment | EQ |  | During the emergency clearance (80022903) to reduce pressure in L-134A, pressure equalized across a regulator valve V-2 into dead-end station piping. | • Further investigate the emergency clearance 80022903 and how the decision was made to draft into L-118A via V-2 instead of opening a blow down valve to vent gas. • Update Herndon Junction operating diagram – MOP/MAOP delineation & valve position of V-3 to reflect normal operation condition • Evaluate FHE_PT0001 alarm setting – potentially move MOP alarm up or off the PT to eliminate false (Suggestion) | Transmission | Near Hit | No | No
OP | 7027290 7027522 | SSW_PT0007 | Sacramento | 2016-04-07 11:53 | 562 | 520 | 42 | 8.077% | Clearance Execution | HU | P50.2 | Crew failed to secure valve positions during a clearance upon discovering a leak; depressurizing of the sense line caused the monitor valve to swing open. | • Crew manually closed V-53 after they noticed that the V-53 was inadvertently opened. • A 20% pressure reduction was issue on L-172A from Swingle Junction to Sacramento Gas Load Center • Leak survey was performed on L-172A between Swingle Junction and Sacramento Gas Load Center. No leaks were found along L-172A. • Integrity Management conducted an “Engineering Critical Analysis (ECA)” to further analyze other essential actions. No immediate actions are required per ECA finding. • PFLs were reviewed, and all features that were affected by the OP event are rated for at least 520 psig. | Transmission | Large OP Event | No | No | No | Yes |  | H-19 | GT.STAT.COMP.MCDONLDISL |  | 467 | 480
Near Hit | 7028288 | NV_ORO_S041 | North Valley | 2016-04-26 02:31 | 11 | 12 | -1 | -8.333% | Failure - Equipment | EQ |  |  | CTT- closed to trend | LP Distribution | Near Hit | No | No
Near Hit | 7028289 | KE_RGC_R522_PT3 | Kern | 2016-04-27 03:07 | 52.03 | 55 | -2.97 | -5.4% | Failure - Equipment | EQ |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7028177 | FT2_PT0002 | Stockton | 2016-04-27 09:17 | 325 | 326 | -1 | -0.3067% | Low Demand |  |  |  | • Crew bleed down L-148 at Whitmore Station by increasing the regulation set point from 235 psig to 240 psig • When L-148 was returned to 310 psig NOP, Whitmore regulation was returned to 235 psig • All regulators set points were checked by the crew and no reports of lock up issues (Set points mentioned above) | Transmission | Near Hit | No | No
Near Hit | 7028757 | SRB_PT0002 | North Valley | 2016-04-18 05:06 | 464 | 470 | -6 | -1.277% | Low Demand |  |  |  | GTCC contacted local I&R supervisor and when a crew was dispatched out the pressure had already subsided below the HIHI & HI alarm limits. No issues were reported by field crew. | Transmission | Near Hit | No | No
Near Hit | 7028790 | SMS_PT0005 | Sacramento | 2016-04-19 12:48 | 85 | 95 | -10 | -10.53% | Failure - Equipment | EQ |  |  | • GTCC contacted the local I&R Supervisor, and Supervisor dispatched a crew • Crew identified that the 1st stage cut failed and monitor was in control • Crew replace the 1st stage pilot diaphragm and test the pilot before returning it to normal operation | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.LVCR.0000000523 |  | LVC
Near Hit | 7029724 | CC_WAT_S006_PT1 | Central Coast | 2016-05-19 00:51 | 46.24 | 50 | -3.76 | -7.52% | Low Demand |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7030392 | SO_RNP_S004 | Sonoma | 2016-05-28 01:15 | 49.01 | 50 | -0.99 | -1.98% | Low Demand |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7030450 | ALM_PT1004 | Diablo | 2016-05-26 04:13 | 428.5 | 590 | -161.5 | -27.37% | Design Issue - Other |  |  |  | Immediate Action – GTCC contacted the local I&R regarding the HIHI alarm at Los Medanos PLS. | Transmission | Near Hit | No | No
Near Hit | 7031558 | FMW_PT0001 | Stockton | 2016-05-27 08:32 | 320.2 | 326 | -5.8 | -1.779% | Low Demand |  |  |  | Tech was dispatched to Whitmore Station and bleed down the pressure of 319 psig down to 230 psig. Regulators were also checked for lock up and no reported issues found by the Tech. | Transmission | Near Hit | No | No
Near Hit | 7031115 | SO_RNP_S004 | Sonoma | 2016-06-02 01:00 | 49.01 | 50 | -0.99 | -1.98% | Low Demand |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
OP | 7030546 | Gauge | Yosemite | 2016-06-02 13:00 | 67 | 60 | 7 | 11.67% | Maintenance Operations Quality | HU | P50.2 | Mainline filter was not installed correctly. Contaminants were discovered in regulator equipment during customer shut-in. | • Tech also inspected the monitor and regulator – no issues were found on the monitor but metal shavings were found on the regulator rubber seat • The regulator was cleaned of debris and lock up tests were done on both regulations – no reported lock up issues • The main filter was also inspected and found that the filter cartridge was not fully set • The filter was reinstalled by the Tech • A leak survey was done and no leaks were found during the survey | HP Distribution | Large OP Event | No | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000105 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Mer\Tif\Gas\REGSTATION\0805204.PDF | 45 | 55
OP | 7030585 | SHS_PT0008 | Sacramento | 2016-06-05 05:19 | 807 | 800 | 7 | 0.875% | Gas Control Center Operations | HU |  | Gas Control Operator did not fully assess risk before creating an atypical operating configuration to address a pressure issue. | Control Room G | Transmission | Small OP Event | No | No | No | ACE |  |  | GT.STAT.MISC.HERJCTPLS_ |  | 730 | 750
Near Hit | 7031116 | KE_BKD_S004 | Kern | 2016-06-15 01:34 | 10.52 | 12 | -1.48 | -12.33% | Low Demand |  |  |  | CTT- closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00151
Near Hit | 7031211 | KE_BKD_S004 | Kern | 2016-06-16 01:03 | 10.5 | 12 | -1.5 | -12.5% | Low Demand |  |  |  | CTT- closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00151
Near Hit | 7031442 | KE_BKD_S004 | Kern | 2016-06-18 02:49 | 10.51 | 12 | -1.49 | -12.42% | Low Demand |  |  |  | CTT- closed to trend | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00151
Near Hit | 7031443 | SO_RNP_S004 | Sonoma | 2016-06-21 00:23 | 49 | 50 | -1 | -2% | SP Too Close to MOP/HiHi |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7031444 | SO_PET_S022 | Sonoma | 2016-06-21 00:23 | 48 | 50 | -2 | -4% | SP Too Close to MOP/HiHi |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7031554 | SO_PET_S022 | Sonoma | 2016-06-22 23:40 | 48.17 | 50 | -1.83 | -3.66% | Low Demand |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7031555 | SI_ROC_R406 | Sierra | 2016-06-22 02:04 | 59.1 | 60 | -0.9 | -1.5% | Low Demand |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
OP | 7031602 | JDL_PT0002 | Hollister District | 2016-06-23 11:35 | 465.9 | 408 | 57.9 | 14.19% | Clearance Preparation | HU | P50.2 | Regulated into blocked-in section of piping returning equipment to service at end of clearance. Written clearance had a poor sequence of operations for this activity. | Leak survey, ECA, OP Stand-down, OP Refresher Training, etc. | Transmission | Large OP Event | No | No | No | Yes |  | H-19 | GT.STAT.MISC.DOLNRDPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\083812.pdf | 395 | x
Near Hit | 7031484 | SO_PET_S022 | Sonoma | 2016-06-24 01:38 | 48.17 | 50 | -1.83 | -3.66% | Low Demand |  |  |  | Repeating alarm, will notify the control room per email process CTT- closed to trend | HP Distribution | Near Hit | Yes | No
Near Hit | 7031733 | YO_CHW_S021 | Yosemite | 2016-06-27 01:03 | 42.16 | 43 | -0.84 | -1.953% | Low Demand |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | Yes | No
OP | 7031764 | Gauge | Fresno | 2016-06-27 09:24 | 238 | 60 | 178 | 296.7% | Failure - Equipment | EQ | P95.8 | Leaking bypass valve on HPR set with relief valve that did not relieve due to wrong spring installed. Also, HPR was not in GT-GIS. | • Crew shut in the inlet fire valve and vented pressure from the over pressurized service line • New HPR and service line are to be installed at 970 East Floral Avenue | HP Distribution | Large OP Event | No | No | No | Yes |  | H-10 | GD.STAT.FTAP.05194 |  | 45 | 180
Near Hit | 7032550 | SO_UKI_S024 | Sonoma | 2016-07-11 20:52 | 23.11 | 25 | -1.89 | -7.56% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7032551 | SO_UKI_S024 | Sonoma | 2016-07-12 20:59 | 23.11 | 25 | -1.89 | -7.56% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7032702 | SO_UKI_S024 | Sonoma | 2016-07-13 21:41 | 23.11 | 25 | -1.89 | -7.56% | SP Too Close to MOP/HiHi |  |  |  | CTT - closed to trend | HP Distribution | Near Hit | No | No
OP | 7032831 7032778 | Gauge | Yosemite | 2016-07-16 18:18 | 370 | 60 | 310 | 516.7% | Failure - Equipment | EQ | P99.1 | Regulator boot failed. Oversized equipment that was in service for an extensive period without a full inspection. Obsolete monitor common sense and bleed. TD-4540S does not specify timeframe to perform "B" inspection from the 2014 update. |  | HP Distribution | Large OP Event | No | No | No | Yes |  | H-10 | GT.STAT.LVCR.0000000121 |  | 40 | 45
Near Hit | 7033279 | SO_HBL_S014 | Sonoma | 2016-07-27 01:15 | 48.06 | 50 | -1.94 | -3.88% | Low Demand |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7033416 | SO_SON_S006 | Sonoma | 2016-07-29 01:18 | 40.04 | 42 | -1.96 | -4.667% | Low Demand |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7033590 | DI_OKL_S004 | Diablo | 2016-07-31 02:33 | 57 | 58 | -1 | -1.724% | Low Demand |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7033591 | FR_KMN_S011 | Fresno | 2016-07-31 02:33 | 52 | 53 | -1 | -1.887% | Low Demand |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
Near Hit | 7033719 | MMT_PT0084 | Milpitas District | 2016-08-03 06:50 | 392 | 400 | -8 | -2% | Clearance Execution | HU |  | Clearance steps delivered and executed concurrently rather than sequentially (steps 20 before step 21), station did not have gauges US/DS of MAOP break during preparation for the 3rd pig run of L-100 at Milpitas (identical clearance used on first two runs). | Stand-down for pigging L-100 and all TPCO employees (8/4/2016 0815) Roundtable for clearance writers and supervisors related to OP events (RBQ2) | Transmission | Near Hit | No | No
Near Hit | 7033982 | DI_OKL_S004 | Diablo | 2016-08-07 02:30 | 57 | 58 | -1 | -1.724% | SP Too Close to MOP/HiHi |  |  |  | CTT- closed to trend | HP Distribution | Near Hit | No | No
OP | 7034290 7034273 | Gauge | Fresno | 2016-08-10 15:00 | 84 | 60 | 24 | 40% | Gas Contaminants - Debris | EQ | P50.7 | Regulator failed to lock up due to equipment contaminants and poor maintenance. Also, vintage relief valve was set above the MAOP limit. | • The original HPR was removed and shipped for further testing by CTL • The HPR was rebuilt and new HPR (Fisher 627 with ¼” orifice) and relief valve (Fisher H202) were installed by the Tech • Two existing system wide CAP notifications for HPR - 7025880 and 7025881 (ongoing) | HP Distribution | Large OP Event | No | No | No | Yes |  | H-10 | #N/A |  | 55 | 135
OP | 7034115 | FRI_PT0005 | Stockton | 2016-08-09 16:55 | 428.2 | 408 | 20.2 | 4.951% | Clearance Execution | HU |  | The operation of manually throttling an inlet valve resulted in the valve swinging open which caused a rapid increase of pressure downstream. |  | Transmission | Small OP Event | Yes | No | No | ACE |  |  | GT.STAT.MISC.RIPONMDSTO |  | x | x
Near Hit | 7035454 | OCW_PT0001 | East Bay | 2016-08-17 19:45 | 140.9 | 246 | -105.1 | -42.72% | Failure - Equipment | EQ |  |  |  | Transmission | Near Hit | No | No
OP | 7035005 7035057 | SSA_PT0009 | Sacramento | 2016-08-24 17:45 | 269 | 260 | 9 | 3.462% | Clearance Execution | HU |  | During the emergency portion of the clearance to reduce set points for an increasing in pressure, the technician did not follow best practices or the standard to adjust set point pressure. |  | Transmission | Small OP Event | Yes | No | No | ACE |  |  | GT.STAT.MISC.SACGASLDCR | \\fairfield07\gis\giswebMiscFiles\GasStations\385186.pdf | 240 | 265
Near Hit | 7035421 7035338 | BRT_PT0066D | Diablo | 2016-08-30 14:25 | 423 | 867 | -444 | -51.21% | Maintenance Operations Quality | HU |  |  | • V-64 (the RCV) was opened with caution and D/S pressure stabilized below 300 psig • GTCC SCADA reading and field gauge reading were validated – no issues reported • Facility Engineer was contacted and determined that the pipe line was rated for 867 psig (Excursion within the station) • Per Facility Engineer, no further actions were required • Lesson learned to lower the regulation set point U/S of the maintenance work so that pressure spikes are not experienced when valve are close or operated D/S of the regulation. | Transmission | Near Hit | No | No
Near Hit | 7035428 | SF_SF_S046 | San Francisco | 2016-09-01 01:15 | 8.08 | 9.2 | -1.12 | -12.17% | Low Demand |  |  |  |  | HP Distribution | Near Hit | No | No
Near Hit | 7036066 | FFN_PT0013 | Fresno | 2016-09-13 09:47 | 619.7 | 650 | -30.3 | -4.662% | Maintenance Operations Quality | HU |  |  | Pressure stabilize a minute after the MOP alarm activated | Transmission | Near Hit | No | No
Near Hit | 7035996 | BRT_PT0131S | Diablo | 2016-09-17 14:05 | 377 | 500 | -123 | -24.6% | Gas Control Center Operations | HU |  |  | Pressure stabilize a minute after the MOP alarm activated | Transmission | Near Hit | No | No
Near Hit | 7036611 | FPN_PT0001 | Kern | 2016-09-18 20:14 | 255.32 | 238 | 17.32 | 7.277% | Failure - Equipment | EQ |  |  | • GTCC received a MOP/HIHI alarm at Pioneer Station inlet pressure • Technician was dispatched out to Pioneer Station • Technician went to Bakersfield Reg Station (the inlet source) and gauged D/S of regulation. Field reading was at 210 psig. • A D/S SCADA point at Bakersfield Reg Station was at 211 psig far below the 238 psig MOP limit. • Pioneer Station existing inlet pressure transmitter was replaced with new Rosemount 3051 pressure transmitter | Transmission | Near Hit | No | No
Near Hit | 7036825 | SF_SF_S023 | San Francisco | 2016-09-24 01:53 | 8 | 9.2 | -1.2 | -13.04% | Communication |  |  |  | Adjusted HIHI alarm to better align with other ERXs in the HIS | HP Distribution | Near Hit | No | No
OP | 7037295 | SA_GAL_RB07 | Sacramento | 2016-10-06 19:04 | 62.37 | 60 | 2.37 | 3.95% | Gas Contaminants - Debris | EQ |  | Debris was discovered in the pilot cartridge during an alarm activation response. Earlier that day a ‘B’ inspection was performed by another crew with no reported issues. | • Technician was dispatched to the reg station • Both the regulator and monitor were rebuilt, rechecked for lock up, and pressure stabilized below MAOP limit • Left run was set as the lead run with monitor at 58 psig and regulator at 54 psig • Post OP event, both runs were bore scoped by the Non Destructive Examination group. There were no sign of loose debris between the filters and regulators on both runs. | HP Distribution | Small OP Event | Yes | No | No | ACE |  | H-14 | GD.STAT.DIST.01048 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Sac\Tif\Gas\RegStation\0804213.PDF | 54 | 58
OP | 7037549 | SNH_PT0025 | Sacramento | 2016-10-14 09:40 | 239 | 180 | 59 | 32.78% | Design Issue | HU | P95.9 | When a pipe section was blown down in preparation for valve replacement this resulted in the regulator valve (V-139) losing power gas, and swinging open which caused a rapid increase of pressure and overpressure event on DFM 0614-04. | TDB | Transmission | Large OP Event | No | Yes | No | Yes |  | H-14 | GT.STAT.MISC.NSACHOLDER |  | x | x
Near Hit | 7037617 | MMT_PT0088 | San Jose | 2016-10-10 | 553 | 558 | -5 | -0.8961% | Failure - Equipment | EQ |  | MLV-490.65A was an isolation point (closed) and V-3 was operated in order to regulate the inlet pressure form L-300A. GTCC noticed an increase of pressure D/S of MLV and decrease in U/S pressure. As a result V-3 comanded to close. After the change, V-3 remained open and D/S pressure continued to increase and until it triggered the HIHI alarm. | GTCC stabilized the pressure by controlling U/S of PLS #7 and changing the regulation set point at Milpitas Terminal located D/S of PLS #7. I&R Tech was dispatched to PLS # 7 and the V-3 was manually closed and further inspected. | Transmission | Near Hit | No | Yes
Near Hit | 7037798 | SO_UKI_S020 | Sonoma | 2016-10-21 00:39 | 24 | 25 | -1 | -4% | SP Too Close to MOP/HiHi |  |  |  | • GDCC contacted the on-call supervisor • On-call dispatched an I&R Technician to further investigate • I&R Technician checked associated District Reg Stations and noticed a drift in set points. The regulatiion set points were adjusted by the Technician to about 23 psig. | HP Distribution | Near Hit | No | Yes
OP | 7038541 | Chart Recorder | Yosemite | 2016-10-30 | 67 | 60 | 7 | 11.67% | Failure - Equipment | EQ | P50.7 | Equipment failed to protect to downstream system after the customer went on a hot shutoff (rapid load change) - and the load dropped off almost instantaneously. | Planning engineer discussed 4 options: reduce dreg set point, redesign meter set, replace piping from reg to customer, and install relief vavle | HP Distribution | Large OP Event | Yes | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000218 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Mer\Tif\Gas\REGSTATION\0805090.PDF | 50 | 55
Near Hit | 7038458 | ALM_PT1703 | Diablo | 2016-11-01 | 437 | 468 | -31 | -6.624% | Failure - Equipment | EQ |  |  |  | Transmission | Near Hit | No | No
OP | 7038547 | Gauge | Mission | 2016-11-03 15:30 | 66 | 55 | 11 | 20% | Clearance Execution | HU | P50.7 | GC M&C Crew failed to follow special instructions and call for I&R support prior to pinching the 3" plastic main adjacent to a distribution regulator station. |  | HP Distribution | Large OP Event | Yes | No | No | Yes |  | H-14 | GD.STAT.DIST.11157 | file://utility.pge.com/projects/metcat/metcatprd-fs01/comp_pub/Hay/Tif/Gas/RegStation/0804644.PDF | 49 | 53
OP | 7039284 | SYC_PT0012 | Sacramento | 2016-11-22 10:34 | 494 | 485 | 9 | 1.856% | Clearance Execution | HU |  | While performing the maintenance in accordance with the clearance, the crew omitted to gauge pressure on isolated section of line where valves were known to leak. |  | Transmission | Small OP Event | No | Yes | No | ACE |  |  | GT.STAT.MISC.YUBACITYUH |  | 470 | 480
Near Hit | 7039509 | BBC_PT0002 | Stockton | 2016-11-02 04:26 | 1034 | 1040 | -6 | -0.5769% | High Demand |  |  |  | Immediate action - GTCC operator acknowledge the alarm, and the compressor unit at the station was shut in | Transmission | Near Hit | No | No
Near Hit | 7039630 | ALM_PT0004 | Diablo | 2016-11-22 22:00 | 427 | 590 | -163 | -27.63% | Design Issue - Other |  |  |  | Immediate Actions: • GTCC acknowledge the HIHI alarm activation • GTCC operator contacted the local on-call GPOM supervisor • After the call was made to local GPOM, pressure stabilized below the 426 psig HIHI alarm limit • GTCC continued to monitor the pressure U/S and D/S of the V-716 | Transmission | Near Hit | No | No
OP | 7039714 | BBC_PT0004 | Diablo | 2016-12-06 20:18 | 63 | 60 | 3 | 5% | Gas Contaminants - Debris | EQ |  | During an MAOP excursion call out, Technician discovered weld slag on the regulator diaphragm and heavy external ice formation on reg pilot's vent hole | • Crew responded to the MOP excursion and stabilized the D/S pressure down to NOP • The secondary/lag run was placed in control and the primary/working run was further inspected for cause • Addition, inspections are scheduled in the couple days e.g. bore scope | HP Distribution | Small OP Event | No | No | No | ACE |  | H-14 | GD.STAT.DIST.00160 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Cnd\Tif\Gas\RegStation\0806264.PDF | 56 | 58
Near Hit | 7040115 | JTL_PT0004 | San Jose | 2016-12-16 11:50 | 552 | 600 | -48 | -8% | Clearance Preparation | HU |  |  |  | Transmission | Near Hit | No | No
Near Hit | 7040206 | BRT_PT16_71U | Diablo | 2016-12-19 13:15 | 462 | 595 | -133 | -22.35% | Maintenance Operations Quality | HU |  |  |  | Transmission | Near Hit | No | Yes
OP | 7040178 | Gauge | Yosemite | 2016-12-20 06:03 | 264 | 125 | 139 | 111.2% | Clearance Preparation | HU | P50.7 | The clearance to hydrotest upstream inadvertently introduced contaminants into the regulation of the downstream system because steps were written in a manner which blew known downstream contaminants upstream. |  | Transmission | Large OP Event | No | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000125 |  | 115 | 125
Near Hit | 7040490 | SSW_PT0007 | Sacramento | 2016-12-25 22:47 | 499 | 500 | -1 | -0.2% | Failure - Equipment | EQ |  |  |  | Transmission | Near Hit | No | No
Near Hit | 7040358 | BRT_PT0057A | Sacramento | 2016-12-26 17:44 | 634 | 722 | -88 | -12.19% | Failure - Equipment | EQ |  |  | • 17:43 Hours GTCC contacted the local supervisor to further investigate the HIHI/MOP alarm activations at Brentwood Terminal. Supervisor immediately worked on dispatching a GPOM Technician. • 19:30 Hours GPOM Technician arrived at Brentwood Terminal and requested for operation of V-175 in order to bleed down the pressure. Valve operation was granted, and V-175 was opened to relieve pressure upstream pressure. | Transmission | Near Hit | No | No
Near Hit | 7040492 | BBC_PT0015 | Stockton | 2016-12-28 06:13 | 771 | 777 | -6 | -0.7722% | Failure - Equipment | EQ |  |  |  | Transmission | Near Hit | No | No
Near Hit | 7040560 | KAM_PT0001 | Stockton | 2016-12-28 17:17 | 492.4 | 498 | -5.6 | -1.124% | Low Demand |  |  |  | Crew responded and inspected the regulators , and no sign of lock up issues were reported by the crew. | Transmission | Near Hit | No | No
Near Hit | 7040560 | KAM_PT0001 | Stockton | 2016-12-29 17:17 | 491.1 | 498 | -6.9 | -1.386% | Low Demand |  |  |  | Crew responded and inspected the regulators , and no sign of lock up issues were reported by the crew. | Transmission | Near Hit | No | No
Near Hit | 7041724 | ABH_PT0001 | Diablo | 2017-01-03 | 461.1 | 468 | -6.9 | -1.474% | Failure - Equipment | EQ |  |  | GTCC received a HIHI alarm at Brentwood Dehydrator (inlet pressure SCADA point) . It was determined a regulator located at Brentwood Terminal (U/S of Brentwood Dehydrator) had failed open. After further investigation, technician discovered mositure on V-127 controller cabinet contributed to the electrical glitch. | Transmission | Near Hit | No | No
Near Hit | 7041158 | SO_SON_S006 | Sonoma | 2017-01-03 23:49 | 40.22 | 42 | -1.78 | -4.238% | Low Demand |  |  |  | GDCC contacted the on-call and continued to monitor per GPOM request | HP Distribution | Near Hit | No | No
Near Hit | 7041158 | SO_UKI_S020 | Sonoma | 2017-01-03 23:57 | 23.99 | 25 | -1.01 | -4.04% | Low Demand |  |  |  | GDCC contacted the on-call and continued to monitor per GPOM request | HP Distribution | Near Hit | No | No
Near Hit | 7041158 | SO_SRO_R121_PT3 | Sonoma | 2017-01-04 01:21 | 59 | 60 | -1 | -1.667% | Low Demand |  |  |  | GDCC contacted the on-call and continued to monitor per GPOM request | HP Distribution | Near Hit | No | No
Near Hit | 7041133 | PN_SM_RA61_PT3 | Peninsula | 2017-01-04 | 33.08 | 34 | -0.92 | -2.706% | SP Too Close to MOP/HiHi |  |  |  | Technician went out to the reg station and lowered the reg set point to ~ 31 psig | HP Distribution | Near Hit | Yes | No
Near Hit | 112879627 | PN_SM_RA61_PT3 | Peninsula | 2017-01-07 | 33.2 | 34 | -0.8 | -2.353% | Low Demand |  |  |  | Tech lowered set point | HP Distribution | Near Hit | Yes | No
Near Hit | 112872755 | SO_SON_S006_PT1 | Sonoma | 2017-01-08 | 40.1 | 42 | -1.9 | -4.524% | Low Demand |  |  |  | Boot replaced under clearance 80035502 | HP Distribution | Near Hit | Yes | No
Near Hit | 112879623 | SJ_GIL_RH83_PT3 | San Jose | 2017-01-08 | 54.1 | 55 | -0.9 | -1.636% | Low Demand |  |  |  | Tech lowered set point | HP Distribution | Near Hit | Yes | No
Near Hit | 7041664 | MMT_PT3838A | Milpitas District | 2017-01-20 09:05 | 495 | 300 | 195 | 65% | Clearance Execution | HU |  |  | • The clearance was postponed for the other monitors within Milpitas Terminal. • Additional review and possible revision to the original maintenance clearance is to be considered. | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.MISC.MLPTSTPLM_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\383510.pdf
Near Hit | 7041668 | ALM_PT0004 | Diablo | 2017-01-21 20:03 | 426.7 | 590 | -163.3 | -27.68% | Design Issue - Other |  |  |  | Minutes after the HIHI, BTU level from Ryer Island increased and V-716 reopened and mitigated from further buildup of pressure | Transmission | Near Hit | No | No
OP | 7041620 | SA_FOL_RA04 | Sacramento | 2017-01-25 | 114.7 | 60 | 54.7 | 91.17% | Gas Contaminants - Debris | EQ | P95.9 | Contaminants caused failure of station regulation and monitoring equipment contributed by the ILI last year. | • Concord Test Lab conducted inspection on the shut-in regulator station and found heavy black sand like material. • Leak survey was conducted and several grade 1 leaks (~9 leaks) were identified and fixed by crew | HP Distribution | Large OP Event | No | No | No | Yes |  | H-14 | GD.STAT.DIST.01039 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Sac\Tif\Gas\RegStation\0804246.PDF | 54 | 58
Near Hit | 7041680 7041636 | ASQ_PT0001B | North Valley | 2017-01-26 18:09 | 909.7 | 911 | -1.3 | -0.1427% | Gas Control Center Operations | HU |  | Shift change and multiple operations of the same compressor without clear communication resulted in the compressor tripping multiple times, and the hihi alarm. | • Technician gauged the line and determined that SCADA was not calibrated to line pressure (about 1.0 psig above actual pressure) • Tailboard/Training will be delivered to avoid operation adjustment during shift changes and engage the senior before making the changes | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.COMP.BURNEY____ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284542.pdf
Near Hit | 112873051 | YO_OKD_EX01_PT1 | Yosemite | 2017-01-31 | 11.02 | 12 | -0.98 | -8.167% | Low Demand |  |  |  | Set point lowered on regulator | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00190
Near Hit | 7042258 | ALM_PT0004 | Diablo | 2017-02-01 14:09 | 433.4 | 590 | -156.6 | -26.54% | Design Issue - Other |  |  |  | After the HIHI alarm activation, the BTU leve from Ryer Island increased, and V-716 reopened and mitigated further buildup of pressure. GTCC continued to monitor the pressure at Los Medanos PLS. Technicians from PG&E & Ryer Production were also dispatched to the site, no reported issues. | Transmission | Near Hit | No | No
Near Hit | 112583543 | ALM_PT0004 | Diablo | 2017-02-11 07:41 | 431.6 | 590 | -158.4 | -26.85% | Design Issue - Other |  |  |  | After the HIHI alarm activation, the BTU level from Ryer Island increased, and V-716 reopened and mitigated further buildup of pressure. GTCC continued to monitor the pressure at Los Medanos PLS. Technicians from PG&E & Ryer production were also dispatched to the site, no reported issues. | Transmission | Near Hit | No | No
Near Hit | 112873186 | ST_RIP_S016_PT1 | Stockton | 2017-02-14 | 59.02 | 60 | -0.98 | -1.633% | Failure - Equipment | EQ |  | Regulator equipment appears to be iced over that may have contributed to the control issues and increasing pressure. | Tech was dispatched to assess and repair the regulator | HP Distribution | Near Hit | Yes | No
Near Hit | 112618134 | MMT_PT0088 | Milpitas District | 2017-02-15 07:40 | 552 | 557 | -5 | -0.8977% | Gas Control Center Operations | HU |  |  | • V-3 set point was readjusted by GTCC (13 psig below the HIHI alarm limit) and allowed the D/S pressure to re-stabilize • Lessons learned were identified, per discussion with GTCC. 1) Draft down D/S pressure before increasing the U/S regulation set point 2) Retain the 20 psig difference between the HIHI/MOP alarm limit and regulation set point to ensure a buffer | Transmission | Near Hit | Yes | No |  |  |  |  | GT.STAT.MISC.MLPTSTPLM_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\383510.pdf
Near Hit | 112640260 | KGF_PT0002 | Kern | 2017-02-28 07:41 | 498.9 | 600 | -101.1 | -16.85% | Clearance Preparation | HU |  |  | Immediate actions - Job momentary stopped per discussion between the supervisor and Gas Control Center - Collaboration with eng, control center, clearance supervisor on preventive measures - Lowering regulation set points at the Station was agreed upon - Stand down was conducted prior to the next pig run | Transmission | Near Hit | Yes | No
Near Hit | 112659484 | ACD_PT0033 | Sacramento | 2017-03-05 21:45 | 647.5 | 650 | -2.5 | -0.3846% | Failure - Equipment | EQ |  |  | • Technician identified that the solenoid needed to be replaced based on the recorded cycle count on the DNGP • V-33 was closed until the solenoid is replaced • Gas was rerouted through Meter 1 regulator V-7 from L-400 to L-210A • New solenoid has been ordered | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.MISC.CREEDPLS__ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\182416.pdf
OP | 112656282 | MIS_PT0043 | Mission | 2017-03-06 11:01 | 337 | 336 | 1 | 0.2976% | Failure - Equipment | EQ | P5.1 | Equipment failure with the current to pressure transducer output reading caused the load and trimmer valves to fail open. The output reading indicated 0 psig instead of expected 24 to 30 psig. | • Technician was dispatched to Irvington Station • Load & Trimmer electrical components were inspected by Tech • Tech discovered a discrepancy with I/P transducer output reading • Tech conducted several tests before replacing the existing I/P transducer (like to like) • The new I/P transducer was retested with no issues reported and then released to Gas Control Center | Transmission | Small OP Event | Yes | No | No | ACE |  |  | GT.STAT.MISC.IRVGTNPLS_ |  | x | 333
Near Hit | 112764744 | KEL_PT0001 | Los Padres/Kettleman | 2017-03-06 03:01 | 563 | 636 | -73 | -11.48% | Failure - Equipment | EQ |  |  | The run was isolated and tested by crew and CTL. No significant issues were identified. | Transmission | Near Hit | No | No
Near Hit | 112707551 | KAM_PT0001 | Stockton | 2017-03-09 23:05 | 494.74 | 498 | -3.26 | -0.6546% | Low Demand |  |  |  | N/A | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.MISC.AMADORSTAT | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\085551.pdf
Near Hit | 112674260 | SSW_PT0007 | Sacramento | 2017-03-11 16:58 | 494.9 | 500 | -5.1 | -1.02% | Failure - Equipment | EQ |  | Diaphragm was damaged on the pilot, potentially due to poor installation practices. Facility is scheduled to undergo a complete rebuild. Design 2017 build in 2018. | • Gas Control Center contacted on-call personnel • Technician identified that the primary reg had failed open and monitor in control • Technician also isolated the primary run and secondary run was placed in control • Field Technician found a damage diaphragm that was also exposed to powder debris • The diaphragm was replaced and controller retested for lock up | Transmission | Near Hit | No | No
Near Hit | 112873580 | SO_SON_S006_PT1 | Sonoma | 2017-03-18 | 40.1 | 42 | -1.9 | -4.524% | Low Demand |  |  |  | Regulator set points needed to be adjusted in response to a capacity project | HP Distribution | Near Hit | Yes | No
Near Hit | 112877776 | ST_STK_S018_PT1 | Stockton | 2017-03-20 | 10.59 | 11 | -0.41 | -3.727% | Low Demand |  |  |  | None, Gas Control monitored the situation as pressures stabilized. Local Maintenance was contacted to find out when winter operations would cease. | HP Distribution | Near Hit | Yes | No
Near Hit | 112877198 | SO_SON_S006_PT1 | Sonoma | 2017-03-20 | 40.1 | 42 | -1.9 | -4.524% | Low Demand |  |  |  | No action was taken. Set Points were stated to be adjusted the following day. | HP Distribution | Near Hit | Yes | No
Near Hit | 112877470 | SO_SON_S006_PT1 | Sonoma | 2017-03-20 | 40.23 | 42 | -1.77 | -4.214% | Low Demand |  |  |  | No action was taken. Set Points were stated to be adjusted the next day. | HP Distribution | Near Hit | Yes | No
Near Hit | 112876470 | SJ_SJS_S014_PT1 | San Jose | 2017-03-30 | 59.15 | 60 | -0.85 | -1.417% | Low Demand |  |  |  | No action was taken. Winter operations to be ramped down the next day. | HP Distribution | Near Hit | Yes | No
Near Hit | 112876882 | SF_SF_R017_PT3 | San Francisco | 2017-04-11 | 11.04 | 12 | -0.96 | -8% | Failure - Equipment | EQ |  |  | Set point was adjusted and crew sent to repair regulator. Tailboard was later held with control room since it was a B-inspection which may have caused the alarm | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00007
OP | 112772011 | Gauge | Kern | 2017-04-15 | 663 | 335 | 328 | 97.91% | Gas Contaminants - Liquids | EQ | P50.7 | Free liquids, in the pipeline, accumulated in the inlet filter and regulator, reducing loading pressure at the regulator station. PG&E failed to recognize the risk that clearance activities have the potential to move contaminants in the pipeline effecting the operations of metering and regulator equipment. |  | Transmission | Large OP Event | No | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000711 |  | 250 | 260
Near Hit | 112915185 | CBF_PT0003 | North Valley | 2017-04-25 03:30 | 574 | 580 | -6 | -1.034% | Clearance Execution | HU |  |  | The next day when a duplicate clearance, 80040369, was performed, Valve 21.71 was closely monitored in the field in order to avoid a repeat event. | Transmission | Near Hit | No | No
OP | 112819827 | BMD_PT2205 | McDonald Island District | 2017-04-27 15:39 | 2314 | 2160 | 154 | 7.13% | Failure - Equipment | EQ | P95.10 | Layers of protection in the programming logic controller (suction and discharge valves), relief valve and pilot, and impairment process failed to protect piping from the overpressure event. |  | Transmission | Large OP Event | No | Yes | No | Yes |  | H-19 | GT.STAT.COMP.MCDONLDISL | 385179 | x | x | 1725
Near Hit | 112915334 | SI_RSV_S021 | Sierra | 2017-04-30 22:38 | 59.89 | 60 | -0.11 | -0.1833% | Gas Contaminants - Sulfur |  |  |  | Sulfur was cleaned out. | HP Distribution | Near Hit | Yes | No
Near Hit | 112931288 | SF_SF_PR017 | San Francisco | 2017-05-01 02:08 | 11 | 12 | -1 | -8.333% | SP Too Close to MOP/HiHi |  |  | x | • GCC contacted the local on-call of the HIHI alarm activation. • The decision was made for GCC to continue monitoring the pressure. • Same day regulation adjustments at several reg stations were scheduled per the completion of winter operations. | LP Distribution | Near Hit | No | No |  |  |  |  | GD.STAT.LPRS.00007
Near Hit | 112931750 | M21_PT0005 | San Jose | 2017-05-02 00:57 | 243.01 | 250 | -6.99 | -2.796% | SP Too Close to MOP/HiHi |  |  | x | • GCC contacted the local division for HIHI alarm response • Local Technician was dispatched out to Diana Ave Reg Station • Technician found pressure below the 243 psig HIHI alarm limit (at about 238 psig) • Technician lowered the existing pressure from 238 psig to 231 psig • No other issues reported by the Technician | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.MISC.DIANALRCV_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\082126.pdf
OP | 112844207 | Gauge | Yosemite | 2017-05-05 06:31 | 61.44 | 60 | 1.44 | 2.4% | Failure - Equipment | EQ | P5.1 | Severe wear on the regulator boot, debris found on the monitor diaphragm resulted in unstable control of the regulation equipment. |  | HP Distribution | Small OP Event | No | Yes | No | ACE |  | H-14 | GT.STAT.LVCR.0000000105 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Mer\Tif\Gas\REGSTATION\0805204.PDF | 45 | 50
OP | 112859343 | SYC_PT0012 | Sacramento | 2017-05-08 03:17 | 487 | 485 | 2 | 0.4124% | Gas Contaminants - Sulfur | EQ | P5.1 | Sulfur contaminants were found on lead pilot cartridge which caused the lead regulator set point to drift and exceed the MAOP limit. The monitor as found set point was higher than normal set point. | • GPOM Technician dispatched to Marysville Buttes Station, and upon arrival the Technician gauged D/S and recorded a reading of ~465.6 psig with lead regulator in control. • Crew isolated the lead run, and lag run placed in control for further inspection of the lead run. • Crew conducted an internal inspection of the lead regulation and identified the following: o Regulator diaphragm showed signs of wear (See Figure 6 – Left) o Indentations from foreign debris were also identified (See Figure 6 – Right) o Sulfur/contaminant build up found on the pilot cartridge o Pilot stem also showed signs of sulfur/contaminant residues • Crew rebuilt the regulator, checked for lock up, and run returned to service the same day. • Sulfur gon filter will be installed at this regulation system as soon as the required maintenances are completed (per local supervisor e-mail) | Transmission | Small OP Event | No | No | No | ACE |  |  | GT.STAT.MISC.YUBACITYUH |  | 470 | 480
Near Hit | 112932546 | KKD_PT0200 | Kern | 2017-05-09 09:44 | 703.96 | 1000 | -296.04 | -29.6% | Maintenance Operations Quality | HU |  |  | • V-1 was opened and relieved the abrupt pressure buildup U/S | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.MISC.KRNRVRPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\087429.pdf
OP | 112879269 | KE_THP_I010 | Kern | 2017-05-14 04:45 | 662.06 | 335 | 327.06 | 97.63% | Gas Contaminants - Liquids | EQ | P50.7 | Free liquids, in the pipeline, accumulated in the inlet filter and regulator, reducing loading pressure at the regulator station. PG&E failed to recognize the risk that clearance activities have the potential to move contaminants in the pipeline effecting the operations of metering and regulator equipment. |  | Transmission | Large OP Event | No | Yes | No | Yes |  | LVCR | GT.STAT.LVCR.0000000711 | 082609 | 250 | 260
Near Hit | 112884865 | SSD_PT0003 | Sacramento | 2017-05-17 03:10 | 694.8 | 700 | -5.2 | -0.7429% | Low Demand |  |  | Regulator over shot while power plant shut in, and monitor took control and also activated the HIHI alarm. | Immediate Actions - • GCC notified the local sup of the HIHI alarm • Tech dispatched to SMUD station • Tech confirmed that the monitor was in control and continued to observed outlet pressure until it dropped below HI alarm | Transmission | Near Hit | No | No
Near Hit | 112934853 | SO_PET_S022 | Sonoma | 2017-05-21 02:52 | 48.04 | 50 | -1.96 | -3.92% | SP Too Close to MOP/HiHi |  |  |  | • GCC contacted the local supervisor regarding the HIH alarm • Local supervisor dispatched a Technician to the HIS reg stations • Technician lowered two reg stations in the Santa Rosa Southward HIS by 0.5 to 1 psig | HP Distribution | Near Hit | Yes | No
OP | 113141481 | SA_EMR_I008 | Sacramento | 2017-05-22 | 61.83 | 60 | 1.83 | 3.05% | Gas Contaminants - Sulfur | EQ | P5.1 | Gas Control discovered a legacy ERX had not alarmed an overpressure event. Upon further investigation, it was determined the sulfur contaminants were found on lead pilot cartridge which caused the lead regulator set point to drift and exceed the MAOP limit. | Technician requested to disable the alarm notification function prior to an inspection at the Legacy ERX, there is no record of the technician removing the maintenance clearance, so the ERX remained unable to send email notifications in an alarming state to the Division - upon returning to the station after the overpressure event notification sulfur residue was identified on the pilot stem, and the regulator was rebuilt and returned to service with lower set points. | HP Distribution | Small OP Event | Yes | No | No | ACE |  | H-14 | GD.STAT.DIST.01119 |  | 54 | 58
Near Hit | 112917620 | DA_SUN_RC42_PT3 | De Anza | 2017-05-31 00:22 | 59.1 | 60 | -0.9 | -1.5% | Failure - Equipment | EQ |  |  | Technician checked the regulator at Ross Dr. and Hamlin Ct. station and adjusted the reg set point to ~57 psig | HP Distribution | Near Hit | No | No |  |  |  | H-14 | GD.STAT.DIST.00585
Near Hit | 112923093 | SO_PET_S022 | Sonoma | 2017-05-31 00:49 | 48.04 | 50 | -1.96 | -3.92% | SP Too Close to MOP/HiHi |  |  |  | Immediate Actions: • Gas Control Center contacted the on-call personnel • A Technician was dispatched to the site and found the regulator operating as intended at about 47.5 psig (48 psig HIHI alarm limit - originally) • After further discussions, the HIHI alarm limit was changed to 49 psig HIHI alarm limit | HP Distribution | Near Hit | Yes | No
Near Hit | 112980390 | EB_BER_RE09 | East Bay | 2017-06-18 03:26 | 14.01 | 15 | -0.99 | -6.6% | SP Too Close to MOP/HiHi |  |  |  | Immediate Actions: • Technician dispatched to the reg station • Technician readjusted regulator to ~12.4" | HP Distribution | Near Hit | Yes | No |  |  |  | H-14 | GD.STAT.DIST.01473
Near Hit | 112993769 | M6A_PIC_74A | Hollister District | 2017-06-22 12:12 | 610 | 625 | -15 | -2.4% | Gas Control Center Operations | HU |  | GSO (GTCC) Operator inadvertently entered a set point change meant for PLS-4A into PLS-6A which resulted in release of gas at relief valve J at PLS-6A. | The operator was relieved of their duties, turnover shift was completed, fatigue assessment was performed and the employee was sent for PAT testing. | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.MISC.PLS-6A____; GT.STAT.MISC.PLS-6B____ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\081817.pdf
Near Hit | 112993859 | SO_PET_R471 | Sonoma | 2017-06-25 01:34 | 49.01 | 50 | -0.99 | -1.98% | SP Too Close to MOP/HiHi |  |  |  | Gas Control Center contacted on call personnel and Technician adjusted reg set point at the station | HP Distribution | Near Hit | Yes | No
Near Hit | 113018649 | SAR_PT0001 | Sacramento | 2017-06-29 10:57 | 179.4 | 180 | -0.6 | -0.3333% | Maintenance Operations Quality | HU |  |  | Gas Control Center contacted the crew and validated other SCADA points in the vicinity. | Transmission | Near Hit | No | No
Near Hit | 113019137 | SRB_PT0002 | North Valley | 2017-07-04 05:56 | 463.5 | 470 | -6.5 | -1.383% | Low Demand |  |  |  | Technician was dispatched to the station and reg adjustment was performed. | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.MISC.REDBLUFFPR | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\082621.pdf
Near Hit | 113049430 | SO_PET_R471 | Sonoma | 2017-07-09 01:32 | 49.2 | 50 | -0.8 | -1.6% | SP Too Close to MOP/HiHi |  |  |  | • Technicians were dispatched to Santa Rosa & Southward HIS • Six stations were inspected by Technicians • Regulation set point was lowered at one of the reg station(DR-507) • DR-507 reg set point was lowered from 49 psig to 46.5 psig | HP Distribution | Near Hit | No | No
Near Hit | 113098995 | Gauge | Kern | 2017-07-31 | 68 | 250 | -182 | -72.8% | Gas Contaminants - Debris |  |  |  |  | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.LVCR.0000000270
OP | 113114495 | Chart Recorder | Sierra | 2017-07-30 18:00 | 73 | 60 | 13 | 21.67% | Failure - Equipment | EQ | P50.7 | Event identified by a chart run, a teardown of the station found debris in various portions of the station. |  | HP Distribution | Large OP Event | No | No | No | Yes |  | H-14 | GD.STAT.DIST.11162 | file://utility.pge.com/projects/metcat/metcatprd-fs01/comp_pub/Aub/Tif/Gas/RegStation/0806087.PDF | 54 | 57
Near Hit | 113112850 | K2B_PT0004 | Kern | 2017-08-01 10:28 | 567.6 | 572 | -4.4 | -0.7692% | False Alarm |  |  |  | • GCC contacted GPOM and Technician was dispatched to PLS 2 • Technician confirmed the stuck valve and adjusted the limit switch on the valve • The valve was retested and returned to service | Transmission | Near Hit | Yes | No |  |  |  |  | GT.STAT.MISC.PLS-2B____ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\082328.pdf
Near Hit | 113132389 | MMT_PT0088 | Milpitas District | 2017-08-07 10:55 | 400 | 400 | 0 | 0% | Gas Control Center Operations | HU |  | Gas Control Operations cracked V-22 open to initiate flow to L300B |  | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.MISC.MLPTSTPLM_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\383510.pdf
OP | 113133907 | FFN_PT0002 | Fresno | 2017-08-08 10:30 | 413.8 | 400 | 13.8 | 3.45% | Maintenance Operations Quality | HU | P5.1 | Technicians closed in primary run too quickly, demand was low and regulation was slow to react, causing a overpressure event |  | Transmission | Small OP Event | Yes | No | No | ACE |  | H-14 | GT.STAT.MISC.FRESNOLOAD |  | 380 | 395
OP | 113133907 | FFN_PT0002 | Fresno | 2017-08-10 08:55 | 402 | 400 | 2 | 0.5% | Maintenance Operations Quality | HU | P5.1 | Technicians working on 'B' inspection while hand throttling a valve outside of the clearance steps exceeded the pipeline MAOP. |  | Transmission | Small OP Event | No | No | No | ACE |  | H-14 | GT.STAT.MISC.FRESNOLOAD |  | 380 | 395
Near Hit | 113167040 | M19_PT0106 | Hollister District | 2017-08-17 08:02 | 508.7 | 631 | -122.3 | -19.38% | Maintenance Operations Quality | HU |  | While performing the maintenance in accordance with the clearance 80045608, valve operations lead to pressure reaching 508 psig | CAP#113167040 | Transmission | Near Hit | Yes | No | No | No | No |  | GT.STAT.MISC.HILLSTRPLS_
OP | 113181647 | Gauge | Yosemite | 2017-08-21 11:38 | 241.8 | 145 | 96.8 | 66.76% | Failure - Equipment | EQ | P50.7 | During Annual maintenance, the technician discovered a 20ft section of pipe where pressure was 240 psig. By-pass valve (V-1) was leaking into the downstream resulting in an overpressure condition. | Appears to have gone into OP last year - according to chart - will review in more detail. | Transmission | Large OP Event | No | No | No | Yes | No | LVCR | GT.STAT.MISC.SPCKLSPLS_ |  | 145 | 155
OP | 113242778 | OS3_PT0004 | Diablo | 2017-08-22 06:36 | 340.8 | 338 | 2.8 | 0.8284% | Clearance Preparation | HU | P5.1 | Clearance steps were not written in a sequence where risk was minimized during the valve operations. Valves bled by into the isolated section of pipe. |  | Transmission | Small OP Event | No | No | No | ACE |  | H-19 | GT.STAT.MISC.SP3191XTI_ | 085535 | x | x
Near Hit | 113643635 | YO_FRB_I013 | Yosemite | 2017-09-28 13:55 | 59.98 | 60 | -0.02 | -0.03333% | Maintenance Operations Quality | HU |  |  |  | HP Distribution | Near Hit | No | No |  |  |  |  | GT.STAT.LVCR.0000000105
OP | 113643635 | YO_FRB_I013 | Yosemite | 2017-09-28 13:55 | 66.53 | 60 | 6.53 | 10.88% | Maintenance Operations Quality | HU | P50.2 | Technicians did not address ongoing overpressure condition during maintenance. |  | HP Distribution | Large OP Event | No | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000105 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Mer\Tif\Gas\REGSTATION\0805204.PDF | 45 | 50
Near Hit | 113643635 | YO_FRB_I013 | Yosemite | 2017-09-28 13:55 | 523 | 620 | -97 | -15.65% | False Alarm |  |  | Incorrect alarm settings. |  | Transmission | Near Hit | No | No
OP | 113738595 | Gauge | Fresno | 2017-10-13 15:21 | 465 | 200 | 265 | 132.5% | Maintenance Operations Quality | HU | P50.2 | Technicians gauged bypass line and not main run - did not follow procedures. |  | Transmission | Large OP Event | No | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000231 |  | 200 | 215
Near Hit | 113748028 | FCT_PT0005 | Yosemite | 2017-10-19 15:39 | 191 | 180 | 11 | 6.111% | False Alarm |  |  | Gas trapped in a senseline tube. |  | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.LVCR.0000000231 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0810923.pdf
OP | 113754369 | Gauge | Stockton | 2017-10-21 16:34 | 450 | 60 | 390 | 650% | Design Issue | HU | P99.1 | 3rd Party struck regulator station removing senselines from the equipment. |  | HP Distribution | Large OP Event | No | No | No | Yes |  | H-14 | GD.STAT.DIST.01594 | 385158.pdf | 54 | 58
OP | 113791819 | ACD_PT008B | Sacramento | 2017-10-24 06:49 | 651.86 | 650 | 1.86 | 0.2862% | Gas Control Center Operations | HU | P5.1 | Adjusting source load did not address differential pressure before switching lines - PLC programmed control. |  | Transmission | Small OP Event | No | No | No | ACE |  |  | GT.STAT.MISC.CREEDPLS_ |  | 600 | 639
OP | 114157455 | Gauge | Fresno | 2017-10-26 | 365 | 175 | 190 | 108.6% | Failure - Equipment | EQ | P50.7 | Check valve failure - maintenance did not catch event |  | Transmission | Large OP Event | No | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000232 |  | 150 | 170
OP | 113776779 114049473 | YO_MDA_I017 | Yosemite | 2017-10-31 07:45 | 165.99 | 145 | 20.99 | 14.48% | Failure - Equipment | EQ | P50.7 | Leaking Bypass Valve |  | Transmission | Large OP Event | No | No | No | Yes | No | LVCR | GT.STAT.MISC.SPCKLSPLS_ |  | 130 | 140
Near Hit | 113792213 | KAM_PT0001 | Stockton | 2017-11-07 04:00 | 495 | 498 | -3 | -0.6024% | Low Demand |  |  |  |  | Transmission | Near Hit | No | No
OP | 113792516 | FR_FOW_RL51 | Fresno | 2017-11-07 10:15 | 13.8 | 12 | 1.8 | 15% | Maintenance Operations Quality | HU | P5.1 | While technican was making monitor set point adjustment pressure increased. |  | LP Distribution | Small OP Event | No | No | No | ACE |  | 1 | GD.STAT.LPRS.00165 | http://wwwt2/METFileAccess/get.ashx?file=\\utility.pge.com\projects\metcat\metcatprd-fs01\COMP\FRE\TIF\GAS\REGSTATION\0805991.PDF | 8.5 | 10 | 14
Near Hit | 114031802 | SJ_MGH_S002 | San Jose | 2017-11-22 01:37 | 54 | 55 | -1 | -1.818% | Low Demand |  |  |  |  | HP Distribution | Near Hit | Yes | No |  |  |  |  | GT.STAT.MISC.SPCKLSPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\085533.pdf
Near Hit | 114051294 | SMB_PT0001 | Sacramento | 2017-12-04 05:24 | 372 | 463 | -91 | -19.65% | Gas Contaminants - Liquids |  |  | Disassembly discovered liquids in the pilot. |  | Transmission | Near Hit | Yes | No |  |  |  |  | GT.STAT.MISC.AMADORSTAT | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\085551.pdf
Near Hit | 114277982 | SMR_PT0007 | Sacramento | 2018-01-12 09:26 | 99 | 100 | -1 | -1% | Failure - Equipment | EQ |  | Rapid increase of line pressure from 94.5 psig to 99.0psig which may have resulted from delay in regulation. Regulation seems to have been slow to react. | N/A | Transmission | Near Hit |  | No
Near Hit | 114277987 | K15_PT032 | Kettleman District | 2018-01-17 03:40 | 861 | 890 | -29 | -3.258% | Failure - Equipment | EQ |  | V-32 Controller did not react fast enough, and pressure increased above alarm state. | N/A | Transmission | Near Hit |  | No |  |  |  | H-19 | GT.STAT.MISC.PANOCHPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284100.pdf
Near Hit | 114277988 | RCC_PT0003 | Humboldt | 2018-01-24 19:25 | 692 | 1440 | -748 | -51.94% | Failure - Equipment | EQ |  | The regs are not in service as Cummings is now handling the regulation and both U/S & D/S block valves are closed and there must be a slight leak in V-1 (U/S) causing the pressure to increase. The expectation is that the pressure will continue climbing to equalize the U/S L177 pressure, currently at 692 psig. | N/A | Transmission | Near Hit |  | No |  |  |  |  | GT.STAT.MISC.CUMMINGSCK | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\082474.pdf
OP | 114253943 | AWD_PT0001 | Willows District | 2018-01-28 19:30 | 1057 | 1040 | 17 | 1.635% | Failure - Equipment | EQ |  | V-7 shut on its own due to equipment malfunction. | Replace i/o card, reprogram to fail last. | Transmission | Small OP Event | No | Yes | No | ACE |  | H-19 | GT.STAT.MISC.WLDGSEPLS_ |  | x | 1035
OP | 114270026 | DI_CND_I001 | Diablo | 2017-12-20 15:30 | 345.5 | 338 | 7.5 | 2.219% | Failure - Equipment | EQ | P5.1 | During routine maintenance crew discovered failed boots in both the monitor and regulator on the backup run, additionally there was debris in the control loop. (ERX not in Gas Control) |  | Transmission | Small OP Event | No | No | No | ACE |  | LVCR | GT.STAT.LVCR.0000000352 |  | 320 | 330
Near Hit | 114277989 | M19_PT0105 | Hollister District | 2018-02-02 06:45 | 297.8 | 300 | -2.2 | -0.7333% | Failure - Equipment | EQ |  | ​A valve was closed, and when the valve was opened built up pressure behind came through and the reg valve could not catch in time causing a HIHI. | N/A | Transmission | Near Hit |  | No |  |  | No | H-19 | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
Near Hit | 114390138 | K15_PT0035 | Kettleman District | 2018-02-20 17:28 | 861 | 890 | -29 | -3.258% | Clearance Execution | HU |  | ​The field working under clearance 80052342 at Panoche station hit HiHi and MOP breech while testing valve V43r. Pressure stayed in station (rated at 890#) and never made it to L300A/L300b. | N/A | Transmission | Near Hit |  | Yes |  |  |  | H-19 | GT.STAT.MISC.PANOCHPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284100.pdf
Near Hit | 114390139 | OOA_PT0002 | East Bay | 2018-02-20 11:15 | 147.8 | 150 | -2.2 | -1.467% | Failure - Equipment | EQ |  | Oakland GLC - regulation seems to have drifted up and now controlling at high-high (maybe monitor control) - station not on monitor control when technician arrived |  | Transmission | Near Hit |  | No
Near Hit | 114400067 | OS3_PT0006 | Diablo | 2018-02-17 08:20 | 427.3 | 573 | -145.7 | -25.43% | Gas Contaminants - Gas Quality |  |  | Low BTU of 747.2 at Ryer Island caused V716 to throttle shut causing Hi Hi alarms of 427.3. |  | Transmission | Near Hit |  | Yes |  |  |  | H-19
Near Hit | 114401215 | OCM_PT0002 | Diablo | 2018-03-11 23:50 | 170 | 170 | 0 | 0% | SP Too Close to MOP |  |  | Winter set points and low consumption - Crystal gauge measured pressure 0.2 psig higher than SCADA |  | Transmission | Near Hit | Yes | No
Near Hit | 114422916 | K15_PT0032 | Kettleman District | 2018-03-18 03:30 | 850 | 890 | -40 | -4.494% | Failure - Equipment | EQ |  | Panoche station piping is rated at 890#. pressures somehow reached 850# with V32 shut. |  | Transmission | Near Hit |  | Yes |  |  |  | H-19 | GT.STAT.MISC.PANOCHPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284100.pdf
Near Hit | 114428316 | SFD_PT0001` | Sacramento | 2018-03-20 | 228.8 | 230 | -1.2 | -0.5217% | Clearance Execution | HU |  | Distribution tech in the field adjusted regulators> Causing them to open which caused a near hit at Suisun under clearance 80054244 Station 081528 |  | Transmission | Near Hit |  | No |  |  |  |  | GT.STAT.MISC.FAIRFIELDS | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\183969.pdf
Near Hit | 114450784 | SMR_PT0003 | North Bay | 2018-03-28 12:05 | 168.05 | 175 | -6.95 | -3.971% | Failure - Equipment | EQ |  | Benicia Reg hit Hi Hi of 168.05 for aproximately 15 minutes till regulation started controling. (0800103) |  | Transmission | Near Hit |  | No
Near Hit | 114483170 | SMR_PT0003 | Sacramento | 2018-04-01 09:35 | 173.01 | 180 | -6.99 | -3.883% | Failure - Equipment | EQ |  | Unclear about issue or response from GLS |  | Transmission | Near Hit |  | No | [5 empty] | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\081622.pdf
Near Hit | 114483190 | SNH_PT0004 | Sacramento | 2018-04-03 18:45 | 253.22 | 260 | -6.78 | -2.608% | Failure - Equipment | EQ |  | ​V-142 at NSH had been oscillating and u/s line pressure would start to climb. In an attempt to pull line pressure down, order was given to raise v-142 setpoint from 165# to 170# only issue is once setpoint was acheived, valve started to throttle causing u/s line pressure to spike and hit hi-hi. Order was then given to return v-142 setpoint back to 165# and line pressure settled out. |  | Transmission | Near Hit |  | Yes |  |  |  |  | GT.STAT.MISC.NSACHOLDER | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\382860.pdf
Near Hit | 114483196 | ALM_PT0004 | Los Medanos District | 2018-04-07 21:45 | 431.2 | 590 | -158.8 | -26.92% | Failure - Equipment | EQ |  | V-704 controller went bad and froze in position causing hihi alarms at LMS Ryer Island and Concord station. |  | Transmission | Near Hit |  | No
Near Hit | 114483211 | ALM_PT1005 | Los Medanos District | 2018-04-07 23:50 | 432 | 590 | -158 | -26.78% | Maintenance Operations Quality | HU |  | Los Medanos Crews were opening up v-1 at los medanos ryer island, pressure spiked to 432 hihi |  | Transmission | Near Hit |  | No
Near Hit | 114502646 | SSA_PT0009 | Sacramento | 2018-04-10 00:08 | 253.23 | 260 | -6.77 | -2.604% | Failure - Equipment | EQ |  | Reg valves 17 & 21 are not closing when demand drops off causing d/s to hit HiHi. Engineering and supervision is aware due to this incident also happening 04/04/2018. They are in the process of lowering regulation. Regulation valves 17 & 21 not adjusting for lower demand. |  | Transmission | Near Hit | Yes | No |  |  |  | H-14 | GD.STAT.DIST.01090 | \\fairfield07\gis\giswebMiscFiles\GasStations\385186.pdf
Near Hit | 114502702 | ALM_PT1004 | Los Medanos District | 2018-04-10 01:16 | 434 | 590 | -156 | -26.44% | Failure - Equipment | EQ |  | ​BTU dropped to 731 causing V-716 to pinch to 18% and breaching MOP of 433#. Pressure spiked to 438#, then recovered. Abnormal incident reports indicates 434 psig, and SCADA error. MAOP 590psig |  | Transmission | Near Hit
Near Hit | 114502482 | SNH_PT0004 | Sacramento | 2018-04-11 09:25 | 253 | 260 | -7 | -2.692% | Maintenance Operations Quality | HU |  | DFM 0613-01 hit a Hi Hi of 253.0# with a Hi Hi alarm of 253# for aproximately 2 minutes while techs working on clearance 80040088.DFM 0613-01 hit a Hi Hi of 253.0# with a Hi Hi alarm of 253# for aproximately 2 minutes while techs working on clearance 80040088. Leaky valve is suspected although it is still being investigated which one. Tech opened V142 to bleed pressure down. |  | Transmission | Near Hit |  | Yes |  |  |  |  | GT.STAT.MISC.NSACHOLDER | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\382860.pdf
OP | 114506352 | SNH_PT0204 | Sacramento | 2018-04-14 06:57 | 518.46 | 500 | 18.46 | 3.692% | Clearance Execution | HU |  | Crews are working under clearance #80038113 at the NSUGH to retire DFDS 3561 and regulated gas into blocked-in section of piping. |  | Transmission | Small OP Event | No | Yes | No | ACE |  |  | GT.STAT.MISC.NSACHOLDER |  | 480 | 495
Near Hit | 114513463 | ALM_PT0004 | Los Medanos District | 2018-04-17 09:30 | 433.3 | 590 | -156.7 | -26.56% | Failure - Equipment | EQ |  | ​BTU value out of Ryer Island dropped below 750 causing v-716 to close backing into v-1 (closed) breaching both Hi-Hi at 426 psig then MOP at 733psig. Slug of ow btu gas coming from Ryer Island caused v-716 to close per ratio control. |  | Transmission | Near Hit
Near Hit | 114526337 | K15_PT0032 | Kettleman District | 2018-04-20 18:15 | 875 | 890 | -15 | -1.685% | Gas Control Center Operations | HU |  | ​V-32/32r regulation raised to 800# when v-43/43r regulation at 790# closed, causing mop to hit inside the station at 875#. Station piping mop is 890#. 300A regulation was not fully of the way above L401 pls regulation setpoint. Regulation sp too close and was not regulation out of L401 pls as intended. |  | Transmission | Near Hit | [6 empty] | GT.STAT.MISC.PANOCHPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284100.pdf
Near Hit | 114526379 | K15_PT0032 | Kettleman District | 2018-04-22 05:45 | 863 | 890 | -27 | -3.034% | Failure - Equipment | EQ |  | Near Hit MOP event occured within Panoche station. Pressure reached 863#. Pipe with in station rated at 890#. No Panoche moves were made at the time of incident. V32 is attributed to short section being locked in and leakage at V-32. Tech will need to do a full investigation of station to determine what equipment is malfunctioning. ​Graded a 4 due to the fact that GCC was not able make operations to prevent from MOP alarm being breached. MAOP of station piping is 890psig, therefore a OP near miss |  | Transmission | Near Hit | [6 empty] | GT.STAT.MISC.PANOCHPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284100.pdf
Near Hit | 114542084 | AAN_PT000B | Diablo | 2018-04-26 | 713.2 | 720 | -6.8 | -0.9444% | Gas Control Center Operations | HU |  | Gas Control Operations Human Performance Operator was making a set point change from 675 to 680# And had inavertantly put a set point of 800# causing the valves to swing open. Once the pressures went to 710 the monitor valves went into control. The point AN_PT000B hihi is 713 psig breached hihi 713.1875 psig. |  | Transmission | Near Hit | [6 empty] | GT.STAT.MISC.ANTGSTPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\4807103.pdf
Near Hit | 114582238 | KLM_PT0003 | Kern | 2018-05-02 13:00 | 356 | 400 | -44 | -11% | Maintenance Operations Quality | HU |  | SoCal had people working and they accidently opened up a valve over pressuring a distribution line on their side. On Scada it appeared to be a line break but that was false. |  | Transmission | Near Hit | [6 empty] | GT.STAT.MISC.ANTGSTPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\4807103.pdf
Near Hit | 114596313 | OOA_PT0002 | East Bay | 2018-05-11 12:00 | 145.5 | 175 | -29.5 | -16.86% | Maintenance Operations Quality | HU |  | Discovered that regulator that should control at 121#, was wide open (no control) with the downstream monitor controlling @127#. Inlet pressure was 220#. 2 GCTs called to investigate the station at 945pm. Techs discovered the gas supply to the rack was turned off (supply gas to rack for regulation sensing and control). Shut station in, repaired leak on rack, reset regulation set points and put back in service. Oakland PLS regulating v-21 & 21R failed open and upon arrival mon v-22 was in control. |  | Transmission | Near Hit | [6 empty] | GT.STAT.MISC.LAMONTMTRS | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0806461.pdf
OP | 114623401 | SF_SF_R123 | San Francisco | 2018-05-18 09:50 | 13.5 | 12 | 1.5 | 12.5% | Maintenance Operations Quality | HU |  | While undergoing an A-inspection the station inlet and fire valves (#2603, and #9069) were operated which resulted in increase in pressure. |  | LP Distribution | Small OP Event | No | No | No | ACE |  | LP | GD.STAT.LPRS.00051 | file://utility.pge.com/projects/metcat/metcatprd-fs01/comp_pub/SFO/Tif/Gas/RegStation/0801904.PDF | 7.3 | 10 | 14
OP | 114622191 | JDL_PT0002 | Hollister District | 2018-05-18 04:35 | 427.5 | 408 | 19.5 | 4.779% | Clearance Preparation | HU |  | While returning equipment to service under clearance #80040088 the crew regulated gas into blocked-in section of piping. The clearance had a poor sequence of operations. |  | Transmission | Small OP Event | No | No | No | ACE |  |  | GT.STAT.MISC.DOLNRDPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\083812.pdf | x | x
Near Hit | 114668426 | OOA_PT0002 | East Bay | 2018-06-06 06:50 | 151.8 | 175 | -23.2 | -13.26% | Maintenance Operations Quality | HU |  | Crew was working on 80054948 |  | Transmission | Near Hit
Near Hit | 114670370 | M19_PT0105 | Hollister District | 2018-06-06 09:35 | 296.9 | 300 | -3.1 | -1.033% | Maintenance Operations Quality | HU |  | Loss of power gass to V10R during 80056972 clearance operation. |  | Transmission | Near Hit |  | No |  |  | No | H-19 | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
OP | 114697464 | SWL_PT0002 | North Valley | 2018-06-13 01:00 | 102.49 | 100 | 2.49 | 2.49% | Failure - Equipment | EQ |  | Equipment failure with Grove regulator. |  | Transmission | Small OP Event | Yes | No | No | ACE |  | H-14 | GT.STAT.MISC.WILLOWSREG | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\087580.pdf | 90 | 100
OP | 114808684 | SBR_PT0002 | Sierra | 2018-07-22 08:00 | 480 | 60 | 420 | 700% | Failure - Equipment | EQ | P99.1 | Equipment failure resulted in a rupture as a result of an overpressure. |  | Transmission | Large OP Event | No | No | No | Yes | No | H-10 | 0 |  | 45 | 50 | 53
OP | 114833220 | EB_OAK_RA54 | East Bay | 2018-07-27 | 13.9 | 12 | 1.9 | 15.83% | Maintenance Operations Quality | HU |  | M&C squeezed the main resulted in back up of pressure. |  | LP Distribution | Small OP Event | No | No | No | ACE |  | H-10 | GD.STAT.LPRS.00075 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Oak\Tif\Gas\RegStation\0808707.PDF | 9 | 10.2 | 14
OP | 114863666 | CC_CML_RM27 | Central Coast | 2018-08-07 10:42 | 53.5 | 51 | 2.5 | 4.902% | Failure - Equipment | EQ |  | Equipment failure and monitor lockup resulted in an overpressure event. |  | HP Distribution | Small OP Event | Yes | No | No | ACE |  | H-14 | GD.STAT.DIST.00390 | 0806466.PDF | 47 | 50
Near Hit | 114907960 | THM_PT0125 | Hollister District | 2018-08-20 09:54 | 493.7 | 500 | -6.3 | -1.26% | Maintenance Operations Quality | HU |  | Clearance operations ignored human performance tool of having a questioning attitude |  | Transmission | Near Hit | Yes | No |  |  | No | H-19 | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
OP | 114909830 | FFN_PT0002 | Fresno | 2018-08-21 08:00 | 401.3 | 400 | 1.3 | 0.325% | Clearance Execution | HU |  | While performing steps as written in clearance #80060108 (isolating L-111A from Chateau Fresno Station to Fresno GLC to replace MLV 21.60) the crew was manually throttling V-106 pressure upon the return to service of Fresno GLC regulation did not catch. |  | Transmission | Small OP Event | Yes | No | No | ACE |  |  | GT.STAT.MISC.FRESNOLOAD | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\382885.pdf | 380 | 395
Near Hit | 114960848 | FLP_PT0004 | Yosemite | 2018-09-06 01:28 | 60.85 | 70 | -9.15 | -13.07% | 3rd Party - Equipment |  |  | Customer ESD shut-in resulted in slow reaction of equipment. |  | Transmission | Near Hit | [6 empty] | GT.STAT.LVCR.0000000258 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0806404.pdf
Near Hit | 114960750 114959264 | DI_WLC_RW26_PT3 | Diablo | 2018-09-04 | 58.3 | 60 | -1.7 | -2.833% | Failure - Equipment | EQ |  |  |  | HP Distribution | Near Hit | Yes | No |  | N |  | H-14 | GD.STAT.DIST.00203
OP | 114978037 | KE_BKD_R130 | Kern | 2018-09-14 11:50 | 52.61 | 51 | 1.61 | 3.157% | Clearance Execution | HU |  | During the return to service and restoration of pressure after clearance #80061266 downstream pressure exceeded MAOP for 10 minutes. |  | HP Distribution | Small OP Event | Yes | No | No | ACE |  | H-14 | GD.STAT.DIST.00606 | 0804706.PDF | 47 | 50
Near Hit | 115002879 | ALM_PT1703 | Diablo | 2018-09-25 14:18 | 434.2 | 468 | -33.8 | -7.222% | Failure - Equipment | EQ |  | Obselete regulation equipment (Moore 352) failed causing the monitor to control. |  | Transmission | Near Hit | No | Yes
Near Hit | 115051378 | FLP_PT0004 | Yosemite | 2018-10-11 02:02 | 63 | 70 | -7 | -10% | 3rd Party - Equipment |  |  | Customer ESD shut-in resulted in slow reaction of equipment. |  | Transmission | Near Hit | [6 empty] | GT.STAT.LVCR.0000000258 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0806404.pdf
OP | 115080794 | MiniAT | Yosemite | 2018-10-08 | 650 | 125 | 525 | 420% | Gas Contaminants - Sulfur | EQ | P95.8 | Customer identified OP on houseline with gauge, sulfur identified between regulator diaphragm and grid. |  | Transmission | Large OP Event | No | No | No | Yes |  | H-15 | GT.STAT.LVCR.0000000125 |  | 115 | 125
OP | 115250853 | Gauge | Diablo | 2018-11-04 08:00 | 63 | 60 | 3 | 5% | Failure - Equipment | EQ |  | Customer went offline with full stop; regulators failed to lock up, and set points to close to MAOP. | • GPOM crew has engaged the Planning Engineer for a distribution request to reduce set points on the regulator set from (lead/lag/monitor of 55/52/60 psig to 52/50/56psig), and will perform full ‘B’ inspection during the pressure reduction. • Crystal gauge pressure has been requested to confirm extent of overpressure event. • The LVCR is flagged for rebuild during the LVCR replacement scope of 2019. | HP Distribution | Small OP Event | Yes | No | No | ACE |  | H-14 | GT.STAT.LVCR.0000000174 | 806288 | 56 | 60
OP | 115388527 | Gauge | Diablo | 2018-11-16 21:00 | 230 | 160 | 70 | 43.75% | Gas Contaminants - Sulfur | EQ | P50.7 | Sporadic control from pilot hydrates and sulfur debris. |  | Transmission | Large OP Event | No | No | No | Yes |  | H-14 | GT.STAT.MISC.BYRONTAPRG | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\083679.pdf | 145 | 160
OP | 115388895 | SJ_SMT_RH22 | San Jose | 2018-11-19 11:15 | 55.4 | 55 | 0.4 | 0.7273% | Maintenance Operations Quality | HU |  | During station deactivation, crew closed downstream fire valve to isolate station. |  | HP Distribution | Small OP Event | Yes | No | No |  |  |  | GD.STAT.DISC.00429 |  | 49 | 55
Near Hit | 115410689 | FR_FRE_RD40 | Fresno | 2018-11-17 23:31 | 400.3 | 593 | -192.7 | -32.5% | Failure - Equipment | EQ |  | Poor lockup as a result of moisture and ice inside the pilot. |  | Transmission | Near Hit | [5 empty] | H-14 | GT.STAT.MISC.ASHLANGARF
OP | 115413614 | MiniAT | Stockton | 2018-11-20 09:00 | 225 | 175 | 50 | 28.57% | Failure - Equipment | EQ | P50.5 | Customer went offline with full stop and regulators failed to lock up. |  | Transmission | Large OP Event | No | No | No | Yes |  | H-14 | GT.STAT.MISC.RIPONCOGEN; GT.STAT.LVCR.0000000313 |  | 90 | 100 | 115
Near Hit | 115509864 | ART_PT0028 | North Valley | 2018-12-14 09:12 | 439.15 | 600 | -160.85 | -26.81% | Failure - Equipment | EQ |  | Erratic regulation valves behavior on SCADA was a result of Mark & Locate equipment being left too close to the regulation valves interfering with the transmitter. | The locator was not able to get a signal on the pipe, so an extension lead was connected to the screwdriver and attached to the station fence. | Transmission | Near Hit | Yes | No |  |  |  |  | GT.STAT.MISC.REDDNGTAP_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\183694.pdf
OP | 115524902 | YO_FRB_RC15 | Yosemite | 2018-12-15 10:55 | 92.2 | 60 | 32.2 | 53.67% | Failure - Equipment | EQ | P50.7 | Failure of primary and secondary over pressure protection resulted from debris and manufacturing issue. |  | Transmission | Large OP Event | No | No | No | Yes |  | H-14 | GT.STAT.LVCR.0000000105 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Mer\Tif\Gas\REGSTATION\0805204.PDF | 45 | 50
OP | 115585110 | SA_ELK_RB39_PT3 | Sacramento | 2018-12-19 | 65.2 | 60 | 5.2 | 8.667% | Failure - Equipment | EQ |  | Regualtor failed to lock up, but monitor worked as intended. |  | HP Distribution | Small OP Event | Yes | No | No |  |  | H-14 | GD.STAT.DIST.01339 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Sac\Tif\Gas\RegStation\0809380.PDF | 55 | 58
OP | 115638848 | SSJ_PT0018 | Sacramento | 2018-12-30 15:20 | 801.6 | 800 | 1.6 | 0.2% | Failure - Equipment | EQ |  | Potentially thermal expansion coupled with a small leak and station design. |  | Transmission | Small OP Event | No | No | No |  |  |  | GD.STAT.MISC.SWINGLERMS | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\183987.pdf | 600 | 615
OP | 115705607 | FR_FRE_RA17 | Fresno | 2019-01-17 11:44 | 82 | 60 | 22 | 36.67% | Clearance Preparation | HU | P50.2 | While performing steps as written in clearance #80067690 the crew was manually throttling the downstream fire valve to isolate the station in order to replace/install a sense lines and a ladder when regulation did not catch and reached 82 psig, on the 60 psig MAOP. | • January 17, 2019, District Regulator Station A-17 at N Maple Ave and E Alluvial Ave in Fresno experienced a large overpressure event as the station was being taken out of service for scheduled maintenance under a clearance to relocate SCADA sensing lines. Note: this station was rebuilt a month earlier. • Immediate Actions Taken: Gas Control contacted the PG&E crew performing the clearance with instructions to immediately stop clearance activities and re-open the fire valve. GPOM isolated the station and performed a B-inspection and returned the station back to service • Apparent and Contributing Causes: Clearance writers lack training and understanding of basic gas facility operation and maintenance. Less than adequate guidance provided on gas clearance standards and procedures to take a regulator station out of service when the inlet pressure is greater than the outlet MAOP. | HP Distribution | Large OP Event | Yes | No |  | Yes |  | H-14 | GD.STAT.DIST.11140 | 085930.pdf | 54 | 58
OP | 115760211 | FR_FRE_RB04 | Fresno | 2019-01-27 06:03 | 63 | 60 | 3 | 5% | Gas Contaminants - Liquids | EQ |  | Sulfur filter moisture production | Equipment stand down, temporary variance for installation, communication, vendor discussions. | HP Distribution | Small OP Event | Yes | No |  | ACE |  | H-14 | GD.STAT.DIST.00646 | 0805937.pdf | 54 | 58
OP | 115858633 | NV_RDG_RR31 | North Valley | 2019-02-07 07:30 | 64 | 60 | 4 | 6.667% | Gas Contaminants - Liquids | EQ |  | Gas contaminants and pipeline liquids prohibited proper regulation control. | • MCTL and GPOM responded to the location to determine the cause of the failure, and put the standby run into operation. • Gas Planning provided a list of high flow stations off L-402 (R22, R21, and R42). • Internal inspections of these stations continue as an extent of cause in order to prevent additional overpressure events. • Although this is not a large overpressure event, leak survey may be performed if it is necessary. • CNG/LNG will be engaged in case stations need to be shut-in due to continuing liquids identification. | HP Distribution | Small OP Event | No | No | Yes/Yes |  |  | H-14 | GD.STAT.DIST.00923 | 0807087.PDF | 55 | 58
OP | 116503137 | SEA_PT0001 | Sacramento | 2019-02-20 03:16 | 651.85 | 650 | 1.85 | 0.2846% | Clearance Execution | HU |  | Emergency clearance operations to fix a grade 1 leak resulted in creating a dead-end system. | • V-13 @ Creed was opened so we were not deadheading into a closed valve, the cross tie was in service at creed. The section of L210A from Creed to Fairfield was pre-packed prior to putting M1 into service. We pre-packed this to 630# to try to get a smooth transition from M3 to M1 • It looks like the valve swung when closing MLV 1.37 and transferring the feed from M3 to M1. M1 was set to 620# prior to transferring over the feed, that is 10# under normal operating setpoint giving 30# of separation between the MOP and setpoint. I think we could have opened E. Fairfield first but we don’t think it would have made much difference when transferring the feed. | Transmission | Small OP Event | No | No |  | WGE |  |  | GT.STAT.MISC.EFAIRFIELD |  | X | X
OP | 116684084 | FLV_PT0006 | Stockton | 2019-03-07 12:13 | 431.5 | 412 | 19.5 | 4.733% | Clearance Execution | HU |  | Clearance operations to replace several valves resulted in creating a dead-end system. |  | Transmission | Small OP Event | Yes | No |  |  |  |  | GT.STAT.MISC.LASVNAPLS_ |  | 375 | X
OP | 116711809 | FCT_PT0003 | Yosemite | 2019-03-10 14:12 | 152.1 | 150 | 2.1 | 1.4% | Failure - Equipment | EQ |  | Leaking valves from clearance operations to isolate pressure. | • GPOM technician responded to pressure alarm and confirmed station lock up and SCADA calibration of station. • Clearance was revised to include lowering set points at Burneyville & Riverside, and Santa Fe & Clause. • Isolation valves between systems were opened. | Transmission | Small OP Event | Yes | No |  |  |  |  | GT.STAT.MISC.COFFEECLAR |  | 135 | X
Near Hit |  | K15_PT0032 | Yosemite | 2019-03-12 20:45 | 869 | 890 | -21 | -2.36% | Gas Control Center Operations | HU |  | Gas control inadvertently lowered setpomts causing increase in line pressure inside Panohce Station. | ​Original order was L401 to L300A which was the reason for the cause of OP near hit. The incorrect order was not caught until alarm breach and then corrected to L401 to L300BN. If collaboration was done before order was carried out, this could of been avoided. Multiple training has been issued to control room to always have a path for L401 gas at Panoche otherwise you run risk of OP event. | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.MISC.PANOCHPLS_
OP | 116938286 | Gauge | Kern | 2019-04-02 11:42 | 107 | 60 | 47 | 78.33% | Failure - Equipment | EQ | P50.7 | During customer return to service leaking bypass valve was discovered. | • For most of March, L314A was hydrotested and a large volume customer off that section took a shutdown to perform maintenance. During the return to service it was identified that one of the bypass valves was leaking by, but the regulation equipment controlled and locked up properly. Three days later, GPOM was called out to investigate and identified a large overpressure event downstream of the customer regulation. Equipment was checked, and bypass valves were greased. On April 2, 2019, GPOM was again notified of a second large OP event. • Immediate Actions Taken: Completed A-inspection, installed blind flanges on the bypass valves, confirmed 2 out 3 valves were leaking, and installed a token relief valve. | Transmission | Large OP Event | No | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000230 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\082445.pdf | 45 | 50
OP | 116952002 | KE_BKD_R405 | Kern | 2019-04-03 01:05 | 51.2 | 51 | 0.2 | 0.3922% | Maintenance Operations Quality | HU |  | Control line to the regulator was found to be closed. | GPOM has returned the station back to normal operations. | HP Distribution | Small OP Event | Yes | No |  |  |  | H-14 | GD.STAT.DIST.00617 | 0804877.PDF | 47 | 49
OP | 116963647 & 116959723 | CC_SAL_RS02 | Central Coast | 2019-04-05 01:14 | 60.8 | 60 | 0.8 | 1.333% | Gas Contaminants - Sulfur | EQ |  | Regulator failed to control due to sulfur found in regualtor and pilot. Monitor came into control and operated as intended. | GPOM onsite. FIMP has requested slam-shuts and sulfur filters be installed at this location. | HP Distribution | Small OP Event | Yes | No |  |  |  | H-14 | GD.STAT.DIST.00403 | 0804433.pdf | 54 | X
OP | 117345165 | FLP_PT0004 | Yosemite | 2019-05-30 | 641 | 400 | 241 | 60.25% | Failure - Equipment | EQ | P50.5 | Customer purging and regulators could not control pressure during the rapid shutoff. | GPOM and MCTL onsite | Transmission | Large OP Event | No | No |  | Yes |  | LVCR | GT.STAT.LVCR.0000000258 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0806404.pdf | 280 | 310
OP | 117445540 | MiniAT | Fresno | 2019-06-13 | 80 | 60 | 20 | 33.33% | Failure - Equipment | EQ | P50.7 | Regulating equipment failed to control pressure. | • Confirm MAOP • Potentially retire meter set | Transmission | Large OP Event | No | No | No | Yes |  | H-15 | 0 |  | 55 | 65
OP | 117595394 | FLP_PT0004 | Yosemite | 2019-07-11 20:18 | 470 | 400 | 70 | 17.5% | Failure - Equipment | EQ | P50.7 | Surging of Regulation Equipment | • GPOM responded to the location to determine the cause. • NDE has completed a Borescope Inspection, no debris found. • Engineering, MCTL and GPOM are working to develop a long term solution to improve the existing regulation control. | Transmission | Large OP Event | No | No |  | Yes |  | LVCR | GT.STAT.LVCR.0000000258 |  | 280 | 310
OP | 117602142 | SI_ROC_R399 | Sierra | 2019-07-14 01:18 | 61.5 | 60 | 1.5 | 2.5% | Gas Contaminants - Sulfur | EQ |  | Regulator failed to control due to sulfur found in regualtor and pilot. Monitor came into control and operated as intended. | • GPOM responded to the location to determine the cause. The equipment was inspected and rebuilt, returning to normal operations. • Sulfur Filters will be installed on the control loop to prevent future sulfur build-up on the pilots. | HP Distribution | Small OP Event | No | No |  |  |  | H-14 | GD.STAT.DIST.00953 | 0805899.PDF | 55 | 58
Near Hit | 117632492 | SJ_SJS_RF13 | San Jose | 2019-07-22 09:42 | 517 | 558 | -41 | -7.348% | Clearance Execution | HU |  | While performing step 2 to check-closed crossover valve V-52-F4a as written in clearance #80077988 to isolate district regulator station F-13, the valve inadvertently went passed the stops and leaked by, the valve was recently installed in 2017. | • Responsible engineer to conduct assessment of downstream piping. • MAOP determined to be 558 psig not 400 psig | HP Distribution | Near Hit | No | No |  |  |  | H-14 | GD.STAT.DIST.00460
Near Hit | 117710192 | ST_TRA_RT80_PT1 | Stockton | 2019-07-27 18:38 | 892.5 | 1040 | -147.5 | -14.18% | Failure - Equipment | EQ |  | Valve (V-3) leakage. | No Further actions | Transmission | Near Hit | No | No
Near Hit | 117751072 | KKD_PT0200 | Kern | 2019-08-12 02:00 | 583 | 1000 | -417 | -41.7% | Gas Control Center Operations | HU |  | Gas Control operators initiated flow into a closed valve. | Tailboard Gas Control on Operations and Clearances identification | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.MISC.KRGTPGEDAG
OP | 117749747 | JHW_PT0042 | San Jose | 2019-08-12 11:00 | 254 | 250 | 4 | 1.6% | Failure - Equipment | EQ |  | Regulating equipment failed to control pressure. | • Responsible engineer to conduct assessment of downstream piping. • Replace regulator equipment. | Transmission | Small OP Event | No | No |  |  |  |  | GT.STAT.MISC.HWY101SHLR |  | 235 | 245
OP | 117753819 | MiniAT | Kern | 2019-08-09 18:00 | 85.7 | 60 | 25.7 | 42.83% | Failure - Equipment | EQ | P50.7 | Regulating equipment failed to control pressure. Upon inspection crew discovered tears in the boot. | Gas Pipeline Operations and Maintenance will report onsite to complete the following initial corrective actions: • Install relief valve • Complete Inspections as necessary Additional considerations will be: • Install slam-shut device, and monitoring There is currently a project to replace the bypass valves and address regulation concerns. | Transmission | Large OP Event | No | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000230 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\082445.pdf | 80 | 85
Near Hit | 117809123 | KKT_PT0006 | Fresno | 2019-08-17 | 868 | 900 | -32 | -3.556% | Gas Control Center Operations | HU |  | Gas Control operators initiated flow into a closed valve. | Future interactions will require the following: Coordinator discusses the operational change with the Senior before moving forward. GSO and Coordinator have a brief discussion while they both examine the station configuration prior to executing the order. Coordinator issues the order on the GLS for clarity and documentation. Coordinator and GSO should monitor the execution of this order to assure the equipment is functioning correctly. | Transmission | Near Hit | No | Yes |  |  |  |  | GT.STAT.COMP.KETTLEMAN_
Near Hit | 117809039 | K15_PT0032 | Fresno | 2019-08-21 | 876 | 890 | -14 | -1.573% | Gas Control Center Operations | HU |  | Gas Control operators improperly operated station valves. | Future interactions will require the following: Coordinator discusses the operational change with the Senior before moving forward. GSO and Coordinator have a brief discussion while they both examine the station configuration prior to executing the order. Coordinator issues the order on the GLS for clarity and documentation. Coordinator and GSO should monitor the execution of this order to assure the equipment is functioning correctly. | Transmission | Near Hit | No | Yes |  |  |  |  | GT.STAT.MISC.PANOCHPLS_
Near Hit | 117808536 | THM_PT0112 | Hollister District | 2019-08-23 09:30 | 300 | 304 | -4 | -1.316% | Failure - Equipment | EQ |  | Electrical breaker closed causing unexpected regulator to fail open, monitor took over as intended. | Station team and GPOM to figure out why regulation was lost when the breaker was closed. Revise clearances dependent on station team and GPOM findings. The clearance and process are being reviewed to verify that semiannual breaker exercise is both safe and correct for the future maintenance of the station. | Transmission | Near Hit | Yes | No |  |  | No | H-19 | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
Near Hit | 117825012 | K2B_PT0004 | Kern | 2019-08-29 07:28 | 572 | 574 | -2 | -0.3484% | Gas Control Center Operations | HU |  | Gas Control operator inadvertently changed the set point of the station. | Tailboard Gas Control on Operations and Clearances identification | Transmission | Near Hit | No | Yes |  |  |  | H-19 | GT.STAT.MISC.PLS-2A____
OP | 117844012 | Chart Recorder | Humboldt | 2019-08-16 | 61 | 60 | 1 | 1.667% | Failure - Equipment | EQ |  | Event identified by a chart run, a teardown of the station found sulfur on the regulator boot. | • GPOM responded to the location to perform a ‘B’ inspection on the station. • Lowered the regulation set points by 5 psig to provide more headroom for the MAOP. | HP Distribution | Small OP Event | Yes | No | No |  |  | H-14 | GD.STAT.DIST.01168 | 0805679.pdf | 50 | 55
OP | 117901240 117903194 | SL2_PT0002 | Sacramento | 2019-09-19 09:24 | 502.9 | 500 | 2.9 | 0.58% | Clearance Preparation | HU |  | Downstream valve was closed per Clearance resulting in an inadvertent pressure increase. | • Immediately reduced pressure of the pipe section with 502.9 psig. • Submit a CAP to review future clearance writing procedure. | Transmission | Small OP Event | No | No |  |  |  |  | GT.STAT.MISC.L172L222XT |  | 470 | 495
OP | 117998113 | SA_GRM_SG02 | Sacramento | 2019-10-14 11:00 | 51.79 | 50 | 1.79 | 3.58% | Failure - Equipment | EQ |  | Regulation failed due to debris in the orifice and seat. |  | HP Distribution | Small OP Event | Yes | No |  |  |  | H-10 | GD.STAT.HPRS.00758 | 0800221.pdf | 44 | 50
Near Hit | 118059299 | NV_RDG_S053 | North Valley | 2019-10-16 | 3 | 60 | -57 | -95% | Gas Contaminants - Liquids |  |  | Previously known gas contaminants in the pipeline resulted in slam shut equipment tripping. | • Submit a CAP • Install Gas Control telemetry at the station • NDE station for additional debris • Conduct full B inspection • Install remaining filter/separator prior to full return to service | HP Distribution | Near Hit | No | No |  | Yes | Yes | H-14 | GD.STAT.DIST.00930 |  | SS
OP | 118026345 | Gauge | San Jose | 2019-10-18 10:28 | 80 | 60 | 20 | 33.33% | Clearance Execution | HU | P50.2 | Delayed reaction to pressure change, leading to valve operated to quickly. (FROM the ACE) Valve stuck open during the restoration of repairs at a Farm Tap. | • Responsible engineer to conduct assessment of downstream piping. • Leak Survey and determined no leaks found • Pump test • Meter set regulator replaced | HP Distribution | Large OP Event | No | No | No | Yes | No | H-10 | GD.STAT.FTAP.00161 |  | x | x
OP | 118123950 | Gauge | Topock District | 2019-10-30 | 45 | 32 | 13 | 40.62% | Clearance Preparation | HU | P95.9 | Work package was prepared with incorrect return to service equipment set points. | • Regulator station set point changes • Leak Survey | HP Distribution | Large OP Event | No | No | No | Yes |  | H-10 | GD.STAT.HPRS.10195 | 0804882.pdf | 45 | 50
OP | 118127372 | SI_LMS_R445 | Sierra | 2019-10-31 04:57 | 61.6 | 60 | 1.6 | 2.667% | Gas Contaminants - Liquids | EQ |  | Regulation failed to control pressure due to the liquids and moisture found in the pilot. | • B-inspection & Borescope • NDE to investigate • Slam Shut installation • Removing Debris prior to returning to service | HP Distribution | Small OP Event | No | No | Yes/Yes |  |  | H-14 | GD.STAT.DIST.00958 | 0805905.pdf | 55 | 58
OP | 118128269 | PN_SM_RA77 | Peninsula | 2019-10-31 15:20 | 62 | 60 | 2 | 3.333% | Failure - Equipment | EQ |  | Regulation failed to control pressure. | Replace equipment | HP Distribution | Small OP Event | No | No |  | No | No | H-10 | GD.STAT.FTAP.04141 |  | 40 | 50
OP | 118147673 | SSA_PT0009 | Sacramento | 2019-11-05 11:07 | 268 | 260 | 8 | 3.077% | Clearance Execution | HU |  | Downstream station valve was opened quickly resulting in an inadvertent pressure increase to a dead-end section of pipe | • It is important to have situational awareness when opening valves with large pressure differentials. • Full Rebuild of station D-40 (PM74022060). | Transmission | Small OP Event | Yes | No |  |  |  | H-14 | GD.STAT.DIST.01090 | \\fairfield07\gis\giswebMiscFiles\GasStations\385186.pdf | 240 | 265
OP | 118155550 | SA_ESP_S045 | Sacramento | 2019-11-08 | 55.29 | 55 | 0.29 | 0.5273% | Gas Contaminants - Liquids | EQ |  | Regulation failed to control pressure due to the liquids and moisture found in the pilot. | Perform B inspection, NDE borescope | HP Distribution | Small OP Event | No | No | Yes/Yes |  |  | H-14 | GD.STAT.DIST.01128 | WI-01 | 49 | 53
OP | 118197814 | MiniAT | Fresno | 2019-11-09 | 79 | 60 | 19 | 31.67% | Failure - Equipment | EQ | P50.7 | Regulation failed to control pressure due to the debris in the regulation. | • Per FIMP risk - no additional data has been gathered on the MAOP of this section. | Transmission | Large OP Event | No | No | No | Yes |  | H-15 | 0 |  | 55 | 60
OP | 118190702 | CC_HST_S001 | Hollister District | 2019-11-20 04:42 | 84 | 60 | 24 | 40% | Clearance Preparation | HU | P95.9 | Work package was prepared with incorrect sense line configuration. | • MCTL report onsite to perform B Inspection. • NDE to perform station Borescope at H-64. • Leak survey performed per hydraulic analysis of the Hollister HIS (~1400 services). • Independent sense lines will be installed for each pressure control device (regulator and monitor). • The station will be assessed for potential rebuild. • Regulation Engineering, MCTL, and DPM&E will collaborate on a more permanent solution. | HP Distribution | Large OP Event | No | No | Yes/Yes | Yes |  | H-14 | GD.STAT.DIST.00397 | 0807396.pdf | 53 | 58
OP | 118202752 | BMA_PT0002 | Tracy District | 2019-11-25 06:14 | 376.73 | 365 | 11.73 | 3.214% | Failure - Equipment | EQ |  | Regulation failed to control pressure due to diaphragm/boot failure. | • GPOM currently onsite to determine the cause - delamination on diaphragm • NDE to investigate with borescope - minimal debris, tar like substance identified | Transmission | Small OP Event | No | No | Yes/Yes |  |  | H-14 | GT.STAT.MISC.MCCARTHUR_ | 081666.pdf | 325 | 340
OP | 118207557 | SI_ROC_R410 | Sierra | 2019-11-26 20:45 | 64.9 | 60 | 4.9 | 8.167% | Gas Contaminants - Liquids | EQ |  | Regulation failed to control pressure due to the liquids and moisture found in the pilot. | • MCTL & GPOM responded to address overpressure • Isolate lead run to perform further investigation, switch to stand-by run • Station to remain shut-in over the weekend per Gas Planning/Gas Control approval • NDE performed borescope and identified liquids in the intermediate pipe on lead run • Previously installed slam shuts to protect downstream system • Assess station for installation of working monitor, and installation of filter/separator DA-6 on all regulator pilots | HP Distribution | Small OP Event | Yes | No |  |  |  | H-14 | GD.STAT.DIST.00956 | 805903 | 55 | x
OP | 118240107 | MiniAT | Kettleman District | 2019-12-04 01:10 | 120 | 60 | 60 | 100% | Failure - Equipment | EQ | P50.7 | Regulation failed to control pressure. | • FIMP Risk engineer to conduct assessment of downstream piping. • Perform leak survey on the meter set. • Potentially confirm bypass valve is not leaking by leaving chart. | Transmission | Large OP Event | No | No | No | Yes |  | H-15 | GT.STAT.LVCR.0000000615 |  | 35 | 40
OP | 118231052 | MMT_PT00083 | Milpitas District | 2019-12-03 10:25 | 301 | 300 | 1 | 0.3333% | Clearance Execution | HU |  | During pigging clearance valve operations induced operating valves into a dead-end system | • Evaluate additional steps to eliminate pressure control issues. | Transmission | Small OP Event | No | No |  |  |  | H-19 | GT.STAT.MISC.MLPTSTPLM_ | 383510.pdf | 285 | x
OP | 118231054 | SI_OH_X109 | Sierra | 2019-12-04 01:10 | 65.53 | 60 | 5.53 | 9.217% | Gas Contaminants - Liquids | EQ |  | Regulation failed to control pressure due to the liquids and moisture found in the pilot. | • MCTL & GPOM responded to address overpressure • Isolate lead run to perform further investigation, switch to stand-by run • NDE to perform borescope on both runs • Install filter/separator DA-6 on pilots and pilot heaters | Transmission | Small OP Event | No | No | Yes/Yes |  |  | H-14 | GT.STAT.LVCR.0000000109 | 0809533 | 15 | 18 | yes
OP | 118409154 | SJ_SJS_RF33 | San Jose | 2020-01-08 22:15 | 62.4 | 60 | 2.4 | 4% | Maintenance Operations Quality | HU |  | Rapidly isolated main directly downstream of the station (F-33) resulting in an inadvertent pressure increase. | • Tailboard best practices and reiterate the squeeze step is to be performed slowly. Gradually squeezing until the pressure drops. • GPOM will provide supervision to assist with GC to complete clearance 80092910. | HP Distribution | Small OP Event | No | No |  |  |  | H-14 | GD.STAT.DIST.00467 | 0808151.pdf | 57 | 60
OP | 118409611 | SA_FRF_RR62 | Sacramento | 2020-01-09 11:42 | 54 | 50 | 4 | 8% | Gas Contaminants - Liquids | EQ |  | Regulation failed to control pressure due to the liquids and moisture found in the pilot. | Initial Corrective Actions, Long-term Corrective Actions, if available • NDE to perform borescope to identify additional liquids. • Station to be shut in until borescope is performed and further investigation is completed. • Stain tube sample was pulled. | HP Distribution | Small OP Event | No | No |  |  |  | H-14 | GD.STAT.DIST.01342 | 0809315.pdf | 44 | 48
OP | 120650090 | MiniAT | San Jose | 2020-01-24 | 330.9 | 330 | 0.9 | 0.2727% | Design/Process* | EQ |  | During a review of MiniAT data it was determined that this overpressure event occurred. | N/A | Transmission | Small OP Event | No | No | No |  |  | H-15 | GT.STAT.LVCR.0000000267 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0800689.pdf | float | float
OP | 118475986 | MiniAT | Sonoma | 2020-01-28 11:00 | 151.4 | 150 | 1.4 | 0.9333% | Failure - Equipment | EQ |  | Deactived service leaks were repaired resulting in a deadend system. | • Station to be shut in until further investigation is completed. • Evaluate for deactivation | Transmission | Small OP Event | No | No | No |  |  | H-10 | GT.STAT.LVCR.0000000183 | 0800590 | 145 | 150
OP | 118492422 | FLP_PT0004 | Yosemite | 2020-02-03 05:10 | 418.82 | 400 | 18.82 | 4.705% | Failure - Equipment | EQ |  | Liberty Packing returned to service resulting in an inadvertent pressure increase. | • GPOM & MCTL report onsite and check lockup and operation of equipment. • GPOM to meet with Liberty Packing personnel to discuss future corrective actions surrounding Liberty plant start-up operation. • GPOM to contact plant engineer to discuss verification of MAOP values for Liberty Packing. • Further investigation required with division PLE and Plant engineer. | Transmission | Small OP Event | No | No |  |  |  | H-14 | GT.STAT.LVCR.0000000258 | 0806404.pdf | 280 | 310
OP | 118499724 | HU_ARC_RR09 | Humboldt | 2020-02-04 13:30 | 44 | 40 | 4 | 10% | Clearance Preparation | HU |  | Work package was prepared that did not identify tie-in of differing MAOPs. Clearance process did not identify MAOP difference. | • Leak Survey • Evaluate the necessity of a pressure test on the main and service to the Mobile Home Park. • Station Engineering to run an SAP query to flag projects with bottom taps. The identified projects will be reviewed, and construction will be notified in case of changes. • A causal evaluation to be performed to identify and review all concerns related to this incident in the design, clearance and execution phases of this project. Design: • When tying two systems together, add detailed notes to design drawings about specific hydraulic independent systems (HIS) names and MAOP on mains and services impacted by the project. • When tying two systems together, add a critical note for field execution to work with GPOM to verify/monitor relief valve set point versus the new delievery pressure to minimize/eliminate gas release. • Process Safety will be engaged to update the PHA checklists for HPR projects Other: • The clearance and execution process controls to be reviewed in the cause evaluation. | HP Distribution | Small OP Event | No | No |  |  |  | H-10 | GD.STAT.HPRS.00779 |  | 55 | 58
OP | 118505829 | Gauge | Peninsula | 2020-02-07 | 197.13 | 175 | 22.13 | 12.65% | Failure - Equipment | EQ | P50.7 | Leaking check valve (customer owned) during periods of low/zero gas demand. Pressure confirmed with MiniAT (AIS2388). | • Customer will isolate the section of piping with the leaking check valve and will inform GPOM when repairs are complete. • GPOM to perform weekly checks of the pressure data to ensure the customer equipment is operating correctly. • PG&E to investigate adding additional equipment to prevent over pressurization by the customer. | Transmission | Large OP Event | No | No | No | Yes |  | H-15 | GT.STAT.LVCR.0000000505 | 0812689.pdf | 120 | 130
OP | 118518787 | SYC_PT0011 | Sierra | 2020-02-06 08:47 | 805.29 | 800 | 5.29 | 0.6612% | Failure - Equipment | EQ |  | Leaking valves from clearance operations to isolate pressure. | • The valve V-43 was replaced that same day 02/06/2020. • Confirm pressure increase with further test. | Transmission | Small OP Event | No | Yes |  |  |  | H-19 | GT.STAT.MISC.YUBACITYUH | 284091.pdf | x | x
OP | 118537638 | SJ_SJS_RF02 | San Jose | 2020-02-14 11:36 | 62.03 | 60 | 2.03 | 3.383% | Design/Process* | EQ |  | Regulation failed to control pressure after a third party operated the downstream fire valve. | • GPOM to perform B inspection to confirm equipment was not the cause of the event. | HP Distribution | Small OP Event | Yes | No | No |  |  | H-14 | GD.STAT.DIST.00453 | 0804517.PDF | 56 | 58
OP | 118779581 | SA_RVS_S050 | Sacramento | 2020-02-17 05:30 | 46.74 | 46 | 0.74 | 1.609% | Failure - Equipment | EQ |  | Regulation failed to control pressure due to tear/hole in the regulator diaphragm. | • GPOM checked lockup and operation of all equipment including, both monitors, both regulators and the first stage cut. • B-inspection performed, regulator boot replaced. • Fill out an MPR for the regulator boot that failed. | HP Distribution | Small OP Event | Yes | No |  |  |  | H-14 | GD.STAT.DIST.01102 | 0804220.PDF | 38 | 44
OP | 118576487 | Gauge | San Jose | 2020-02-24 09:45 | 56.6 | 55 | 1.6 | 2.909% | Gas Contaminants - Sulfur | EQ |  | Regulation failed to control pressure due to identified sulfur on the equipment. | • Consider lowering the standby regulator set point and monitor set points below the MAOP. • Check lock up and confirm bypass valve is not leaking by. | HP Distribution | Small OP Event | Yes | No | No |  |  | H-14 | GD>STAT.DIST.00434 | 0811184.PDF | 52 | 55
Near Hit | 118574680 | THM_PT0110 | Hollister District | 2020-02-20 13:06 | 485.22 | 500 | -14.78 | -2.956% | Maintenance Operations Quality | HU |  | AS described by the technician, this station is challenging to maintain without hitting an alarm |  | Transmission | Near Hit | No | No |  | No | No | H-19 | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
OP | 118604570 | MiniAT | Central Coast | 2020-03-04 12:00 | 61.98 | 60 | 1.98 | 3.3% | Gas Contaminants - Sulfur | EQ |  | Regulation failed to control pressure due to identified sulfur on the equipment. | • The set points of the regulator and monitor were lowered to 56 psig, and 59 psig respectively. | Transmission | Small OP Event | No | No | No |  |  | LVCR | GT.STAT.LVCR.0000000166 | 0809588 | 54 | x
OP | 118649351 | THM_PT0110 | Hollister District | 2020-03-06 10:00 | 569.29 | 304 | 265.29 | 87.27% | Clearance Execution | HU | P50.2 | Manual clearance operations during sense line leak repair return to service. | • Additional GPOM district technicians currently on route. • Leak Survey has been scheduled on L-301A from Hollister Station to Moss Landing Power Plant. • Gas Control has initiated a pressure reduction on L-301A | Transmission | Large OP Event | No | No |  |  |  | H-19 | GT.STAT.MISC.HLLSTRPLS_ | 282255.pdf | x | x
Near Hit | 120113515 | MiniAT | Yosemite | 2020-03-09 | 106 | 125 | -19 | -15.2% | Gas Contaminants - Sulfur | EQ |  | Regulation failed to control pressure due to identified sulfur on the equipment. Regulation failed to control pressure after a third party operated the downstream fire valve. | • GPOM will install a token relief valve. • Customer requested to be shut-in maintenance and leak test. • Replace the MiniAT. | Transmission | Near Hit | No | No |  |  |  |  | GT.STAT.LVCR.0000000685 | 0812720.pdf | 20 | 25
OP | 118710571 | KAM_PT0001 | Fresno | 2020-03-16 06:47 | 500 | 498 | 2 | 0.4016% | Failure - Equipment | EQ |  | Regulator failed to lock-up due to sulfur build-up, so the Monitor took control. Downstream customer abruptly shutdown. | • GPOM replaced the rubber goods in the regulator and successfully tested the monitor for lock-up. | Transmission | Small OP Event | No | No |  |  |  | H-14 | GT.STAT.MISC.COALINGATP | 082494.pdf | 478 | 493
OP | 118710697 118711748 | KE_BKD_R119 | Kern | 2020-03-16 10:47 | 12.47 | 12 | 0.47 | 3.917% | Maintenance Operations Quality | HU |  | Inadvertent pressure increase while throttling the bypass valve during an “A” inspection. | • GPOM has returned the station back to normal operating conditions. • GPOM will regroup and return to the station to complete the “A” Inspection | LP Distribution | Small OP Event | No | No |  |  | No | LPRS | GD.STAT.LPRS.00148 | 0804701.PDF | 9 | 10.5 | 14
OP | 118748521 | MiniAT | Kern | 2020-03-26 05:15 | 62.34 | 60 | 2.34 | 3.9% | Gas Contaminants - Liquids | EQ |  | Regulation failed to control pressure due hydrates/ice found in the pilot which resulted in the slam shut activation. | • GPOM reset slam shuts equipment and returned the station to service. • Per the recent 5MM, GPOM is to remove the sulfur filter cartridges as the potential cause to the hydrate formation and freezing in the pilots. | Transmission | Small OP Event | No | No | No |  | Yes | LVCR | GT.STAT.LVCR.0000000153 | 0809575.pdf | 5 | 7
OP | 118915610 | NV_RDG_RR20 | North Valley | 2020-04-11 | 60.59 | 60 | 0.59 | 0.9833% | Gas Contaminants - Debris | EQ |  | Regulation failed to control pressure due to debris found on the regulator and monitor. | • GPOM performed a “B” Inspection and returned the station back to normal operating conditions. • Division submitted Corrective Notification to add a Filter/Strainer which would mitigate further debris buildup at the station. | HP Distribution | Small OP Event | No | No |  |  |  | H-10 | GD.STAT.HPRS.10294 | 0809575.pdf | 50 | 55
OP | 119079521 | MiniAT | Central Coast | 2020-05-27 07:00 | 60.36 | 60 | 0.36 | 0.6% | Gas Contaminants - Sulfur | EQ |  | Regulation failed to control pressure due to identified sulfur on the equipment. | GPOM resolved immediate equipment concerns. S-1024 has a planned clearance start date/MOB of 7/15/2021 - reduce regulator set points, and install token RV | Transmission | Small OP Event | No | No | No |  |  | H-15 | GT.STAT.LVCR.0000000166 | 0809588 | 54
OP | 119088546 | MiniAT | Yosemite | 2020-05-31 14:00 | 64.32 | 60 | 4.32 | 7.2% | Failure - Equipment | EQ |  | Regulating equipment failed to control pressure. | • GPOM checked for lock up at the customer location, and regulator station upstream. • The relief valve set point from 55 psig to 50 psig. • 60-day audit trail will be pulled. • Filter will be checked for liquid intrusion. | HP Distribution | Small OP Event | No | No | No |  |  | H-14 | GD.STAT.DIST.00695 | 0807279.PDF | 40 | 50
OP | 119107816 | SHS_PT0026A | Willows District | 2020-06-04 06:17 | 985 | 975 | 10 | 1.026% | Clearance Execution | HU |  | Manual clearance operations on an isolated section of pipe where sense lines were tied in preparation for pigging. | Project teams will be reviewing the following corrective actions for the upcoming pigging runs on L-400:• Control pressure with V-4, which is located upstream of V-3. • Lower L-400 pressure from Delevan Compressor Station to Buckeye Creek Station. • Temporarily relocate control lines for V-3 and V-A for the duration of the pigging operations. | Transmission | Small OP Event | No | No |  |  |  |  | GT.STAT.MISC.BCKEYEPLS_ | 082472.pdf | 900
OP | 119144634 | FLP_PT0004 | Yosemite | 2020-06-10 | 651.2 | 400 | 251.2 | 62.8% | Failure - Equipment | EQ | P50.5 | Liberty Packing returned to service resulting in an inadvertent pressure increase. | • More information will be available: Potentially, GPOM to meet with Liberty Packing personnel to discuss future corrective actions surrounding Liberty plant start-up operation. • Further investigation required with division PLE and Plant engineer. | Transmission | Large OP Event | No | No |  |  |  | LVCR | GT.STAT.LVCR.0000000258 | 0806404.pdf | 280 | 310
OP | 119170752 | PN_MLP_DR93 | Peninsula | 2020-06-13 | 42.8 | 40 | 2.8 | 7% | Maintenance Operations Quality | EQ |  | Inadvertent sense line valve operation resulted in pressure surge. Downstream block valve was closed and did not result in system overpressure. | GPOM to investigate | HP Distribution | Small OP Event | Yes | No |  |  |  | H-14 | GD.STAT.DIST.00139 | 0804057.PDF | 35 | 38
OP | 119295179 | MI_HAY_RH02 | Mission | 2020-06-25 10:43 | 308.5 | 250 | 58.5 | 23.4% | Clearance Execution | HU | P50.7 | CE: Clearance. DC: Valve leakage at the inlet valve lead to pressure increases |  | Transmission | Large OP Event | No | No |  |  |  | H-14 | GD.STAT.DIST.00252; GD.STAT.DIST.00241 | 0804616.PDF | x | x
OP | 119341612 | YO_LBN_RC03 | Yosemite | 2020-07-09 | 60.25 | 60 | 0.25 | 0.4167% | Failure - Equipment | EQ |  | Regulating equipment failed to control pressure. |  | HP Distribution | Small OP Event | Yes | No |  |  |  | H-14 | GD.STAT.DIST.01400 | 0806533.PDF | 54 | 58
Near Hit | 119432267 |  | Diablo | 2020-07-11 |  |  |  |  | Slam shut activation | EQ |  | overpressure elimination is tracking slam shut activations, as near hits that were prevented by the activation. |  | Transmission | Near Hit | No | No | Yes | No | Yes | H-14 | GT.STAT.MISC.RELIEZREGL | 083692.pdf
OP | 119378227 | MiniAT | Yosemite | 2020-07-14 | 61.46 | 60 | 1.46 | 2.433% | Failure - Equipment | EQ |  | Regulators could not control pressure during the customer rapid shutoff. | GPOM installed a token relief valve with a 50 psig set point to alleviate similar issues in the future. | Transmission | Small OP Event | Yes | No | No |  |  | H-15 | GT.STAT.LVCR.0000000668 |  | 40 | 46 | 50
OP | 119479109 | KT2_PT0100A | Kern | 2020-07-17 15:57 | 671.7 | 660 | 11.7 | 1.773% | Failure - Equipment | EQ |  | Automated cross-tie control valve inadvertently closed causing pressure increase. |  | Transmission | Small OP Event | No | Yes |  |  |  | H-19 | GT.STAT.COMP.TOPOCK | 383655 | x | x
OP | 119518807 | CC_APT_RJ44 | Central Coast | 2020-07-27 | 38.9 | 30 | 8.9 | 29.67% | Maintenance Operations Quality Gas Control Operations Equipment Failure | HU | P50.2 | CE: SS FCO failed to inhibit alarm EQ: Spurious SS trip. DC: Pressure increased while throttling the bypass valve to support dropping pressure in the HIS. | • GPOM has returned the station back to normal operating conditions. • Existing restrictor plates to be replaced with 75% reduced flow plate at station. • 2” Mooney Slam shut to be replaced. • MCTL to conduct testing on Slam shut. | HP Distribution | Large OP Event | No | No |  | Yes |  | H-14 | GD.STAT.DIST.00520 | 0806503.PDF | 27 | 29
OP | 119618698 | MiniAT | Fresno | 2020-07-31 | 459 | 250 | 209 | 83.6% | Failure - Equipment | EQ | P50.7 | Leaking bypass valve |  | Transmission | Large OP Event | No |  |  | Yes |  | H-15 | GT.STAT.LVCR.0000000251 |  | 225 | 250
OP | 119567547 | FFN_PT0002 | Fresno | 2020-08-05 11:43 | 598.6 | 400 | 198.6 | 49.65% | Maintenance Operations Quality | HU | P50.2 | Pressure surged during the return to service operations. | • Technicians took quick action to isolate the header within the station and blew down the header pipe. • A temporary reduction in pressure was instituted to reduce the MAOP by 20% to 304 psig. • Leak survey completed over the impacted area. • There is a project in place to rebuild Fresno GLC. | Transmission | Large OP Event | No | No |  | Yes |  | H-14 | GT.STAT.MISC.FRESNOLOAD | 3808517.pdf | 380 | 395
OP | 119618698 | MiniAT | Fresno | 2020-08-13 12:00 | 459 | 250 | 209 | 83.6% | Failure - Equipment | EQ | P50.7 | Leaking bypass valve | • Station made safe. • Regulator was rebuilt. • Bypass regulator will be removed and replaced with blind flange. | Transmission | Large OP Event | No | No | No | Yes |  | H-15 | GT.STAT.LVCR.0000000251 |  | 225 | 250
Near Hit | 119667096 | MiniAT | East Bay | 2020-08-21 | 124.9 | 125 | -0.1 | -0.08% | Failure - Equipment | EQ |  | Customer personnel closed a valve causing a rapid increase in pressure. | GPOM performed a "B" Inspection and returned the station back to normal operating conditions. GPOM performed a soap test at the site. GPOM to replace meter. Token Relief Valve to be installed. | Transmission | Near Hit | Yes | No |  | No |  | H-14 | GT.STAT.LVCR.0000000371 | 804741
OP | 119683226 | MiniAT | Fresno | 2020-08-26 09:00 | 63.6 | 60 | 3.6 | 6% | Failure - Equipment | EQ |  | Regulation failed to control pressure during a customer shut-down due to wear on the regulator seat. | GPOM performed "B" Inspection, regulator seat replaced. | Transmission | Small OP Event | Yes | No | No |  |  | H-15 | 0 |  | 53 | 58
Near Hit | 119696894 | MiniAT | Yosemite | 2020-08-28 | 102.28 | 125 | -22.72 | -18.18% | Low Demand | N/A |  | High temperatures and low demand caused an increase in pressure. | GPOM performed a "B" Inspection and returned the station back to normal operating conditions. GPOM performed a soap test at the site. GPOM to replace meter. | Transmission | Near Hit | Yes | No |  | No |  | H-15 | 0
OP | 119697018 | CC_SAL_S088 | Central Coast | 2020-08-28 | 61.38 | 60 | 1.38 | 2.3% | Gas Contaminants - Debris | EQ |  | Regulation failed to control pressure due to debris found in the station equipment. | GPOM performed an “B” Inspection and returned the station back to normal operating conditions. NDE has completed a Borescope Inspection, no further debris found. | HP Distribution | Small OP Event | No | No | Yes/No |  |  | H-14 | GD.STAT.DIST.00417 | 807420 | 56 | 58
OP | 119727251 | SJ_SJS_RG55 | San Jose | 2020-09-08 | 232 | 60 | 172 | 286.7% | Clearance preparation | HU | P95.8 | Leaking valve from clearance operations caused downstream pressure increase. | Blow down the intermediate pipe to 5 psig. Determine which valves are leaking. Check regulators for lock-up. Leak Survey the downstream pipe (approximately 30'). | HP Distribution | Large OP Event | No | No |  | Yes |  | H-14 | GD.STAT.DIST.00491 | 809690 | 51 | 56
OP | 119824028 | YO_NEW_S025 | Yosemite | 2020-09-27 | 53.42 | 50 | 3.42 | 6.84% | Maintenance Operations Quality | HU |  | Both the short and long sense lines were found to be simultaneously open causing the monitor to erratically control pressure. | GPOM performed a “B” Inspection and returned the station back to normal operating conditions. Further investigation may be required to determine why the short line was left open. | HP Distribution | Small OP Event | Yes | No | No |  |  | H-14 | GD.STAT.DIST.00760 | 809190 | 44 | 48
OP | 119829827 | MiniAT | Fresno | 2020-09-27 19:00 | 75.57 | 75 | 0.57 | 0.76% | Failure - Equipment | EQ |  | Regulation failed to control pressure due to a hole in the primary regulator diaphragm. | GPOM checked lockup and operation of all equipment. GPOM performed a ”B” Inspection to the regulator and returned the station back to normal operating conditions. Fill out an MPR for the regulator boot that failed. Engineering to evaluate if the proper equipment is installed for the pressure differential. | Transmission | Small OP Event | Yes | No | No |  |  | H-15 | GT.STAT.LVCR.0000000409 | 812128 | 60 | 75
OP | 119878071 | KE_BKD_R103 | Kern | 2020-10-09 11:15 | 327.3 | 300 | 27.3 | 9.1% | Maintenance Operations Quality | HU |  | During the return to service and restoration of pressure after multiple clearances a multiturn valve was not returned to its position. | - Valve testing to confirm leakage, valve position and valve condition. - Confirmation that clearance steps were executed in sequence. - Assess updating the current clearances into one document. - Attempt to locate temporary replacement diaphragms for regulation at Gosford Station. - Evaluate capacity concerns for return to service of Gosford Station. - Shut-in Gosford Rd Station, and feed L-142S from Bakersfield tap and L-142N. If necessary, GPOM will attend to the station until it can be shut-in. X1857 | Transmission | Small OP Event | No | No |  | Yes |  | H-19 | GT.STAT.MISC.BRUNDAGELN | 83802 | x | x
OP | 119893542 | BRT_PT0065 | Diablo | 2020-10-09 16:06 | 737.1 | 722 | 15.1 | 2.091% | Failure - Equipment | EQ |  | Pressure fluctuations occurred while both the regulator and the monitor control valves were actuating. | More investigation may be necessary to determine corrective actions. | Transmission | Small OP Event | No | No |  |  |  | H-19 | GT.STAT.MISC.BRNTWDPLS_ | 384748.pdf | x | x
OP | 119924577 | YO_CRL_S090 | Tracy District | 2020-10-18 23:02 | 56.4 | 56 | 0.4 | 0.7143% | Clearance Preparation | HU |  | Records | set points lowered from 52 to 48 psig - completed on the field. | HP Distribution | Small OP Event | Yes | No |  |  |  | H-10 | GD.STAT.HPRS.11242 |  | 52 | x
OP | 119926969 | NV_ORB_R057 | North Valley | 2020-10-19 04:39 | 60.45 | 60 | 0.45 | 0.75% | Gas Contaminants - Sulfur | EQ |  | Erratic control of the equipment was caused by sulfur on the diaphragm. | B-inspection to replace diaphragm on working run – completed during op response. Reduced set points from 58/55 psig to 57/52 psig – completed during op response. | HP Distribution | Small OP Event | Yes | No |  |  |  | H-14 | GD.STAT.DIST.00895 | 0806922.PDF | 55 | 58
OP | 119943167 | YO_CRL_S090 | Tracy District | 2020-10-23 | 61.45 | 56 | 5.45 | 9.732% | Gas Contaminants - Sulfur | EQ |  | Sulfur was identified on the regulator pilots. | MAOP Engineering is processing the event to understand if the MAOP is 56 psig, or 58 psig, based on operating diagram discrepancies. – In progress The station was rebuilt, with rubber goods, and internal components replaced. – Complete | HP Distribution | Small OP Event | Yes | No |  |  |  | H-10 | GD.STAT.HPRS.11242 |  | 48 | 52
OP | 120120386 | KE_BKD_R119 | Kern | 2020-12-02 | 14.06 | 12 | 2.06 | 17.17% | Failure - Equipment | EQ |  | Pressure increased after low downstream demand to regulator set. | • GPOM shut-in the station closing inlet and outlet valves and removing bypass. • Station to be formally decomissioned on 12/7. • GC will regroup and finish converting the last three services from low pressure to high pressure on 12/2/2020. • Leak survey is not required because the main is being shut-in and deactivated. • All services that saw an MAOP excursion will have an appliance safety check at time of restoration. | LP Distribution | Small OP Event | Yes | No | No |  | Yes | H-14 | GD.STAT.LPRS.00418 |  | 9 | 10.5 | 14
Near Hit | N/A | AWD_PT0001 | North Valley | 2020-12-04 | 1056.2 | 1200 | -143.8 | -11.98% | Clearance Execution | HU |  | An outlet block valve was closed resulting in a temperature-driven expansion of trapped gas and breach of the MOP alarm threshold. | • GPOM returned the station to normal operating conditions. • No further action is required at this time. | Transmission | Near Hit | Yes | No |  | No |  |  | GT.STAT.MISC.WLDGSEPLS_ | 0803161.pdf
OP | 120201167 | RMO_PT0002 | North Coast | 2020-12-12 | 205.8 | 200 | 5.8 | 2.9% | Maintenance Operations Quality | HU |  | Adjusting the lag run during semi-annual maintenance caused a pressure increase. | • | Transmission | Small OP Event | Yes | No |  |  |  | H-14 | GT.STAT.MISC.MONROEREGS | 081915.pdf | 190 | 195
OP | 120228202 | YO_FRB_RC_15 | Yosemite | 2020-12-21 06:01 | 61.9 | 60 | 1.9 | 3.167% | Gas Contaminants - Sulfur | EQ |  | Regulation failed to control pressure due to sulfur on the boots of the regulation equipment. | • GPOM performed an internal inspection on both the regulator and monitor. Presence of sulfur was found on both boots of the regulation equipment which prohibited lockup on the regulator, prompting GPOM to replace the boots. • Set points were re-established to the correct settings. • Control and lock-up tests for regulation were performed before primary regulation set was put back into service. • Due to discrepancies between the slam shut set point and ERX data, additional testing by GPOM at this site has been requested from Regulation Engineering. • GPOM to work with Gas Control to bring slam shut into the control center. • A token relief valve has been installed at this location. | HP Distribution | Small OP Event | No | No |  |  |  | H-14 | GT.STAT.LVCR.0000000105 | 0805204.PDF | 45 | 55
OP | 120262229 | SJ_GIL_SH65 | San Jose | 2021-01-05 21:17 | 50.51 | 50 | 0.51 | 1.02% | Gas Contaminants - Sulfur | EQ | P5.1 | Regulation failed to control pressure due to sulfur identified on the equipment and worn seat. | o GPOM responded to address sulfur issues on the orifice and seat. o Additional testing to occur with MCTL, with consideration to replace the regulation equipment. o Assess adjacent stations off Line 300A for sulfur contamination. | HP Distribution | Small OP Event | No | No | No | No |  | H-10 | GD.STAT.HPRS.11169 | 0808387.pdf | 40 | 44
OP | 120501378 | FR_FRE_EX11_PT2, FR_FRE_EX12_PT4, & FR_FRE_S032 | Fresno | 2021-02-04 | 64 | 60 | 4 | 6.667% | Gas Contaminants - Liquids | EQ | P5.1 | Regulation equipment failed to control pressure due to liquids found in the pilot. | • GPOM performed a B-Inspection and returned the station to normal operating conditions. • NDE team to perform a borescope. • MCTL will assess whether pilot heaters should be added to prevent liquids in the pilots. | HP Distribution | Small OP Event | No | No | Yes/No | No |  | H-14 | GD.STAT.DIST.01424 | 0806679.pdf | 54 | 58
OP | 120507369 | SWC_PT0004 | Diablo | 2021-02-06 15:00 | 100.8 | 100 | 0.8 | 0.8% | Gas Contaminants - Debris | EQ | P5.1 | Regulation failed to control pressure due to debris found in the station equipment. | • GPOM performed a B-Inspection and identified slag between the diaphragm and grid plate. • NDE team performed a borescope and identified additional weld slag, which was removed prior to returning the station to service. • Further assessment of additional internal pipe cleaning may be required. | Transmission | Small OP Event | No | No | Yes/Yes | No |  |  | GT.STAT.MISC.WALNUTAVER | 083125.pdf | 90 | 95
OP | 120511361 | YO_LVT_M002 | Yosemite | 2021-02-09 07:53 | 60.6 | 60 | 0.6 | 1% | Gas Contaminants - Debris | EQ | P5.1 | Regulation failed to control pressure due to debris found in the station equipment. Slam shut activation equipment operated as intended. | • GPOM performed a B-Inspection and identified slag between the diaphragm and grid plate. • NDE team performed a borescope and identified additional weld slag, which was removed prior to returning the primary set back to service. | Transmission | Small OP Event | No | No | Yes/Yes | No | Yes | 2 | GT.STAT.LVCR.0000000148 | 0809570.pdf | 30 | 40 | 60
OP | 120556445 | Gauge | Sierra | 2021-02-19 00:03 | 556 | 525 | 31 | 5.905% | Failure - Equipment | EQ | P5.1 | Valve leakage from clearance operations into an isolated section of pipe. | The crew took immediate action to reduce the pressure below the MAOP. A leak survey will be conducted on the affected pipe, which resulted in no leaks. | Transmission | Small OP Event | No | No |  |  |  | H-19 | GT.STAT.MISC.YUBACITYUH | 284091.pdf | 325 | 390
OP | 120569212 | THM_PT0110 | Central Coast | 2021-02-23 14:06 | 410.8 | 396 | 14.8 | 3.737% | Maintenance Operations Quality | HU | P5.1 | Pressure increased while performing annual control valve maintenance. | • GPOM to further assess and investigate root cause. | Transmission | Small OP Event | No | No |  |  | No | H-19 | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
OP | 120584490 | MiniAT | Stockton | 2021-02-27 | 62 | 60 | 2 | 3.333% | Gas Contaminants - Debris | EQ | P5.1 | Regulation failed to control pressure due to debris, liquids, and moisture found in the station piping. | • Removed all debris/liquids and dried pipeline. • Slam shut set points lowered from 64 psig to 62 psig and 60 psig respectively. • Installed a portable ERX (MI_ERE_ER10_PT1). • Identification of remaining liquids in Line 2 from past cleaning operations. • Engineering to evaluate rebuilding or retiring the station. • Review any other Slam Shut sites that do not have control room visibility. | HP Distribution | Small OP Event | No | No | Yes/Yes | No |  | H-14 | GD.STAT.DIST.00864 | 0804914.PDF | 54 | 58 | 64
OP | 120604427 | MiniAT | East Bay | 2021-02-28 13:00 | 135.3 | 125 | 10.3 | 8.24% | Failure - Equipment | EQ | P5.1 | Customer owned check valve experienced leakage during periods of low/no-flow gas demand. | • Leak test was performed, and no leakage was found. • Class B inspection was performed, and no issues were identified. • A token relief valve was installed with a 100 psig set point. • Engineering limits were updated to align with the relief valve set point. | Transmission | Small OP Event | No | No | No | No |  |  | GT.STAT.LVCR.0000000371 |  | 74 | 72
OP | 120728067 | MiniAT | San Jose | 2021-03-31 16:00 | 21.48 | 20 | 1.48 | 0.074 | Failure - Equipment | EQ | P5.1 | Regulation failed to control pressure. | • Evaluate cause of the overpressure event through equipment testing. • Because the diaphragm meter’s 20 psig maximum inlet pressure rating was breached the meter was removed from service. o Install new meter and rebuild meter set assembly per the standard. o The customer will be contacted, and placed on bypass until the equipment is replaced, CNG is on stand-by. | HP Distribution | Small OP Event | Yes | No | No | No |  | H-15 | 0 |  | 15 | 17
OP | 120823992 | Gauge | Mission | 2021-04-15 | 62.5 | 60 | 2.5 | 4.167% | Gas Contaminants - Debris | EQ | P5.1 | Regulation failed to control pressure due to the debris in the regulation. | • Existing regulator and relief were replaced with Fisher 627 set at 35 psig and a Fisher H-202 set at 50 psig. | HP Distribution | Small OP Event | Yes | No | No | No | No | H-10 | 0 |  | 60
OP | 120855335 | BPA_PT0003 YO_PAT_RN02 | Yosemite | 2021-04-20 | 396.8 | 395 | 1.8 | 0.4557% | Maintenance Operations Quality | HU | P5.1 | Maintenance issue resulted in the op event more investigation is required, see ACE. | • Replaced control sense line needle valve with ball valve. • Performed calibration on transmitter – passed. • Class B inspection of the regulation equipment did not identify additional issues. • GPOM is currently calibrating the downstream regulator stations off DFM 7217-01. | Transmission | Small OP Event | Yes | No |  |  |  | 2 | GT.STAT.MISC.PATTERSON_ | 85517 | 380 | 390
OP | 120886870 | SRB_PT0002 | North Valley | 2021-04-26 | 470.9 | 470 | 0.9 | 0.1915% | Gas Contaminants - Sulfur | EQ | P5.1 | Regulation failed to control pressure due to sulfur on the pilot of the regulation equipment. | • FIMP to analyze historical data to understand SCADA trends with respect to maintenance. • GPOM to install FEP Pilots. • Gas Control will adjust alarm settings with respect to lowered equipment set points (LL to 420 psig). | Transmission | Small OP Event | Yes | No | No |  |  |  | GT.STAT.MISC.REDBLUFFPR | 082621.pdf | 450 | 465
OP | 121066673 | YO_PAT_RN13 | Yosemite | 2021-05-10 05:31 | 58.2 | 57 | 1.2 | 2.105% | Gas Contaminants - Sulfur | EQ | P5.1 | An investigation is underway as to why regulation equipment failed to control pressure. Monitor appears to have been valved out at the last maintenance as it does not come to control, sulfur "sticking" the pilot plug seems to have been the cause. | • Working with GSP to reduce set points for the regulator and monitor, 48 psig and 51 psig, respectively. | HP Distribution | Small OP Event | Yes | No | No | No |  | H-14 | GD.STAT.DIST.00687 | 0809232.PDF | 51 | 54 | N/A
OP | 121322720 | YO_PAT_RN13 | Yosemite | 2021-05-10 11:31 | 65.7 | 57 | 8.7 | 15.26% | Maintenance Operations Quality | HU | P50.2 | The risk to identify that closing the d/s fire control valve, block valve, and bypass valve leak by was not assessed. During additional testing it was determined the bypass valve was leaking at a rate of ~4 psig/10 minutes. | • Working with GSP to reduce set points for the regulator and monitor, 48 psig and 51 psig, respectively. Bypass Valve V-3 was removed. | HP Distribution | Large OP Event | No | No | No | Yes |  | H-14 | GD.STAT.DIST.00687 | 0809232.PDF | 51 | 54 | N/A
Near Hit | N/A | SI_WMS_M001 | Arbuckle | 2021-05-29 | NA | 35 | NA | NA | Slam shut activation | EQ |  | Boiler burner fell offline resulting in activation of slam shut device |  | HP Distribution | Near Hit | No | No |  | No | Yes | H-15 | 0 | 0809539.pdf
Near Hit | 121499891 | SJ_SJS_EX09 | San Jose | 2021-06-08 14:11 | 55 | 60 | -5 | -8.333% | Failure - Equipment | EQ |  | SCADA instrumentation malfunction. | • Evaluate additional steps to ensure SCADA equipment was working as intended. • Replaced the RTU SCADA Pack. • Additional trouble shooting with other engineering teams to understand the cause. - A CAP has also been entered for the YO_OAK_RP03 instrumentation failure | HP Distribution | Near Hit | No | No |  | No |  | H-15 | 0 |  |  |  | N/A
OP | 121648530 | Chart Recorder | Humboldt | 2021-06-22 | 41.5 | 40 | 1.5 | 3.75% | Gas Contaminants - Debris | EQ | P5.1 | Regulation failed to control pressure due to debris found in the station equipment. | • GPOM inspected pin-off tees, valves and regs for debris. • GPOM performed an internal inspection and identified debris in the regulation equipment. • Planning to install filters at this location. • Lowered the regulator and monitor set points be 5 psig. • MCTL to conduct testing on the regulator that had issues holding set point and did not achieve lockup. | HP Distribution | Small OP Event | Yes | No | No | No |  | H-10 | GD.STAT.HPRS.00784 | 0805658.PDF | 35 | 40 | N/A
Near Hit | 121722738 | M21_PT0005 | San Jose | 2021-07-12 19:12 | 70 | 250 | -180 | -72% | Clearance Execution | HU |  | TBD: Initial reports suggest valves operated out of clearance sequence. | Issues to resolve with the CAP - Is there an opportunity to alert GPOM sooner? - Assess and mitigate any potential for pigging debris/liquid at Diana Station - Was a pre-clearance meeting held? Was there engagement from all parties involved and was there a clear understanding of roles and responsibilities? Was the clearance reviewed step by step? - Conduct a standdown with GPOM and TPCO around clearances, communication, and completing work with a time constraint. - Was there an opportunity to increase the amount of time allowed to plan for this clearance? | Transmission | Near Hit | No | No |  | No |  | 1 | GT.STAT.MISC.DIANALRCV_ | 082126.PDF | 230 | 215
OP | 121728594 | AAN_PT298A | Diablo | 2021-07-14 01:38 | 733 | 720 | 13 | 1.806% | Gas Control Center Operations | HU | P5.1 | Clearance operations reduced reaction time of dual run PLS regulation equipment. | Leak survey on piping affected by MAOP breach Station equipment has already been identified for rebuild. Explore option to hard code PLC to implement set point change ramp rate for PLS. | Transmission | Small OP Event | No | No |  |  |  | 2 | GT.STAT.MISC.ANTGSTPLS_ | 4807103.pdf | 600 | 715 | N/A
OP | 121737614 | ST_STK_RS10 | Stockton | 2021-07-15 06:12 | 102.44 | 100 | 2.44 | 2.44% | Clearance Preparation | HU | P5.1 | Regulation failed to perform as intended - after clearnace was adjusted to create a dead end system. | • Pigging project is on-hold until clearance procedure is updated & approved. • Perform internal inspection and replace damaged components. • Evaluate equipment setpoints per TD-4125P-07 “Establishing Setpoints on Overpressure Protection Devices” | Transmission | Small OP Event | Yes | No | No | No |  | 2 | GT.STAT.MISC.STADIUMSRF | 800489 | 98 | 90 | N/A
OP | 121770121 | MiniAT | Sierra | 2021-07-17 | 179.11 | 130 | 49.11 | 37.78% | Gas Contaminants - Debris | EQ | P50.7 | Regulation failed to control pressure due to the debris in the regulation. | Internal inspection of filter element Borescope inspection Replaced existing regulation with (2) 2-inch Mooney Flowgrids and reduced set points on regulation equipment and the token relief (Reg at 100 PSIG, Mon at 110 PSIG and token relief at 122 PSIG). Leak survey Will engage customer for equipment/houseline ratings. Potential installation of a slam shut and visibility. Equipment testing to confirm mechanism. | Transmission | Large OP Event | No | No |  | Yes |  | LVCR | GT.STAT.LVCR.0000000603 | 0812907 | 125 | 130 | 170
OP | 121757183 | KA2_PT0001 | Hinkley District | 2021-07-19 | 551 | 524 | 27 | 5.153% | Clearance Execution | HU | P5.1 | TBD: Initial reports suggest valves operated out of clearance (80158726) sequence. | • Station personnel brought the compressor station back safely. • Mainline valve V-149.65A and Monitor valve V-149.64A are now closed. • Station personnel to investigate if further action is required. | Transmission | Small OP Event | No | Yes |  |  |  | H-19 | GT.STAT.MISC.PLS-2XA | 383654
Near Hit | 121805266 | FLV_PT0004 | Stockton | 2021-07-27 | 295 | 300 | -5 | -1.6% | Failure - Equipment | EQ |  | Regulation fails to perform as intended | 1. Per confirmation from facility engineer, S-255 will be installing in-line filtration and slam shut will be installed on both runs. 2. GPOM to perform internal inspection and report to CTL. 3. Rebuild failed run. 4. Perform boroscope. | Transmission | Near Hit | No | No | Yes/No | No |  | 2 | GT.STAT.MISC.LASVNAPLS | 3808137 | 285 | 295 | N/A
OP | 121806111 | MMT | Milpitas District | 2021-07-27 17:43 | 562 | 555 | 7 | 1.261% | Clearance Execution | HU | P5.1 | During pigging clearance valve operations induced pressure control issues. Slam shut equipment operated as intended. | The pigging operation has stopped and we will be conducting a clearance review today. | Transmission | Small OP Event | No | No |  |  | Yes | H-19 | GT.STAT.MISC.MLPTSTPLM_ | 383510.pdf
Near Hit | 121809564 | SI_WMS_M001_PT3 | Sierra | 2021-07-28 02:21 | 30.5 | 35 | -4.5 | -12.86% | Failure - Equipment | EQ |  | Customer experiences hot shutdown. Slam shut activation operated as inteneded. | Tested regulation equipment for control and lockup Set points for regulation, token relief and slam shut were lowered on 5/29/2021 from initial slam shut activation. | Transmission | Near Hit | No | No |  | No | Yes | 1 | GT.STAT.LVCR.0000000115 | 0809539.pdf | 22 | 34 | 35
OP | 121849468 | DA_MVW_RB38 | De Anza | 2021-08-04 | 180.1 | 180 | 0.1 | 0.05556% | Clearance Execution | HU | P5.1 | Clearance execution did not identify risk of dead-end system which resulted in valve leakage | 1. GPOM to make safe by opening mainline valve 49-H5L to remove the dead-end system. 2. GPOM to open PTs at Church & Hwy 237 station for continuous pressure monitoring. 3. GPOM to investigate potential leak by at Whisman & Middlefield Station. | HP Distribution | Small OP Event | No | No | No | No |  | H-14 | GD.STAT.DIST.00567 | 0804562 | 57 | 60
OP | 121907374 | SI_LIO_RB51 | Sierra | 2021-08-14 | 57.1 | 55 | 2.1 | 3.818% | Failure - Equipment | EQ | P5.1 | Regulation failed to control pressure due to a crack in the lead run regulator diaphragm. | • Internal inspection performed. • Submit an MPR for the regulator boot that failed. • Discussion with Planning to lower set points on the regulation. | HP Distribution | Small OP Event | Yes | No | No | No |  | H-14 | GD.STAT.DIST.00976 | 806034 | 50 | 53 | N/A
OP | 121916291 | MiniAT | Sierra | 2021-08-15 | 175.9 | 175 | 0.9 | 0.5143% | SP Too Close to MOP | EQ | P5.1 | Thermal Expansion | Internal inspection of regulation equipment. Lowered set points on relief and regulation equipment. | Transmission | Small OP Event | Yes | No | No | No |  | 1 | GT.STAT.LVCR.0000000182 | 809628 | 150 | 160 | N/A
OP | 121917902 | SA_SAC_RB16 | Sacramento | 2021-08-16 | 53.2 | 50 | 3.2 | 6.4% | Clearance Execution | HU | P5.1 | Clearance operations resulted in a pressure increase in the station up to the closed fire valve. | Station was deactivated and abandoned. | HP Distribution | Small OP Event | No | No | No | No |  | H-14 | GD.STAT.DIST.01053 | 0808682.PDF | 44 | 48 | N/A
OP | 122049686 | SI_WMS_M001 | Sierra | 2021-09-12 | 36.7 | 35 | 1.7 | 4.857% | SP Too Close to MOP | EQ | P5.1 | Boiler stoppage of customer equipment resulted in plant shutdown, and rapid increase of pressure and slam shut activation. Wadham Energy operations resulted in an inadvertent pressure increase. | Tested regulation equipment for control and lockup Lowered set points for monitor, relief and slam shut Monitor: 25 PSIG, Slam Shut: 30 PSIG, Relief: 32 PSIG Downstream MAOP under review | Transmission | Small OP Event | Yes | No | No | No | Yes | 1 | GT.STAT.LVCR.0000000115 | 0809539.pdf | 22 | 25 | 30
OP | 122223644 | SMS_PT0005 | Sacramento | 2021-10-16 | 99.8 | 95 | 4.8 | 5.053% | Failure - Equipment | EQ | P5.1 | Boiler stoppage of customer equipment resulted in a quick decrease of demand leading to a rapid increase of pressure and slam shut activation. Morning Star operations resulted in an inadvertent pressure increase. | Tested regulation equipment for control and lockup Lowered slam shut set point to 95 PSIG | Transmission | Small OP Event | No | No | No | No | Yes | 1 | GT.STAT.LVCR.0000000523 | 807311 | 75 | 85 | 102
OP | 122229820 | Chart Recorder | Yosemite | 2021-10-19 | 73.41 | 60 | 13.41 | 22.35% | Maintenance Operations Quality | HU | P50.2 | Maintenance issue resulted in the op event more investigation is required, see ACE. | · Leak Survey (as required in large overpressure events TD-4911P-02) will be performed. - completed on the 1.3 mile plastic pipe, no leaks found · Borescope scheduled - completed, typical debris not affecting the regulator operation · Station equipment will be removed and station to be blind flanged - completed. Station is scheduled to be removed from service in ~2022 due to the high-speed rail - tentative future assessment required. | HP Distribution | Large OP Event | No | No | Yes/Yes | Yes |  | H-14 | GD.STAT.DIST.11232 - removed? | 0805144.PDF | 30 | 34 | 40
OP | 122241886 | MiniAT | De Anza | 2021-10-19 | 61.3 | 60 | 1.3 | 2.167% | Failure - Equipment | EQ | P5.1 | Regulation equipment failed to control pressure after the downstream system was isolated. | • Further investigation into the principal cause for the pressure increase is ongoing. • Planning to assess for a possible set point reduction. | Transmission | Small OP Event | Yes | No | No | No |  | 2 | GT.STAT.LVCR.0000000138 | 082956.pdf | 55 | 60 | 66
Near Hit | 122257405 | YO_LVT_M002 | Yosemite | 2021-10-25 | 59.95 | 60 | -0.05 | -0.08333% | Gas Contaminants - Sulfur | EQ |  | Regulation failed to control pressure due to sulfur on the pilot and equipment in the station equipment. Slam shut activation equipment operated as intended. |  | Transmission | Near Hit | No | No | No | No | Yes | 2 | GT.STAT.LVCR.0000000148 | 0812689.pdf | 45 | 55 | 60
Near Hit | 122257354 | SI_WMS_M001 | Sierra | 2021-10-25 | 34.2 | 35 | -0.8 | -2.286% | SP Too Close to MOP | EQ |  | Boiler stoppage of customer equipment resulted in plant shutdown, and rapid increase of pressure and slam shut activation. Wadham Energy operations resulted in an inadvertent pressure increase. |  | Transmission | Near Hit | No | No | No | No | Yes | 1 | GT.STAT.LVCR.0000000115 | 0809539.pdf | 22 | 24 | 35
Near Hit | 122267330 | FLP_PT0004 | Yosemite | 2021-10-26 | 390 | 400 | -10 | -2.5% | Failure - Equipment | EQ |  | Customer equipment stoppage contributed to the increase in pressure. Slam shut activation equipment operated as intended. |  | Transmission | Near Hit | No | No | No | No | Yes | 2 | GT.STAT.LVCR.0000000258 | 0806404 | 338 |  | 390
OP | 122292197 | NB_SRF_RA29 | North Bay | 2021-11-02 06:37 | 58.84 | 57 | 1.84 | 3.228% | Failure - Equipment | EQ | P5.1 | The emergency clearance execution inadvertently resulted in pressure exceeding MAOP due to poor lock-up. | • GPOM blew down station to safely repair corroded tap. • Perform Class B internal inspection. • Establish slam shut setpoint at 59 psig per clearance document. • Emergency clearance #08170702 not consistent with execution. GPOM & clearance writer to work together to ensure operational tasks are consistent with execution for future clearance. | HP Distribution | Small OP Event | No | No | No | No |  | H-14 | GD.STAT.DIST.01208 | 0807757.PDF | 51 | 55 | 59
Near Hit | 122328804 | PN_MBR_M001 | Peninsula | 2021-11-05 | 149.77 | 175 | 25.23 | -14.42% | Failure - Equipment | EQ |  | Customer CNG check valve leakage. | • The meter set is currently shut in until repairs are complete. • FIMP Risk determined the downstream MAOP and update necessary documents (ex. OD & MAOP Catalog) per 5MM. • This site has been identified as part of the LVC long term by FIMP for retrofit/rebuild to install check valve. | Transmission | Near Hit | No | No | No | No |  | H-15 | GT.STAT.LVCR.0000000505 | 0812689.pdf | 120 | 130 | 137
Near Hit | 122380254 | SI_WMS_M001 | Sierra | 2021-11-13 12:10 | 28.4 | 35 | -6.6 | -18.86% | SP Too Close to MOP | EQ |  | Boiler stoppage of customer equipment resulted in plant shutdown, and rapid increase of pressure and slam shut activation. Wadham Energy operations resulted in an inadvertent pressure increase. |  | Transmission | Near Hit | Yes | No | No | No | Yes | 1 | GT.STAT.LVCR.0000000115 | 0809539.pdf | 22 | 25 | 30
Near Hit | 122380257 | SI_OH_X109 | Sierra | 2021-11-13 15:00 | 59.5 | 60 | -0.5 | -0.8333% | Failure - Equipment | EQ |  | Regulation equipment failed to control pressure - slam shut cativation. |  | Transmission | Near Hit | Yes | No | No | No | Yes |  | GT.STAT.LVCR.0000000109 | 0809533.pdf | 50 | 55 | 57
OP | 122378030 | KE_BKD_R102 | Kern | 2021-11-15 10:58 | 55.5 | 51 | 4.5 | 8.824% | Failure - Equipment | EQ | P5.1 | Leakage through the bypass valve resulted in the downstream pressure increase during the slam shut installation. | • The bypass valve will be removed, and blind flanged. • The slam shut installation will continue as planned. • Evaluate an update to clearance procedure for distribution regulator stations which includes closing the inlet fire valve prior to the outlet fire valve. | HP Distribution | Small OP Event | No | No | No | No | Yes | H-14 | GD.STAT.DIST.00600 | 0804694 | 47 | 51
Near Hit | N/A | SI_WMS_M001 | Arbuckle | 2021-11-08 | NA | 35 | NA | NA | Slam shut activation | EQ |  | Boiler burner fell offline resulting in activation of slam shut device |  | HP Distribution | Near Hit | No | No | No | No | Yes | H-15 | 0 | 0809539.pdf
OP | 122398490 | DI_BYN_M001_PT3 | Diablo | 2021-11-18 14:55 | 128.8 | 128 | 0.8 | 0.625% | Failure - Equipment | EQ | P5.1 | Regulation equipment failed to control pressure after customer operations. The monitor locked up as intended. | • GPOM returned the station to normal operations. • PLE in process of closing out the G4 notification which returns the MAOP to 160 psig. | Transmission | Small OP Event | No | No | No | No |  | H-14 | GT.STAT.MISC.BYRONTAPRG | 0812689.pdf | 116 | 123 | 132
OP | 122400086 | EB_OAK_RB12 | East Bay | 2021-11-19 10:33 | 33.49 | 25 | 8.49 | 33.96% | Clearance preparation | HU | P50.7 | Clearance execution resulted in the creation of a dead- end system. Slam shut equipment operated as intended. | • GPOM responded and made safe • GPOM to perform Class A inspection. • Leak survey in progress. • Tie-in work is on hold until emergency clearance is developed for isolating station for tie-in and return the station to service. • GPOM to submit operating diagram for update. | HP Distribution | Large OP Event | No | No | No | Yes | Yes | H-14 | GD.STAT.DIST.01566 | 0812022.PDF | 20 | 23 | 26
OP | 122549926 | ST_TRA_M001_PT3 | Stockton | 2021-12-03 | 63.7 | 60 | 3.7 | 6.167% | Gas Contaminants - Sulfur | EQ | P5.1 | Teichert Aggregates sudden operational change and sulfur accumulation on regulation equipment. Slam shut activation. | Perform internal inspection of all regulation equipment. | Transmission | Small OP Event | No | No | No | No | Yes | 1 | GT.STAT.LVCR.0000000141 | 184048.pdf | 46 | 52 | 62
OP | 122502982 | Gauge | Sacramento | 2021-12-17 20:15 | 620 | 412 | 208 | 50.49% | Design/Process* | HU | P50.6 | Multiple feeds and station configuration resulted in pressure above the documented MAOP. | • Leak survey was performed, and no leaks found. • Installed ERX for pressure monitoring. • Shut-in and depressurized PG&E and customer service piping. • Work with AKM and FIMP Risk for MAOP remediation/correction. • Asset engineer to replace or repair leaking check valve and block valve. • Extent of condition and cause to be performed alongside the apparent cause evaluation. | Transmission | Large OP Event | No | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000539 | 0813144 | 280
OP | 122903182 | Gauge | Sonoma | 2022-01-29 | 75 | 60 | 15 | 25% | Failure - Equipment | EQ | P50.2 | Black powder debris identified and lack of maintenance resulted - Regulation failed to control pressure . |  | HP Distribution | Large OP Event | No | No | Yes | Yes | No | H-10 | GD.STAT.FTAP.04934 |  |  |  | RV
OP | 122943721 | YO_MAD_RB54_PT3 | Yosemite | 2022-02-05 | 42.5 | 42 | 0.5 | 1.19% | Maintenance Operations Quality | HU | P5.1 | While performing an A-inspection the sequencing followed resulted in an inadvertent increase in pressure exceeded maximum allowable operating pressure. | · Tailboard best practices while performing regulation maintenance. · Communicate human performance tools to be utilized to prevent error-like situations. · Review station design. | HP Distribution | Small OP Event | No | No | No | No |  | H-14 | GD.STAT.DIST.00702 | 0805154.PDF | 36 | 40 | 44
OP | 122990270 | SFL_PT0001 | North Valley | 2022-02-15 | 560 | 550 | 10 | 1.818% | Gas Contaminants - Sulfur | EQ | P5.1 | Regulation failed to control pressure due to identified sulfur on the equipment. | · GPOM replaced internals on both the regulator, the monitor, and pilots. · Set point reductions to take place. · Borescope inspection scheduled. New Sulfur-Gon filters to be installed. | Transmission | Small OP Event | Yes | No | Yes | No |  | H-14 | GT.STAT.MISC.FELLSTPLS_ | 082551.pdf | 530 | 545
Near Hit | 123057149 | SA_WSA_RS09 PT2 | Sacramento | 2022-03-02 | NA | 500 | NA | NA | Slam shut activation | EQ |  | The root cause for the slam shut to engaged during normal operation is unknown at this time. MTCL conducted testing and hitting it with a dead blow mallet but unable to get the slam shut to tripped. Review of SCADA found no anomaly in filter DP, inlet, intermediate and outlet pressure. Outlet pressure was ~44 psig at the time slam shut tripped. slam shut was set at 52 psig |  | HP Distribution | Near Hit |  | No | No | No | Yes | H-14 | GD.STAT.DIST.01140 | 0804218.PDF
Near Hit | 123038553 | OCM_PT0002 | Diablo | 2022-03-01 | 163 | 170 | 7 | -4.12% | Failure - Equipment | EQ |  | Regulator spring brokes leading to monitor in control. Near Hit |  | Transmission | Near Hit |  |  | No | No |  |  | GT.STAT.MISC.CONCORDMTR | 0811631.pdf
OP | 123152084 | MiniAT | Central Coast | 2022-03-16 11:00 | 89.1 | 75 | 14.1 | 18.8% | Gas Contaminants - Sulfur | EQ | P50.7 | Regulation failed to control pressure due to sulfur in the station equipment. | -PG&E technicians replaced rubber goods in the regulators and installed a token relief valve. -Leak survey completed. -Review station configuration for the installation of secondary overpressure protection. | Transmission | Large OP Event | No | No | No | Yes |  | LVCR | GT.STAT.LVCR.0000000170 | 0809592.pdf | 52 | 58
Near Hit | 123848151 | PN_BUR_RA39 | Peninsula | 2022-04-02 | NA | 34 | NA | NA | Slam shut activation | EQ |  | Submit to close - overpressure elimination is tracking slam shut activations, as near hits that were prevented by the activation. |  | HP Distribution | Near Hit | No | No | No | No | Yes | H-14 | GD.STAT.DIST.00080 | 0803990.PDF
Near Hit | 123248102 | PN_SBR_R190 | Peninsula | 2022-04-05 | 62 | 300 | NA | NA | False Alarm | EQ |  | MAOP separation vavlve closed resulted in slow lock up of the equipment, and MOP Alarm. | 2020 by FIMP-Reg and approved for station rebuild, #31514483 | HP Distribution | Near Hit | No | No | No | No |  | H-14 | GD.STAT.DIST.00024 | 0804102.pdf
OP | 123352722 | FFN_PT0002 | Fresno | 2022-04-16 00:53 | 400.691 | 400 | 0.691 | 0.1727% | Failure - Equipment | EQ | P5.1 | Regulation equipment failed to control pressure at the set point. | - Technician performed lock up test, and equipment locked up as expected. - The station has been temporarily shut-in and further investigation will be undertaken before returning to service. \ | Transmission | Small OP Event | No | No | No | No |  | H-14 | GT.STAT.MISC.FRESNOLOAD | 3808517.pdf | 350 | 365
OP | 123369541 | Gauge | Yosemite | 2022-04-19 | 357 | 230 | 127 | 55.22% | Gas Contaminants - Debris | EQ | P50.7 | The gas contaminants resulted in regulation failing to control pressure. | -PG&E technicians purged pipeline below the 230 psig MAOP, to a safe pressure of 200 psig. -Leak survey completed - no leaks identified. -Install an ERX for visibility into Gas Control. -An extent of condition to investigate taps in the clearance segment. -Reach out to customers to understand operational timelines. -Consider evaluation for capacity reduction at Tellis Gin | Transmission | Large OP Event | No | No | Yes | Yes |  | H-14 | GT.STAT.MISC.TELLISGINR | 0806794.pdf | 220 | 200 | 360
Near Hit | 123386852 | Gauge | Sonoma | 2022-04-21 | NA | 60 | NA | NA | Failure - Equipment | EQ |  | Potential Merrimack valley type incident |  | HP Distribution | Near Hit | No | No | No | Yes |  | H-14 | GD.STAT.DIST.01318 | 0805536.PDF
Near Hit | 123848155 | YO_MAD_RB41 | Yosemite | 2022-04-28 | NA | NA | NA | NA | Slam shut activation | EQ |  | Submit to close - overpressure elimination is tracking slam shut activations, as near hits that were prevented by the activation. |  | HP Distribution | Near Hit |  | No | No | No | Yes | H-14 | GD.STAT.LPRS.00249 | 0805153.PDF
OP | 123543685 | SI_RSV_R396 | Sierra | 2022-05-07 | 62.5 | 60 | 2.5 | 4.167% | Gas Contaminants - Liquids | EQ | P5.1 | Regulation equipment failed to control pressure at the set point. Slam shut equipment operated as intended to prevent large overpressure. | - GPOM to investigate the cause and perform station repairs if necessary. - DA-6 moisture separators were installed, and borescope will be conducted. - GPOM to install working monitor pilot if necessary. | HP Distribution | Small OP Event | Yes | No | Yes | No | Yes | H-14 | GD.STAT.DIST.00950 | 0805896.PDF | 55 | 58 | 62
OP | 123621903 | Gauge | Sierra | 2022-05-17 | 100.4 | 60 | 40.4 | 67.33% | Failure - Equipment | EQ | P50.7 | Leakage in the bypass and isolation valves resulted in downstream pressure increase. | Pressure was purged to normal operating pressure of 50 psig. - Downstream leak survey was performed. - A Borescope inspection was performed on the station components. - The station was identified to receive a slam shut in 2022, and the team will evaluate existing equipment capability and readdress the priority if needed. - Bypass valve removed? | HP Distribution | Large OP Event | No | No | Yes | Yes |  | H-14 | GD.STAT.DIST.01430 | 0809421.PDF | 50 | 55 | N/A
OP | 123883809 | MiniAT | Kern | 2022-06-19 | 120.08 | 120 | 0.08 | 0.06667% | SP Too Close to MOP | HU | P5.1 | Regulation failed to control pressure due to low flow condition with set points too close to MAOP | • Class B Inspection completed on 6/19/2022 (full station rubber good replacement). • Station set point review and future reduction. • CAP 123890751 was submitted to perform an extended review of set points in accordance with GDS 4125P-07. • Evaluate for slam shut or thermal relief installation. • Evaluate for SCADA or ERX visibility. | Transmission | Small OP Event | Yes | No | No | No |  | H-14 | GT.STAT.MISC.DAGGETMTR_ | 082555.pdf (pge.com) | 115 | 120 | N/A
OP | 124162441 | MI_LVM_RL20 | Mission | 2022-07-25 10:00 | 706 | 497 | 209 | 42.05% | Design/Process* | REC | P50.6 | The MAOP of the bridle was inadvertently understood to be 720 psig during the clearance to transfer distribution regulator stations from L-114 to the adjacent L-303. | • An inquiry was made to MAOP Engineering to verify the MAOP. • Gas Control reduced pressure in L-303 during the MAOP evaluation below the 497 psig MAOP. | Transmission | Large OP Event | Yes | No | No | Yes |  | H-14 | GD.STAT.DIST.11205 |  | N/A | N/A
OP | 124201892 | JSI_PT0002 | De Anza | 2022-07-30 14:30 | 201.6 | 201 | 0.6 | 0.2985% | Gas Contaminants - Sulfur | EQ | P5.1 | Regulation failed to control pressure due sulfur identified on the equipment. Equipment pressure set points were operating too close to the MAOP. | • GPOM will return to the site to calibrate the gauge with respect to SCADA to confirm pressure accuracy. • Continue extent of condition, internal and borescope inspections for sulfur contaminants on downstream regulator stations. • Install pilot sulfur filters. • Coordination with Gas Planning to reduce equipment set points to comply with TD-4125P-07. | Transmission | Small OP Event | Yes | No | No | No |  | H-14 | GT.STAT.MISC.SIERRAVIST | 081659.pdf | 195 | 208
OP | 124216219 | SJ_SCL_RE25 | San Jose | 2022-08-02 17:42 | 15.12 | 12 | 3.12 | 26% | Clearance Execution | HU | P5.1 | When the crew closed the outlet fire valve and block valves to perform a painting clearance, a valve leaked by. | • Internal inspection was performed and replaced the rubber good at the regulator station. • The station remains shut-in for the duration of the clearance. • Additional investigation to determine lessons learned is ongoing. | LP Distribution | Small OP Event | No | No | No | No | Yes | H-14 | GT.STAT.LPRS.00131 | 0804519.PDF | 9.5 | 11 | 14
OP | 124236113 | PN_SM_RB07 | Peninsula | 2022-08-04 | 52.4 | 34 | 18.4 | 54.12% | Clearance Preparation/Execution* | HU | P50.2 | The crew failed to recognize the error-like situation and reseated the inlet fire valve with an open bypass. | Station will be left shut-in until the clearance is completed. | HP Distribution | Large OP Event | No | No | No | Yes |  | H-14 | GD.STAT.DIST.00106 | 0804023.PDF | 31 | 34
OP | 124244917 | SI_NCT_S222 | Sierra | 2022-08-07 | 55.5 | 55 | 0.5 | 0.9091% | Gas Contaminants - Debris | EQ | P5.1 | Weld debris accumulation on regulator and monitor seats at recently installed HPR station inhibited lock up. | • Cleaned and rebuilt regulation equipment. • Purged station piping. | HP Distribution | Small OP Event | Yes | No | No | No |  | H-10 | GD.STAT.HPRS.00637 | 0813246.PDF | 45 | 50
Near Hit | 124297296 | KH2_AT1122 | Hinkley District | 2022-08-15 | 568 | 573 | -5 | -0.8726% | Failure - Equipment | EQ |  | Discharge check valve failed allowing discharge pressure to enter the suction bypass. | Repairs completed | Transmission | Near Hit | No | Yes | No | No | No | H-19 | GT.STAT.MISC.HINKLEY_ | 383654.pdf
OP | 124349109 | Gauge | Mission | 2022-08-22 11:11 | 60.2 | 60 | 0.2 | 0.3333% | Maintenance Operations Quality | HU | P5.1 | While on manual bypass maintenance operations the valve was unintentionally turned in the wrong direction which resulted in the increased downstream pressure. | • GPOM took immediate mitigative actions to reduce pressure downstream and conducted an internal inspection which identified internal debris on the regulation. The soft goods were also replaced. • A follow up Human Factors Analysis Classification System (HFACS) assessment will be completed. | HP Distribution | Small OP Event | No | No | No | No | No | H-10 | GD.STAT.FTAP.04775 |  | 45 | 55 | 175
OP | 124391351 | REN_PT0002 | Fresno | 2022-08-29 11:22 | 612 | 495 | 117 | 23.64% | Clearance Execution | HU | P95.6 | V-106 that isolated 2 pipelines with different MAOP’s was mistakenly opened. | • GPOM technicians onsite immediately made area safe and closed the valve. • Leak survey in process for L-138. | Transmission | Large OP Event | No | No | No | Yes | No | H-14 | GT.STAT.MISC.FRESNOLOAD | 3808517.pdf | N/A | N/A
OP | 124433893 | HU_EUR_RR30 | Humboldt | 2022-09-01 06:55 | 127.3 | 50 | 77.3 | 154.6% | Clearance Execution | HU | P50.2 | The vent valve was inadvertently closed creating a bottled section on the station outlet pipe. | The station was taken out of service to evaluate the overpressure extent. • Leak survey was completed on the station piping, and no leaks were identified. | HP Distribution | Large OP Event | No | No | No | Yes | No | H-14 | GD.STAT.DIST.01164 | 0811598.PDF | 44 | 48
OP | 124600188 | MiniAT | Central Coast | 2022-09-30 | 184.3 | 125 | 59.3 | 47.44% | Records | HU | P50.6 | Legacy meter set design that did not consider customer operating condition exceeding requested delivery pressure. | - GPOM Technician inspected equipment, to find no issues - Install token relief valve (set point of 115 psig) - Customer has been isolated from service - Adjust MiniAT Engineering Limits - Engineering to expedite scope to install check valve | Transmission | Large OP Event | No | No | No | Yes | No | H-15 | GT.STAT.LVCR.0000000316 | 0813193.pdf | 110 | 120
Near Hit | 124868685 | MiniAT | Sierra | 2022-10-06 |  | 60 |  |  | Records | REC |  | MAOP Verification to FIMP Risk Tracking |  | HP Distribution | Near Hit | No | No |  |  |  | H-15 | GT.STAT.LVCR.0000000152
Near Hit | 124744137 | YO_LBN_M002 | Yosemite | 2022-10-19 04:00 | 145.75 | 890 | -744.25 | -83.62% | Gas Contaminants - Sulfur | EQ |  | Regulation failed to control pressure due to sulfur in the station equipment. | - Update the operating diagram to reflect to accurate MAOP value. - Update to the pressure alarm settings in Gas Control. | Transmission | Near Hit | No | No | Yes | No | No | H-14 | GT.STAT.LVCR.0000000125 | 0809549.pdf | 115 | 125 | 140
OP | 124765797 | YO_CRL_S090 | Yosemite | 2022-10-23 04:33 | 56.19 | 56 | 0.19 | 0.3393% | Failure - Equipment | EQ | P5.1 | Regulation failed to control pressure. | - Tested for lock up and return to service - MAOP Engineering to verify MAOP is correct on the operating diagram (historical value shows 58 psig) | HP Distribution | Small OP Event | Yes | No | No | No | No | H-14 | GT.STAT.MISC.CROWLANDG |  | 54 | 48
OP | 124769215 | ARH_PT0006 | North Valley | 2022-10-22 17:02 | 954.2 | 911 | 43.2 | 4.742% | Failure - Equipment | EQ | P50.2 | Station control system unexpectedly closed an automated valve resulting in dead-end system. | 1. Station was made safe and returned to operation. 2. Leak Survey was completed - no leaks found. 3. Asset Engineer to reevaluate station control system. | Transmission | Small OP Event | No | No | No | No | No | H-19 | GT.STAT.MISC.RUBYPLINTR | 801821 | N/A | N/A
OP | 124815407 | MI_ERE_ER11 | Yosemite | 2022-11-01 | 63 | 60 | 3 | 5% | Failure - Equipment | EQ | P5.1 | Regulators could not control pressure during the customer rapid shutoff. | GPOM technician responded to the location and confirmed the customer outage and verified calibration of the equipment. | HP Distribution | Small OP Event | No | No | No | No | No | H-15 | GT.STAT.LVCR.0000000668 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0813755.pdf | 40 | 46 | 60
Near Hit | 124857604 | PN_SM_PA55 | Peninsula | 2022-11-08 13:51 | 55.1 | 34 | 21.1 | 62.06% | Clearance Execution | HU |  | With the station out of service measured pressure inadvertently increased resulting in the overpressure event. |  | HP Distribution | Near Hit | No | No | No |  | No | H-14 | GD.STAT.DIST.00087
Near Hit | 124869301 | MiniAT | Kern | 2022-11-09 |  | 465 | -465 | -100% | Records | REC |  | MAOP Verification to FIMP Risk Tracking | No follow up corrective actions | Transmission | Near Hit | No | No | No |  | No | H-15 | GT.STAT.LVCR.0000000431 | 0812132.pdf
OP | 124880564 | SJ_GIL_RH67 | San Jose | 2022-11-11 | 56.07 | 55 | 1.07 | 1.945% | Maintenance Operations Quality | HU | P5.1 | Pilot for controlling regulator tubed incorrectly (pilot sense tapped from regulator bleed port). | • Leak Survey • Borescope inspection • Class B Inspection | HP Distribution | Small OP Event | No | No | No | No | No | H-14 | GD.STAT.DIST.11187 | 0809277 | 49 | 53
OP | 124895134 | AANPT00AH | Diablo | 2022-11-15 | 438.4 | 438 | 0.4 | 0.09132% | Failure - Equipment | EQ | P5.1 | Clearance preparation was written resulted in dead-end system | Station was made safe and returned to operation • Construction to continue monitor pressure until off clearance. | Transmission | Small OP Event | No | No | No | No | No | H-19 | GT.STAT.MISC.ANTGSTPLS_ | 4807103
OP | 124934368 | Gauge | Sierra | 2022-11-23 | 50.2 | 50 | 0.2 | 0.4% | Maintenance Operations Quality | HU | P5.1 | Set Points too close to MAOP. | • Set point request clearance 80211198 created to document and adjust. • H202 Relief Valve to be replaced with Circle Seal. • CAP 124934367 submitted to correct MAOP on OP diagram from 60 psig to 50 psig. • Corrective actions will be created within CAP based on identified gaps in the MAOP validation and set point change request process to prevent future changes. | HP Distribution | Small OP Event | Yes | No | No | No | No | H-14 | GD.STAT.DIST.11203 | 0812207.pdf | 49 | 53
OP | 124954638 | DI_PIT_M001 | Diablo | 2022-11-30 | 61.5 | 60 | 1.5 | 2.5% | Failure - Equipment | EQ | P5.1 | Regulators could not control pressure during the customer rapid shutoff. | “A” inspection performed by GPOM Leak Survey has been requested at the LVCR - no leaks found Reduce set points to 48/54 reg/monitor SS at 58/60 | HP Distribution | Small OP Event | Yes | No | No | No | No | H-14 | GT.STAT.LVCR.0000000174 |  | 54 | 58 | 62
Near Hit | 124960451 | FR_FRE_RA03 | Fresno | 2022-12-01 09:38 |  | 60 | -60 | -100% | Slam shut activation | EQ |  | Submit to close - overpressure elimination is tracking slam shut activations, as near hits that were prevented by the activation. |  | HP Distribution | Near Hit | No | No | No | No | Yes | H-14 | GD.STAT.DIST.11139 |  | 54
Near Hit | 124990724 | EB_OAK_RA63 | East Bay | 2022-12-08 09:38 |  | 12 | -12 | -100% | Slam shut activation | EQ |  | Submit to close - overpressure elimination is tracking slam shut activations, as near hits that were prevented by the activation. |  | LP Distribution | Near Hit | No | No | No | No | Yes | H-14 | GD.STAT.LPRS.00272
Near Hit | 124990266 | MiniAT | Fresno | 2022-12-08 | 299.73 | 650 | -350.27 | -53.89% | Records | REC |  | MAOP Verification to FIMP Risk Tracking | MAOP was determined to be 650 psig through the MOC211 process of evaluation. This was submitted for near hit tracking purposes, and records to understand the andminstrative burden of MOC211. - remove regulation, and replace with mooney flowgrid - replace with norval & ss, and mitigate potential Merrimack by moving the senselines inside the vault Submit to close. | Transmission | Near Hit | No | No | No | No | Yes | H-15 | GT.STAT.LVCR.0000000387
OP | 124993269 | KE_MCP_D204 | Kern | 2022-12-08 | 127 | 120 | 7 | 5.833% | Records | REC | P5.1 | Historical documentation did not account for operating condition allowances. | The station has been identified for rebuild under the 50C MAT code, so short term actions may be: - Consider uprating the station - Consider shutting in the station, and installing a temporary regulator station | Transmission | Small OP Event | No | No | No | No | No | H-14 | GD.STAT.DIST.00673 | 0805245.PDF | 33 | 44
OP | 125015593 | DI_PIT_M001 | Diablo | 2022-12-10 | 60.05 | 60 | 0.05 | 0.08333% | Failure - Equipment | EQ | P5.1 | Regulators could not control pressure during the customer rapid shutoff. | • Evaluate calibration accuracy of SCADA. | HP Distribution | Small OP Event | Yes | No | No | No | No | H-14 | GT.STAT.LVCR.0000000174 |  | 54 | 58 | 62
OP | 125310594 | ST_TRA_M001 | Diablo | 2023-01-07 | 60.79 | 60 | 0.79 | 1.317% | Maintenance Operations Quality | EQ | P5.1 | Slam Shut was manually reset during maintenance activities resulting in the inadvertent pressure increase. | • “A” inspection performed by GPOM. • Technician rebuilt regulator pilot. | HP Distribution | Small OP Event | No | No | No | No | No | H-15 | GT.STAT.LVCR.0000000141 |  | 46 | 52 | 62
Near Hit | 125389183 | SA_SAC_RA58 | Sacramento | 2023-01-25 |  | 46 | -46 | -100% | Gas Contaminants - Debris | EQ | P5.1 | Did not result in OP event, black powder debris was identified during the Maintenance activities | Perform borescope, and cleaning by psc EOC of adjacent stations to identify if additional debris is identified | HP Distribution | Near Hit | No | No | Yes/Yes | No | No | H-14 | GD.STAT.DIST.01042 | 0808301.PDF
Near Hit | 125429011 | EB_OAK_RA54 | East Bay | 2023-02-02 | 66.48 | 12 | 54.48 | 454% | Gas Contaminans - Liquid | EQ | P50.6 | Liquid intrusion was identified in the regulator station. | NOT AN OP EVENT - WATER | LP Distribution | Near Hit | No | No | No | Yes | Yes | H-14 | GD.STAT.LPRS.00075
Near Hit | 125441668 | YO_MAD_RB54_PT3 | Yosemite | 2023-02-02 |  | 42 | -42 | -100% | Slam shut activation | HU | P5.1 | SVCEMTIntegratPrd@pge.comEM Tool ePage: Gas Dist Event Initial/Confirmed/Final Epage on 02-05-23 00:54 hrs. YO_MAD_RB54 at SUNRISE AVE & ROAD 28 MADERA. Activation of pipeline safety device. Slam Shut activation due to Slam Shut set points were set too low during maintenance last Thursday 2/2/23. (Confirmed by PG&E personnel). No customer impact. PG&E Crew on site. |  | HP Distribution | Near Hit | No | No | No | No | Yes | H-14 | GD.STAT.DIST.00702 | 0805154.PDF | 36 | 40 | 37
OP | 125542977 | KH2_PT200B | Hinkley District | 2023-02-21 | 579.7 | 573 | 6.7 | 1.169% | Gas Control Center Operations | HU | P5.1 | Operations led to an Emergency Shutdown (ESD) and rapid increase in pressure exceeding MAOP. | • Responsible engineer, station maintenance and gas control will review procedures to mitigate future shutdowns and overpressure events. | Transmission | Small OP Event | No | Yes | No | No | Yes | H-19 | GT.STAT.MISC.HINKLEY_
OP | 125564692 | SA_DXN_RR59 | Sacramento | 2023-02-27 | 63 | 60 | 3 | 0.05 | Gas Contaminants - Sulfur | EQ | P5.1 | Regulation failed to control pressure due to sulfur in the station equipment. Slam shut activated to control pressure. | - Clean and rebuild regulator pilots. - Install pilot sulfur filter cartridge into the existing housing. | HP Distribution | Small OP Event | No | No | No | No | Yes | H-14 | GD.STAT.DIST.01125 | 0804250.PDF | 54 | 58 | 62
OP | 125668382 | KT2_PT0_10D | Kern | 2023-03-15 | 735.2 | 660 | 75.2 | 11.39% | Failure - Equipment | EQ | P95.6 | Power outage resulted in a rapid increase of pressure. (Relief valve failed to activate, and suction/discharge bypass valve opened) | • Identification of the affected piping by Pipeline Services and GPOM. • Pressure reduction of 4% (new MAOP of 633 psig). • Leak Survey was performed on the inlet piping and compressor components, and no leaks were identified. • FIMP, PLE, GC, are assessing the safety of returning the station to full operation. | Transmission | Large OP Event | No | Yes | No | Yes | No | H-19 | GT.STAT.COMP.TOPOCK____ | 383655.pdf
Near Hit | 125856961 | YO_MOD_RL16 | Yosemite | 2023-03-23 | N/A | 12" | N/A | N/A | Slam shut activation | EQ | P5.1 | Gas Dist Event Initial/Confirmed/Final Epage on 03-23-23 08:21 hrs. RL16 at 10TH ST & D ST MODESTO. Activation of pipeline safety device- Slam Shut. (Confirmed by PG&E personnel). No customer impact. PG&E Crew on site making repairs. | GPOM rebuilt slam shut For record purpose and tracking | LP Distribution | Near Hit | No | No | No | No | Yes | H-14 | GD.STAT.LPRS.00179 | 808054 | 8.5" | 10" | 14"
OP | 125756464 | Gauged Pressure | Diablo | 2023-03-29 | 645.3 | 468 | 177.3 | 37.88% | Failure- Equipment | EQ | P50.4 | Leaking MAOP valve (V-67) between isolation points. | • Leak survey in progress. • Short Term – Overpressure section of pipe will be blown down and open small gauge tap to atmosphere. • Long Term - Asset Engineer to review FIMP-Risk data to determine long term plan to eliminate isolation points. • Repair leaking valves. | Transmission | Large OP Event | No | No | No | Yes | No | H-19 | GT.STAT.MISC.ANTGSTPLS_ | 4807103 | N/A | N/A | N/A
Near Hit | 125856993 | YO_ATW_M001 | Yosemite | 2023-04-07 | 140.36 | 175 | -34.64 | -19.79% | Failure- Equipment | EQ | P5.1 | Slam shut activation |  | Transmission | Near Hit | N/A | No | N/A | No | Yes | H-14 | GT.STAT.LVCR.0000000106 | 809530 | N/A | 130? | 123
OP | 125895048 | KE_EDW_R810_PT3 | Kern | 2023-04-12 | 40.99 | 25 | 15.99 | 63.96% | Clearance Execution | HU | P50.2 | Loss of working regulator sense lines | • FIMP to work with PLE on installing secondary overpressure protection and location of sense lines. • DIMP to evaluate upgrade downstream piping. | HP Distribution | Large OP Event | No | No | No | Yes | No | LVC | GT.STAT.LVCR.0000000461 | 87572 | 23 | 25 | N/A
Near Hit | 125949467 | YO_MAD_RB42 | Madera | 2023-04-17 | N/A | 12" | N/A | N/A | Slam shut activation | EQ | P5.1 | Gas Dist Event Initial/Confirmed Event on 04-17-23 14:42 hrs. 9TH & E ST MADERA . Activation of pipeline safety device- (Confirmed by PG&E personnel). Foreman found slam shut activated at 9th St & E St in Madera (YO_MAD_RB42) Customer impact. 0 customer(s). PG&E Crew on site. Gas Dist Event Final Epage on 04-28-22 13:39 hrs. 9th & E St MADERA . Activation of pipeline safety device- (Confirmed by PG&E personnel). Crew reset slam shut valve @ YO_MAD_RB42. Station returned to normal Customer impact. TBD customer(s). PG&E Crew on site. |  | LP Distribution | Near Hit | N/A | No | No | No | Yes | H-14 | GD.STAT.LPRS.00249 | 805153 | 8.5" | 10"
OP | 125947351 | Gauge pressure | Sacramento | 2023-04-18 | 507.3 | 500 | 7.3 | 1.46% | Thermal Expansion | NA | P5.1 | Thermal Gas Expansion | • Initial Corrective Actions: Clearance teams made area safe by lowering the gas pressure within the pig launchers. • Long term: o FIMP Risk to discuss with MAOP Engineering on MAOP delineations for pig launchers. o Review procedures for pig launchers on whether internal pressures should remain at NOP or lowered. | Transmission | Small OP Event | N/A | Yes | No | No | No | H-19 | GT.STAT.MISC.NSACHOLDER | 382860 | N/A | N/A | N/A
Near Hit | 126048006 | SJ_SCL_RE27 | San Jose | 2023-04-25 | NA | 12" | N/A | N/A | Slam shut activation | HU | P5.1 | Per Epage, slam shut activation due to paint crew acidentally bumped into SS. |  | LP Distribution | Near Hit | N/A | No | No | No | Yes | H-14 | GD.STAT.LPRS.00132 | 808913
OP | 126044192 | Gauge Pressure | Sonoma | 2023-05-03 | 50.92 | 50 | 0.92 | 1.84% | Records | NA | P5.1 | Sudden operational change | • Planning to evaluate lowering equipment setpoints. • MAOP-Engineering to reevaluate MAOP demarcation. • Extent of condition review for HPR-style station due to overpressure risk. | HP Distribution | Small OP Event | No | No | No | Yes | No | H-10 | GD.STAT.HPRS.00931 | 805472 | 44 | 47 | N/A
Near Hit | 126131134 | CC_MON_RM17_PT3 | Central Coast | 2023-05-04 |  | 313 |  |  | Communication | NA | P5.1 | M&L induced current which caused a misread to the pt - no sources for the overpressure event to occur | potentially adjust future design | HP Distribution | Near Hit | No | No | No | No | No | H-14 | GT.STAT.MISC.FIGUERSTAT | 0812779.pdf |  |  | N/A
Near Hit | 126134296 | ST_ION_M002_PT2 | Stockton | 2023-05-13 | 301.8 | 360 | -58.2 | -16.17% | Thermal Expansion |  | P5.1 | Intermediate piping between the regulator and monitor exceeded MAOP due to thermal expansion under no flow conditions. | • Initial corrective actions: o Switch regulator and monitor positions to prevent the isolated section of gas. • Long term: o Consider uprating for higher MAOP. o Review gas standard updates to test piping to a higher MAOP based on certain regulator combinations. | Transmission | Near Hit | No | No | No | No | No | LVC | GT.STAT.LVCR.0000000633 | 0813627 | 22 | 27 | TBD
OP | 126136492 | CC_LSB_S046_PT1 | Central Coast | 2023-05-15 | 66.15 | 50 | 16.15 | 32.3% | Maintenance Operations Quality | HU | P50.2 | Bypass Operations | Leak survey conduct Reinspected regulation for control and lockup | HP Distribution | Large OP Event | No | No | No | No | No | H-14 | GD.STAT.DIST.00519 | 806502 | 42 | 48 | N/A
OP | 126155328 | MiniAT | East Bay | 2023-05-17 | 132 | 60 | 72 | 120% | Gas Contaminants - Debris | EQ |  | Regulation failed to lockup due to debris | Immediate Action Items: · Leak Survey · Borescope Inspection · Internal Inspection · Regulator size reduction · Token relief installation · Calibrated electronic corrector transducer · Replaced inline filter element Long Term Action Items: Slam shut & ERX installation | Transmission | Large OP Event | No | No | Yes | No | No | H-15 | GT.STAT.LVCR.0000000365 | 812805 | 15 | 18 | N/A
OP | 126833858 | MIR_PT0017 & MIS_PT0045 | Mission | 2023-08-15 | 269 | 250 | 19 | 7.6% | Clearance Preparation | HU | P5.1 | Clearance preparation resulted in dead-end system. | • Station was made safe and returned to pre-clearance operation. • GPOM and Project team to review clearance. • Asset Engineer to review and submit for MAOP uprate. • ACE is request for review of clearance process. | Transmission | Small OP Event | No | No | No | Yes |  | H-19 | GT.STAT.MISC.IRVGTNPLS_ | 282245 | N/A | N/A | N/A
Near Hit | 127151271 | NV_PRB_D1116 | North Valley | 2023-09-27 | 34.5 | 40 | -5.5 | -13.75% | Slam shut activation |  |  | Slam shut activation |  | HP Distribution | Near Hit | No | No | No | No | Yes | H-14 | GD.STAT.DIST.00920 |  | 36 | 33 | 42
OP | 127298657 | YO_RVB_M001 | Yosemite | 2023-10-17 14:20 | 408.7 | 408 | 0.7 | 0.1716% | Slam shut activation | EQ | P5 | Thermal expansion | Adjust configuration such that regulator is upstream of the monitor. Assess to see if the location is on the TRV list | Transmission | Small OP Event | Yes | No | No | No | Yes | H-15 | GT.STAT.LVCR.0000000719 |  | 100 | 105
OP | 127327632 | YO_ESL_S091 | Yosemite | 2023-10-21 15:36 | 60.28 | 60 | 0.28 | 0.4667% | Failure- Equipment | EQ | P5 | Regulation Failed to control pressur. Poor lock up udring low flow condition | Evaluate set point reduction Evaluate replacing pilot unloading regulation with spring operated regulation (PM# 35493194) Evaluate HiHi alarm reduction | HP Distribution | Small OP Event | Yes | No | No | No | No | H-14 | GD.STAT.DIST.01419 | 809099 | 50 | 54 | N/A
OP | 127331042 | YO_ATW_S028 | Yosemite | 2023-10-22 00:50 | 45.51 | 45 | 0.51 | 1.133% | Gas Contaminants - Sulfur | EQ | P5 | Regulation failed to control pressure due to sulfur in the station equipment. |  | HP Distribution | Small OP Event | Yes | No | No | No | No | H-14 | GD.STAT.DIST.00722 | 0805126 | 38 | 43
Near Hit | 127407674 127399866 | YO_LBN_M002 | Yosemite | 2023-10-30 | 136.3 | 150 | -13.7 | -9.133% | Gas Contaminants - Sulfur | EQ | P5 | Regulation failed to control pressure due to sulfur in the station equipment. |  | Transmission | Near Hit | No | No | No | No | No | H-15 | GT.STAT.LVCR.0000000125 | 0809549.pdf (pge.com)
Near Hit | 127398012 | THM_PT0111 | Hollister District | 2023-11-01 | 491.56 | 492 | -0.44 | -0.08943% | Failure - Equipment | EQ | P5 | DNGP failed to control pressure during monthly maintenance. | • MCTL & GPOM To troubleshoot. • Consider an MPR based on troubleshooting outcome | Transmission | Near Hit | No | No | No | No | No | H-19 | GT.STAT.MISC.HLLSTRPLS_ | 282255
Near Hit | 127509955 | SA_SAC_M003 | Sacramento | 2023-11-20 | 315.78 | 720 | -404.22 | -56.14% | Failure - Equipment | EQ | P5 | Regulation failed to control pressure due to sulfur in the station equipment. | A new meter will be installed, customer has been engaged in the solution. Operating diagram shows the correct MAOP of 720psig. | Transmission | Near Hit | No | No | No | No | No | H-14 | GT.STAT.LVCR.0000000525
Near Hit | 127545132 | DI_BTW_RA07 | Diablo | 2023-12-06 |  | 60 | -60 | -100% | Slam Shut Activation | EQ | P5 | Slam shut activation | #NAME? | HP Distribution | Near Hit |  |  |  |  | Yes | H-14 | GD.STAT.DIST.00160
OP | 127584599 | MiniAT | Fresno | 2023-11-27 18:00 | 61.87 | 60 | 1.87 | 3.117% | Gas Contaminants - Sulfur | EQ |  | Regulation failed to control pressure due to sulfur in the station equipment. | - Monitor and regulator were rebuilt to replace the existing boots. - Regulator and monitor set points were lowered to ~55 psig, and 58 psig respectively. - MAOP verification efforts confirmed a 60 psig MAOP and overpressure event. - Consideration for this meter set to be converted to a transmission LVC functional location, operating diagram creation, and annual maintenance cycle. | HP Distribution | Small OP Event | Yes | No | No | No | No | H-15 | GD.SERV.FRES.01539.0001
OP | 127583287 | SF_SF_R196_PT3 | San Francisco | 2023-12-14 13:43 | 13 | 12 | 1 | 8.333% | Failure - Equipment | EQ | P50? | Third-Party work within proximity to LP station caused erratic regulator performance | Performed Class A Inspection at DR-144 Performed internal inspection at DR-196 Replaced Norval regulator at DR-196 to undergo further testing Performed customer equipment inspection per TD-4911P-02 based on Planning and DIMP recommendation. Calibrated all SCADA devices In October, slam shut and regulator sense lines were moved into the vault to prevent against potential third party construction damage. | Low Pressure | Small OP Event | No | No | No | No | No | H-14 | GD.STAT.LPRS. |  | 9 | 10.5 | 14
OP | 127622450 | SO_PET_R468 | Sonoma | 2023-12-15 | 50.07 | 50 | 0.07 | 0.14% | Gas Contaminants - Sulfur | EQ | P5 | Regulation failed to control pressure due to sulfur in the station equipment. | • Monitor and regulators were rebuilt to replace existing boots. • The pilot was cleaned and rebuilt, and new sulfur filters will be installed. • GPOM to consider increasing the maintenance frequency based on past station performance. | HP Distribution | Small OP Event | No | No | No | No | No | H-14 | GD.STAT.DIST.01251 |  | 44 | 47
Near Hit | 127786880 | ST_ION_M002_PT2 | Stockton | 2023-12-21 | 27 | 60 | -33 | -55% | Gas Contaminants - Sulfur | EQ | P5 | Slam shut activation | GPOM responded to return the customer to service - performed an A inspection - reset slam shut - adjusted set points @Muok, Rick, As discussed, below are recommended setpoints for US Mine #1 with the monitor Rockwell Sensus. V-3 Primary Cut set at 100 psig per design V-4 Monitor Rockwell at 26-28 psig. This is slightly above design setpoint due to start up issue with 24 psig where the monitor is not wide open. I am seeing abnormal PT2 fluctuation right now. So, if customer is using more gas, we could hit lo lo like before. Check to make sure that monitor is wide open. Please let me know if it’s wide open and we can discuss increasing along with TRV/Alarm and SS as necessary. V-5 final regulator at 20 psig per design Slam shut (V-3) at 40 psig per design TRV @ 32 psig per design. | Transmission | Near Hit | No | No | No | No | Yes | H-15 | GT.STAT.LVCR.0000000611 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0812909.pdf | 20 | 24 | 27
Near Hit | 127825556 | MI_ERE_ER11 | Yosemite | 2023-12-23 |  |  | 0 | #DIV/0! | Customer Shutdown | EQ | P5 | Slam shut activation | GPOM responded to return the customer to service | Transmission | Near Hit | No | No | No | No | Yes | H-15 | GT.STAT.LVCR.0000000668
Note on L4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Tab: OP Event Classification
Note on U4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Slam shut activation - started in 2023
Note on V4: Singer, Kevin D: N/A - Reg Stations did not contribute to OP Event

## Tracking2013 by Quarter (hidden)
3Q - 2013 OP Event Performance
| Q1 | Q2 | Q3 | Q4 | YTD | Yr-End
Expected Path: Goal OP events | 12 | 6 | 5 | 9 | 32 | 32
Amber Goal - Lowest end of range | 16 | 8 | 6 | 12 | 42 | 42
1Q Actual - All Events | 13 | 8 | 6 | 4 | 31 | 31
Asset Family OP Metrics
| Q1 | Q2 | Q3 | Q4 | YTD | Yr-End
Goal - HP Distribution | 2 | 1 | 1 | 2 | 6 | 6
1Q Actual - HP Distribution | 5 | 3 | 1 | 0 | 9 | 9
Goal - LP Distribution | 2 | 1 | 1 | 2 | 6 | 6
1Q Actual - LP Distribution | 0 | 1 | 1 | 1 | 3 | 3
Goal - Distribution Main Total | 4 | 2 | 2 | 4 | 12 | 12
1Q Actual - Distribution Main Total | 5 | 4 | 2 | 1 | 12 | 12
Goal - Distribution Services Total | 4 | 2 | 2 | 4 | 12 | 12
1Q Actual - Distribution Services Total | 5 | 4 | 2 | 1 | 12 | 12
Goal - Transmission | 8 | 4 | 3 | 5 | 20 | 20
1Q Actual - Transmission | 8 | 4 | 4 | 3 | 19 | 19
Goal - All Large Excursions1 | 3 | 3 | 2 | 3 | 11 | 11
1Q Actual - Large Excursions - HP Distrib | 2 | 1 | 1 | 0 | 4 | 4
1Q Actual - Large Excursions - LP Distrib | 0 | 0 | 1 | 0 | 1 | 1
1Q Actual - Large Excursions - Transmission | 3 | 0 | 1 | 1 | 5 | 5
1Q Actual - Total All Large Excursions | 5 | 1 | 3 | 1 | 10 | 10
Goal - All Equipment Failure | 4 | 3 | 3 | 3 | 13 | 13
1Q Actual - All Equipment Failure | 5 | 5 | 3 | 2 | 15 | 15
Goal - All Operator Error | 5 | 3 | 3 | 3 | 14 | 14
1Q Actual - All Operator Error | 7 | 3 | 2 | 2 | 14 | 14
Goal - At Compressor Stn or Storage | 1 | 1 | 1 | 1 | 4 | 4
1Q Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0
1 - Large Excursions are defined as:
HP Distribution = P ≥ MOP + 10%
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MOP + 10 psi
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Large Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2013 Q3 Goal
HP Distribution |  | 1
LP Distribution |  |  | 1
Transmission | 3 |  | 1
Grand Total | 3 | 1 | 2 | 2
Small Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2013 Q3 Goal
HP Distribution | 11
LP Distribution | 164
Transmission | 19 | 5 | 3
Grand Total | 194 | 5 | 3 | 3
Total OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2013 Q3 Goal
HP Distribution | 11 | 1 | 0 | 1
LP Distribution | 164 | 0 | 1 | 1
Transmission | 22 | 5 | 4 | 3
Grand Total | 197 | 6 | 5 | 5
Metric Comparison - Prior Years - 3rd Quarter
OP Events by Apparent Cause - Third Quarter
2013 Total OP- 5 Events as of 9/30/13 |  |  |  |  | 2013 Large Excursion OP Events - 2 Events
Large Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2013 Q2 Goal
HP Distribution | 5 |  | 1
LP Distribution | 1
Transmission | 6 | 2
Grand Total | 12 | 2 | 1 | 3
Small Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2013 Q2 Goal
HP Distribution | 7 |  | 2
LP Distribution | 147 | 46 | 1
Transmission | 29 | 14 | 4
Grand Total | 183 | 60 | 7 | 3
Total OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2013 Q2 Goal
HP Distribution | 12 | 0 | 3 | 1
LP Distribution | 148 | 46 | 1 | 1
Transmission | 35 | 16 | 4 | 4
Grand Total | 195 | 62 | 8 | 6
Metric Comparison - Prior Years - 2nd Quarter
OP Events by Apparent Cause - Second Quarter
2013 Total OP- 8 Events as of 7/2/13 |  |  |  |  | 2013 Large Excursion OP Events - 1 Events
Large Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2013 Q1 Goal
HP Distribution | 1 | 2 | 2
LP Distribution | 1 |  | 0
Transmission | 12 | 1 | 3
Grand Total | 14 | 3 | 5 | 3
Small Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2013 Q1 Goal
HP Distribution | 4 | 2 | 3
LP Distribution | 172 | 179 | 0
Transmission | 29 | 44 | 5
Grand Total | 205 | 225 | 8 | 9
Total OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2013 Q1 Goal
HP Distribution | 5 | 4 | 5 | 2
LP Distribution | 173 | 179 |  | 2
Transmission | 41 | 45 | 8 | 8
Grand Total | 219 | 228 | 13 | 12
Metric Comparison - Prior Years - First Quarter
OP Events by Apparent Cause - First Quarter
2013 Total OP- 13 Events as of 3/31/13 |  |  |  |  | 2013 Large Excursion OP Events - 5 Events

## Fact Finding (hidden)
Purpose
This document established the fundamental guidelines for questions to investigate to determine the apparent cause of an over pressure event.
The responses to the questions will be incorporated into the over pressure event report, prepared by Gas Control Operations Engineering.
This is an all-encompassing list; some questions may not apply to all over pressure events.
Equipment condition
The following questions are asked to establish the equipment condition and maintenance history of the equipment:
1. Review maintenance Records for the past five (5) years and the latest District Reg Data Sheet
2. When was the station built? To understand the standard design used
3. According to the maintenance records does this station have a history of issues? Sulfur, Water, Lock up?
a. Was there anything discovered in the regulators such as a debris, sulfur, or water?
b. What was the problem with the regulator? Did the monitor catch a potential over pressure?
4. What is the model and manufacturer of the regulator? If Mooney reg, what was the pressure difference across the reg, below 100 psig?
a. Review MPR for equipment type to see if there are known issues
5. When was the gauge last calibrated? What is the gauge serial #?
6. Was the correct spring color installed in reg and monitor?
7. Were there any hard to operate valves involved in the OP event?
8. Is there a history of vault flooding (water lines on vault walls, pumping history)?
a. Are the vents to the top of vault or above ground?
9. Were there any jobs that were recently completed at this location or in the vicinity? If so, what type of work was done?
10. Has hydro testing been completed in the area or upstream piping recently?
a. What were the dew point measurement readings of those projects?
11. When were any ILI activities completed on the upstream piping?
12. Review commissioning documentation or PSSR documentation
13. Was there excessive corrosion on the inside of the piping or equipment?
14. What were the results from MCTL?
15. Is there additional information subsequent to the borescope if completed?
16. Provide necessary pictures.
Overpressure Response
The following questions should be reviewed with the first responder and/or team who responded:
1. What was in control upon arriving to the site - Regulator or Monitor? And what were the As Found set points?
2. How was the station set up upon arrival (as far as valving is concerned in relation to the OP Diagram)?
3. If repairs were done during the incident, what type of repair and/or maintenance was completed?
4. Was the D/S pressure gauged during inspection?
5. How was communication with the control room handed off? Responsible party? GDCC/GTCC?
6. Was the vault flooded when arriving on site?
7. Was there ice formation on the outside of the reg or monitor?
8. Was any ice or debris found inside the reg or monitor?
IF debris was discovered THEN:
a. Can you send it to the Measurement Control Test Lab?
b. Could you take some photos of the debris?
c. Was there any debris found in the monitor and filter? If so, take some photos of the debris?
d. What type of filter was installed at the station? Model and Make?
e. Was a Bore Scope performed? If so, what was the finding?
9. Was the filter properly installed? Seals properly seated?
10. What are the set points of the regulators as found/as left?
a. What valves are being referred to in correlation to the operating diagram?
b. Were the regulators and monitors in good working condition?
11. Was the sensing lines soap tested for leaks? If leak(s) found, where was the leak(s) located?
12. What type of bypass was utilized – hard bypass or temporary bypass? With U/S filter?
13. What time did you arrive on site?
System Operation
The following questions are asked to establish the equipment condition and maintenance history of the equipment:
1. What other regulator station(s) feeds this HIS/System?
2. Which ones were addressed by the field technician (upon their field visit)?
3. What is the MAOP/MOP downstream of the regulator set/customer side?
a. What is the set point of the regulator/monitor/relief valve/over pressure protection?
b. Any indication of internal or external irregularity in the reg set?
c. If a bypass was used, what was the size (diameter) of the bypass?
4. What is the upstream MAOP/MOP?
5. If SCADA is not installed where is the nearest SCADA location?
6. Is there any a paper chart record?
Clearance
The following questions are to be asked to investigate the nature of work being performed:
1. Was there a clearance associated to the event? If so, what is the clearance number?
a. Identify when clearance was written and approved in relation to work being executed, this should not be less than 10 days.
b. Which step did the overpressure occur during?
2. What did the JSSA address prior to starting the work? If so, what was mentioned during the safety tailboard (overpressure)?
a. Obtain a copy of the JSSA
3. When Gas Control Center called regarding the MOP excursion at which step where the crew performing? Simplified question – What was the last clearance step that was completed before the OP excursion?
4. Was a pre-clearance meeting and walk-down done before the work clearance started? Was it a thorough review and discussion?
5. Were the roles and responsibilities clearly defined before the clearance work was started? (Who is the clearance supervisor? Crew member location and responsible clearly defined?)
6. During the clearance work, were there any deviations from the clearance steps? If so, why and was it approved by clearance supervisor/gas control center?
7. Did the clearance have a local approver?
8. Could you anticipate the system response before executing each step? – Did you know what was supposed to happen to the system after executing each step?
Human Performance
The following questions are to be asked to investigate the influence of human performance:
1. What jobs did you have scheduled for the day?
a. Where there time pressures to complete any other work?
b. What day and time did the overpressure occur?
c. How long have people been on the job?
2. Was the field personnel OQ or had validated OQ listed in their record?
3. What documentation were you given prior to arriving on jobsite?
4. What is your familiarity with the job site and the station?
5. Were there traffic, noise, or other environmental issues or concerns?
a. What was the weather like on the day of the incident?
6. Did you call Gas Control and/or Supervisor prior to starting the job?
7. Are the drawings (Operating Diagram, P&ID, Operating Map, etc.) accurate and representative of the facility? (Submit a CAP for corrections)
8. How was your physical condition (Sick, stress, medication, tiredness, alertness and distractions)?
9. Where there other steps besides the normal approved practices used to respond to this issue? (e.g. shop made tools, shortcuts, tasks that have been done in the past but are not routinely done)
10. What do you think would have made this event have a different and positive outcome?

## Sheet1 (hidden)
Date | Title | System Pressure | Excursion type | Event Brief | Apparent causes | Latest Update
2015-01-12 | Alameda Hospital | LP Distribution | Large | Maintenance during customer on bypass | • Contaminants found in bypass regulation
11/8/14 AF (1/13/15) | Sunsweet Dryer - Orland | HP Distribution | Large | Dead-end customer system | • Mooney low/no flow conditions • Regulator/Monitor failure • Contaminants | • Immediate response to alleviate pressure excursion; leak survey to be conducted, and maintenance on HPR set. • Replacement of main and service piping pending assessment
2015-01-07 | Fresno Junction Station | HP Distribution | Large | Complete reg and monitor failure | • Weld slag/debris contaminants in regulator body • Water & Ice inside the pilot body • Deformation and damage to the pilot seal stem and rubber plug • Sulfur-gon filter restriction and moisture | • Immediate corrective actions were taken to address risks from overpressure event • In the process of reviewing potential future station/and area preventative recurrence • Analyzing system-wide actions
2015-01-04 | Gosford Road Station | Transmission | Small | Clearance procedure not followed during welding operations | • Clearance procedure not followed • Clearance procedure does not specify ‘not to exceed’ MOP pressure | • Field took immediate actions to reduce pressure under MAOP • Event did not require additional mitigative action
2014-12-25 | Amador Station | Transmission | Small | Regulator failed to hold set point | • Contaminants • 5/20 rule not implemented | • Upon arrival field took immediate actions to reduce pressure under MAOP
2015-01-07 | PLS 4B | Transmission | Near Hit | Relief valve activation - unknown cause | • Possibly vibrations impacting pilot operation | • New relief valve have been requested by engineering
1/13/15, 1/6/15, 12/31/14 | Indian Springs PLS L401 | Transmission | Near Hit | Required CROP maintenance has resulted in various events | • Trimmer valve V-12 positioner/3-way failure • Procedure/set-up because of ongoing maintenance work • Inadvert valve operation | • Replaced entire pilot valve assembly of V-12 was completed
1/6/15 9/10/14 | CEMEX (Black Mountain Station) | HP Distribution | Near Hit | Dead-end customer system with equipment issues | • Regulator boot damage • Regulator/monitor equipment design | • Replaced damaged boots, will look to upgrade regulators in 2015 • Current review of similar customer stations by Engineering
1/7/14 1/13/14 | Corning | HP Distribution | Large | Regulator failed to hold set point after liquid surge | • Contaminants • Regulator/Monitor failure | • Establish schedule to monitor the station • Recently installed filter separator
2014-01-10 | Topock Station | Transmission | Large | Atypical operating conditions with split compression and discharge | • System operating mode (Split Station) • Valve Operation to reinitiate L300B flow at the Station | • CAP conducted a Cause Evaluation • Further analysis will be conducted - Process Hazard Analysis
2014-08-04 | Dolan Road | Transmission | Large | Clearance procedure created dead-end system through valving | • Review of Clearance (Closing of isolation valve) • Monitor/Regulator slow reaction time | • A 20% pressure reducation was issued • Crew bleed the pressure down below the MAOP limit
2/14/14 3/5, 8/16, 8/19, 8/20 | Acacia Station | Transmission | Large, Near Hit | Pressure build up on intermediate piping created a dead-end system | • No load demand • Monitor/Regulator set point too close to MOP/HIHI • Station Design | • Reconfiguration of station has been proposed • Regs set points have been adjusted in the 2nd Stage Reg Pit
3/5/14, 3/19, 3/22, 9/26, 11/20, 12/16 | Los Medanos Ryer Island | Transmission | Near Hit | Pressure build up due to automated BTU valve regulating based on % Nitrogen; in addition, power outage causing the regs to fail to its last position | • BTU operated valve shut in due to BTU ratio • Power outage at the station and regs failed to the last position | • New uninterruptible power supply has been submitted for emergent funding • Departmential discussion has been initiated for potential improvements (PLE and Control Engineering)
2/12/14, 2/14, 3/4, 3/5 | Los Banos D/S | Distribution | Near Hit | Reoccurring calibration & communication issues with pressure transducer | • Problematic pressure transducer | • New transducer was order and replaced the existing pressure transducer
1/23/14, 3/12, 11/18, 11/20 | Brentwood Terminal | Transmission | Near Hit | Various work/maintenance contributed to the pressure build up within the station | • Leaking valve • Operator inadvertently entered incorrect pressure • Hand throttling valve | • Lesson Learned were identified and discussed with Control Center Management • Valves were greased to reduce leakage
8/31/14, 11/20 | Kettleman Compressor Station | Transmission | Near Hit | Valve operation during the initial phase of compressing pressure | • Valve reaction time when open/close during compression operation • Valve operation by operator | • Tailboard/Lesson Learned concerning compression process at Kettleman
3/13/14, 4/30 | Redding Tap | Transmission | Near Hit | Low pressure differential across of regulation | • Low flow condition/pressure differential - pressure across the regulator and monitor equalize | • Set point pressure adjusted • Validate regulator differential pressure requirements on manufacturer specs
Common Themes
• There has been a recent rise in equipment failures and contaminants found in regulation potentially due to winter flow patterns (Sunsweet, Fresno Junction, Amador) • Process as it relates to maintenance, construction, and special operations with regard to clearances and pressure limitations have been more frequent (Indian Springs, Fresno Junction, Gosford) • Industrial seasonal customer operations causing increased pressure scenarios (Sunsweet, CEMEX)
cold weather potential causes freezing effects, higher flows move debris and liquidds, larger differential b high and large flows make reg different
Medium/Long Term Corrective Actions
• PHA will be performed on large seasonal distribution customers off transmission lines (optimal use of relief valves) • Validation of current pressures of large seasonal distribution customers off transmission lines - through electronic recording devices • Clearance strategy session to enhance existing guidelines about various clearance issues (local review, best practices, special instructions, control room notification) • Develop further field training for instructions on servicing regulation • Mooney regulator/monitor risk analysis

## OP SAR (hidden)
Q1
OP Events | Jan | Feb | Mar | Q2 | Q3 | Q4 | YTD | Target
[15 empty] | 2014 | 2015 | 2016 | 2017 YTD
Goal - Total Events | 8 | 0 | 0 | 2 | 3 | 3 | 8 | 16 |  |  |  | Total OP Events |  |  | 18 | 29 | 18 | 2
Actual - Total All Events | 0 | 0 | 0 | - | - | - | 0 | 16 |  |  |  | Equipment Failure |  |  | 5 | 5 | 4 | 1
[12 empty] | Contaminants |  |  | 5 | 4 | 3 | 1
Goal - Large Excursions | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8 |  |  |  | Human Performance |  |  | 8 | 20 | 11 | 0
Actual - Total All Large | 0 | 0 | 0 | - | - | - | 0 | 8 |  |  |  | Human Performance Cause Breakdown
[12 empty] | GPOM |  |  | 2 | 10 | 6 | 0
[12 empty] | GC M&C |  |  | 1 | 2 | 1 | 0
Q2 | [11 empty] | Gas Control |  |  | 1 | 0 | 1 | 0
OP Events | Q1 | Apr | May | Jun | Q3 | Q4 | YTD | Target |  |  |  | Clearance Preparation |  |  | 2 | 3 | 2 | 0
[12 empty] | Engineering Design |  |  | 2 | 5 | 1 | 0
Goal - Total Events | 8 | 0 | 1 | 1 | 3 | 3 | 10 | 16
Actual - Total All Events | 2 |  |  |  | - | - | 2 | 10 |  |  |  | Near Hits |  |  | 123 | 199 | 136
[12 empty] | Equipment Failure |  |  | 19 | 35 | 61
Goal - Large OPs | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8 |  |  |  | Human Performance |  |  | 104 | 164 | 75 |  |  | ------->
Actual - Total All Large | 0 |  |  |  | - | - | 0 | 4
3q | [13 empty] | High Exposure Events and Near Hits
OP Events | Q1 | Q2 | Jul | Aug | Sep | Q4 | YTD | Target | [5 empty] | 2013 | 2014 | 2015 | 2016 | 2017 YTD
[14 empty] | 38 | 34 | 25 | 21 | 1
Goal - Total Events | 8 | 2 | 1 | 1 | 1 | 3 | 13 | 16
Actual - Total All Events | 0 |  |  |  | - | - | 0 | 3
Goal - Large OPs | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8
Actual - Total All Large | 0 |  |  |  | - | - | 0 | 8
Indiv
4q | [12 empty] | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
[12 empty] | 2015 Actual | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 5
OP Events | Q1 | Q2 | Q3 | Oct | Nov | Dec | YTD | Target |  |  |  | 2017 Target | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 16
[12 empty] | 2017 Actual | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Goal - Total Events | 8 | 2 | 3 | 1 | 1 | 1 | 14 | 16
Actual - Total All Events | 0 |  |  |  | - | - | 0 | 2 |  |  |  | 2015 versus 2016 Comparison
[13 empty] | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | ------->
Goal - Large OPs | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8 |  |  |  | 2015 Actual | 3 | 5 | 7 | 8 | 10 | 11 | 14 | 17 | 20 | 23 | 25 | 30
Actual - Total All Large | 0 |  |  |  | - | - | 0 | 8 |  |  |  | 2016 Target | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 14 | 16
[12 empty] | 2016 Actual | 2 | 2 | 2 | 3 | 3 | 7 | 8 | 11 | 11 | 14 | 16 | 18
[12 empty] | 2017 Targets | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 14 | 16
[12 empty] | 2017 Actual | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OP Events (thru November) | Q1 | Q2 | Q3 | Oct | Nov | Dec | YTD | Target
Goal - Total Events | 5 | 3 | 3 | 1 | 2 | 2 | 14 | 16
Actual - Total All Events | 2 | 5 | 4 | 3 | 2 | - | 16 | 18
Goal - Large OPs | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 4 | Large Excursion Events 2016
Actual - Total All Large | 0 | 4 | 2 | 2 | 1 | - | 9 | 11
[10 empty] | Date | Location |  | 4: Description
[10 empty] | 2016-04-07 11:53 | Swingle Junction L172 |  | 4: No clearance, improper isolation to perform leak repair work
[10 empty] | 2016-06-02 13:00 | Customer - Olam Spices |  | 4: Regulator and monitor failure due to contaminants, filter not installed correctly
[10 empty] | 2016-06-23 11:35 | Dolan Rd L301B |  | 4: Clearance failed to address regulation return to service risk
[10 empty] | 2016-06-27 09:24 | Floral Ave HPR, Selma |  | 4: Leaking bypass on HPR, relief valve did not operate due to wrong spring, not mapped in GT-GIS
[10 empty] | 2016-07-16 18:18 | Customer - Kagome Foods |  | 4: Equipment failure due excessive time in service, and oversized for the application
[10 empty] | 2016-08-10 15:00 | Leonard Ave HPR, Fresno |  | 4: Equipment failure due to contaminants
[10 empty] | 2016-10-14 | North Sac Holder DFM |  | 4: Causal Evaluation not complete
[10 empty] | 2016-10-30 | Customer - Sensient Foods |  | 4: Regulation equipment failed to protect downstream system after hot shut down of customer equipment
[10 empty] | 2016-11-03 | Stanley Blvd & Bernal Ave |  | 4: Crew did not follow special instructions prior to starting clearance, pinched plastic main d/s of regulator station
Note: the list below is associated with YTD OP Events (don’t delete)
Actual
Amber Goal
Monthly OP Goal

## Large_Largest Excursion Events (hidden)
LAST UPDATE 4/4/16
Large OPs
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016
Transmission | 7 | 2 | 4 | 3 | 2 | 1
HP Distribution | 7 | 1 | 3 | 2 | 2
LP Distribution | 3 | 0 | 0 | 0 | 1
Largest OPs
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016
Transmission | 1 | 1 | 0 | 0 | 0
HP Distribution | 3 | 3 | 1 | 2 | 1
LP Distribution | 0 | 0 | 1 | 0 | 1
Total Large OPs
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016
Transmission | 8 | 3 | 4 | 3 | 2 | 1
HP Distribution | 10 | 4 | 4 | 4 | 3 | 0
LP Distribution | 3 | 0 | 1 | 0 | 2 | 0

## Monthly Tasks (hidden)
Legend
|  |  |  | D | Day
Monthly |  |  |  | M | Monday
1D | Send out OPE Agenda & Action item List for upcoming OPE meeting |  |  | T | Tuesday
1D | Send out OP Action Items Tracking for status due EOW These are the 10 items OP is responsible for completing by EOY, Frank to review during OPE |  |  | Th | Thursday
1T | Review OP event ACE reports from prior month - and emphasis SMEs to present discussions for the benefit of the group |  |  | F | Friday
1Th | Order lunch for next weeks meeting |  |  | LD | Last Day
1F | Compile metrics from prior month and report to KTS/BPR, this also updates the stats for the OP agenda |  |  | W | Week
1F | Send out 1-pager of OP Events YTD to OPE and Dan
1W | Resolve questions about reports from review meeting (1T)
1W | Session D monthly updates is mainly to discuss progress and any roadblocks you may have in completing the various mitigations within the committed timeframes with Mary & Venetia
1W | Summarize events for the Weekly Items of Interest Bulletin | AMFQ
2T | OPE Meeting to review reports (1T), statistics (1F), and Action items (1W)
2F | Send out OPE Agenda with notes from meeting
2W | Resolve questions about reports from OPE
2W | Input tasks and corrective actions from OPE into CAP
3W | Resolve questions about reports from OP events
3W | Send email to Frank & Dan for approval to close out near hits and event notifications as necessary. | complete versus closure
3W | Perform QA Process: - Are site specific updates complete? - Any system wide C/A moving forward? - Does OP approve report & ACE?
4W | Resolve questions about reports from OP events
4W | Confirm if any reports need to be 'Final' within 60 days of initiation
LD | Pull MTD Dashboard report that shows closed/risk rank CAP
Long Term
2W of 1st, 4th, 7th, and 10th Month | Compile metrics for quarterly report, review past reports, and develop material to deliver - work with OP SAR
OP SAR | April 29th
45D | After events are presented in OPE - focus on report _Final

## Roles (hidden)
GCSS Roles and Responsibilities for OP Events and Transmission Near Hits |  |  | clarity as of 1/8/16
Receive notification of event - epage or other (SRDC email, AIR updates)
Enter the event into excursion master tracking list
Ensure CAP notification is created for event
48-hour report created for event
Quick hit email to notify others of event and provide 48-hour report
This is sent to OPE team, and steering committee to distribute as they see fit
Review OP event report in GCSS event report review meeting
Week prior to OP elimination team meeting
Review OP event report in OP Elimination team meeting
2nd Tuesday of month (See Monthly tasks page)
Finalize OP event report - post to share point using correct file naming convention
within 45 days of presenting at OPE
Enter system wide corrective actions
and event-specific corrective actions into CAP for the event
Perform QA on CAP notification - scope of QA is that the tasks resolve the overpressure event
Close CAP notification upon completion of Quality Assurance in above step
if OP Event, director/steering committee provides QA
if Near Hit, manager provides QA
Request clarification from manager/director steering committee to complete (checkered flag) CAP notification
If CAP notification closed by others, evaluate quality of CAP item contents (see QA step above)
Correct if necessary, and continue through process
Track and trend OP event statistics
Provide monthly updates to the metrics processes as required (Monthly)
Report our on OP event statistics to Gas Operations
Prepare OP SAR meeting materials as directed

## Clearances (hidden)
CLEARANCE COUNTS | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | Total
2014 GT SYSTEM MAINTENANCE | 183 | 203 | 161 | 133 | 204 | 102 | 105 | 152 | 177 | 231 | 197 | 179 | 2027
2014 GT SYSTEM NEW | 37 | 22 | 61 | 65 | 51 | 35 | 48 | 73 | 65 | 99 | 85 | 69 | 710
2015 GT SYSTEM MAINTENANCE | 177 | 221 | 267 | 247 | 275 | 254 | 258 | 248 | 304 | 276 | 251 | 242 | 3020
2015 GT SYSTEM NEW | 40 | 40 | 67 | 43 | 61 | 54 | 73 | 82 | 69 | 91 | 98 | 95 | 813
2016 GT SYSTEM MAINTENANCE | 271 | 278 | 374 | 362 | 316 | 277 | 283 | 325 | 289 | 282 | 369 | 300 | 3726
2016 GT SYSTEM NEW | 96 | 140 | 108 | 159 | 114 | 83 | 131 | 146 | 127 | 114 | 103 | 78 | 1399
2017 GT SYSTEM MAINTENANCE | JAN: 262; FEB: 156; MAR: 423; APR: 385; MAY: 303; JUN: 272; JUL: 285
2017 GT SYSTEM NEW | JAN: 73; FEB: 87; MAR: 115; APR: 92; MAY: 180; JUN: 100; JUL: 137

## Contact List (hidden)
Department | Name | E-mail | Phone | Cell
Asset Knowledge Management - T & D | Cleveland, Nicole | NEB6@pge.com | 925-328-6366 | 925-322-3311
Codes & Standards - T&D | Davidson, Matt | MEDm@pge.com | 925-328-5763 | 925-324-8201
Compliance | Bradley, Mike | M0Bj@pge.com | 925-328-5724 | 925-967-8371
Construction - T&D | Leverett, Ross | RALw@pge.com | 209-576-6586 | 209-608-9276
DIMP | Stockand, Rich | RMSf@pge.com | 925-244-3104 | 415-412-2854
Engineering & Design - T | Chan, Jonathan | J4Cb@pge.com | 925-244-3205 | 925-788-6114
Engineering & Estimating - D | Rouainia, Ghandi | GXRp@pge.com | 925-244-3047 | 510-292-6857
ERX - Evaluate for Installation | Gupta, Nishal | NXGg@pge.com | 925-244-4535 | 415-349-9827
ERX - Connect to Control Room | Sweeney, Jeff | JK10@pge.com | 925-244-4539 | 925-334-0544
FIMP - Initiative Owner | White, Terry | TGW5@pge.com | 925-244-3323 | 925-285-6781
FIMP | Ross, Tim | TRR0@pge.com | 925-244-3344 | 925-817-9441
FIMP | Singer, Kevin | KDSd@pge.com | 925-328-5740 | 925-324-2289
FIMP | Shahab, Rehan | ROS8@pge.com | 925-328-5725 | 925-719-0534
FIMP | Herrmann, Corine | C2Hh@pge.com | 925-244-3797 | 925-222-0442
FIMP | Yee, Gary | GLY1@pge.com | 925-244-3196 | 925-817-0068
FIMP | Morshead, Roger | RKM3@pge.com | 209-932-6558 | 209-608-1049
FIMP - MCTL | Pace, Matt | MBP9@pge.com | 925-674-6738 | 925-586-3985
FIMP - Station Assessment | Rovella, Troy | TMRn@pge.com | 925-974-4023 | 415-666-6086
Gas Systems Operations | Maxwell, Frank | FWM1@pge.com | 925-244-4536 | 415-260-7956
Gas Systems Operations - Clearances | Quijalvo, Roberto | RBQ2@pge.com | 925-244-4572 | 415-314-5730
Gas Planning | Brown, Rick | RCB3@pge.com | 925-244-3102 | 415-264-2122
Gas Stewardship & LCC | N/A
GPOM - Sulfur Filters | Johnson, Lance | LEJ5@pge.com | 925-381-0756 | 925-381-0756
GPOM - Sulfur Filters | Hernandez, Nicolyn | NDH2@pge.com | 925-551-1813 | 925-551-1813
GPOM | Ball, Kelly | KLBp@pge.com | 408-204-5340 | 408-204-5340
GPOM | Tonetti, Curtis | CLTb@pge.com | 530-351-3570 | 530-351-3570
Investment Planning - T&D | Rizo, Hazzel | HMR2@pge.com | 925-244-3117 | 415-244-0963
Mapping
OQ | Bradley, Mike | M0Bj@pge.com | 925-328-5724 | 925-967-8371
Project Management - D | Saffarzadeh, Samira | S8Sb@pge.com | 408-205-8101 | 408-205-8101
Project Management - T | Khairi, Sam | S3Kk@pge.com | 925-244-3932 | 925-404-4067
Safety Quality and Contract Management | Ramirez, James | JAR2@pge.com | 925-328-5796 | 805-441-5444
SCADA Visibility | Gaebler, George | GEG4@pge.com | 925-244-4545 | 510-612-1671
SPEC Services (Supporting Contractor) | Russo, Ed | erusso@specservices.com | 714-415-7002 | 714-914-7895
SPEC Services (Supporting Contractor) | Black, Kevin | kblack@specservices.com | 562-619-5269 | 562-619-5269
TIMP | Liu, Calvin | C1Li@pge.com | 925-244-3353 | 925-719-4293
Training
CRM | Rakin, Dante
Process Safety | Sass, Stephen
Process Safety | Rengifo, Carlos