## Use cases with requirements
| Final - tags | [7 empty] | Requirements | [5 empty] | Communication Paths
Use Case | V1G | V2G | Agg | No-Agg | Frag | Uni | Oth | Actors | Functional Communication Requirements | Non-Functional Communications Requirements | Customer Requirements | Other Requirements | Alternatives | Power Conversion | NSP to BMS | NSP to EVSE | NSP to EV | NSP to Customer | BMS to EVSE | BMS to EV | BMS to Customer | EVSE to EV | EVSE to Customer | EV to Customer | Cell Optins
Name of use case reviewed by Use Case Sub-Working Group | Indicate which tags the Sub-Working Group agreed to. These tags are described in the VGI Roadmap available at: https://www.caiso.com/Documents/Vehicle-GridIntegrationRoadmap.pdf. | [6 empty] | All actors involved in the use case | What must happen to specifically execute the use case | What overall requirements are necessary that are not specifically related to executing the use case | Requirements for customer control or engagement |  | Alternative ways to execute the use case that do not require a communications protocol | Please state whether the EVSE or the PEV controls the power flow.
Demand Fee Mitigation, in public charging at a commercial building | X |  | X |  |  | X |  | Building Site Controlller/EMS, Site meter, PEV, Customer, EVSE | 1) The Site Controller shall be able to send a command to the EV to reduce the energy in a deterministic manner 2) The Site Controller shall be able to obtain the current Energy for each EV 3) If the Site Controller is managing the Demand charge for the Site, the Site Controller shall be able to obtain the total site energy 4) The Site Controller should obtain the Customer Requirements from the EV or Customer | 1) The communications between the Site Controller and the EV should be secure 2) Site Controller and EV could negotiate power levels based upon pricing curve (such as paying more for a higher power or earlier departure time). 3) Site Controller could be software based and reside within the EVSE, provided as a cloud service, or the physical hardware device connected to the EVSEs onsite. 4) Site Controller communication patheway could be directly to EV or to EVSE which relays, translates, or negotiates with EV. | 1) Should be able to opt in or out of event at the EV or or Site Controller 2) Should be able to enter departure time and needed SOC or miles needed at the EV or Site Controller | 1) Site controller could connect to Network Service Provider regardless of how implemented onsite | 1) For non-communication PEV, Site Controller could manage the PEV load by using the EVSE J1772 Control |  | Optional | None | None | None | Alternative | Primary | Secondary | None | None | Secondary | Primary
PEV0 - Customer Attributes | X | [6 empty] | PFE, EVBS, Energy Meter, EV Driver | PFE [ESI] sends energy available to EVBS [PEV]. This includes amount and charging rate. The PFE [ESI] and EVBS [PEV] shall exchange information, so the EVBS [PEV] can display the cost per distance. The PFE [ESI] and EVBS [PEV] shall send information such as connection start, desired charge start, desired charge finish and expected connection end Fixed or mobile Energy Meter [EUMD] sends energy used to PFE [ESI] The PFE [ESI] and EVBS [PEV] shall send Program information, such TOU (time of use rate), RTP (real time pricing) and CPP (critical peak pricing). | EV Driver & EVBS [PEV] sends energy request to PFE [ESI]. This includes amount and charging rate. | The EV Driver [customer] could input departure time, desired price to charge, desired energy quantity | An ECS EV [EVSE] with multiple ports would require multiple Energy Meter [EUMDs] to associate and record energy transferred to each EVBS [PEV] for the energy transfer session. |  | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary | Optional
PEV1 - Utility Provides Services to PEV Customer | X | [6 empty] | AES – See ESCO Charger Clearinghouse Control Device Customer Customer Account Customer Energy Management System Electric Vehicle Supply Equipment (EVSE) Energy Portal (EP)/Smart Energy Portal (SEP) Energy Services Communication Interface (ESCI) See ESI for similarities ESI End Use Measurement Device (EUMD) ESCO – See AES Guest PEV, EV, PHEV Roaming Utility Utility | The unique ID shall be communicated from the EVBS [PEV] to PFE or BMS. The Utility shall be able to determine EV Driver [customers]/EVBS [PEV] not enrolled in EVBS [PEV] program. PEV shall be plugged into Energy Portal (i.e. PEV in ‘On Plug’ state) prior to participating in communications session with ESCI. PEV shall be able to charge upon plugging into Electric Vehicle Supply Equipment (EVSE) enabled 120V or 240V AC Energy Portal (with or without communications established with utility). The Energy Services Communication Interface (ESCI) shall exist at the customer premise and be capable of communicating to the Utility and can communicate to the PEV and End Use Measurement Device (EUMD) to facilitate exchange of authentication and charging session information. PEV, EUMD, and Energy Services Communication Interface shall be able to establish a secure communications link. If ESCI communications cannot be established between PEV and Utility within a configurable period of time after ‘on plug’ state, charging will proceed (according to customer preferences) with all charges accruing to premise customer account according to that customer’s regular utility rate. PEV shall be capable of communicating with ESCI. PEV is capable of communicating with the Utility through an ESCI. PEV shall be capable of providing to the ESCI its unique PEV ID upon initiation of a communications session between PEV and ESCI. ESCI shall be able to provide the Premise ID to the Utility (along with PEV ID provided by PEV) for validation/verification. The Utility shall be able to verify that usage attributable to PEV charging is sourced from the same customer/premise that has provided the ESCI for PEV-to-Utility communications (e.g., Load correlation to ESCI communications). The Utility shall be able to send a confirmation message via ESCI to PEV to indicate authentication of PEV ID and Premise ID information, establishing a successful PEV/ESCI binding. PEV is capable of receiving a confirmation message from Utility via ESCI establishing valid charging session. This indication can in turn be made available to customer to indicate that communications session has been successfully established. PEV shall be able to receive utility authentication parameters (as necessary) upon initial binding with ESCI, or upon change of utility authentication parameters. PEV shall be able to send message to Utility via ESCI acknowledging successful authentication and completion of initial setup of PEV according to utility PEV program. EUMD is required to discretely measure usage provided for PEV charging. EUMD function can be inclusively located anywhere in a zone from the PEV and the branch circuit panel connection. EUMD shall be capable of communicating with the Utility through an ESCI The Utility shall be able to send a discovery message via ESCI to EUMD to indicate authentication of PEV ID and Premise ID information, establishing a successful PEV/ESCI binding. EUMD is capable of receiving a discovery message from Utility via ESCI establishing valid charging session. This indication can in turn be made available to customer to indicate that communications session has been successfully established. EUMD shall allow for remote reconfiguration of energy measurement interval length. EUMD shall be able to receive utility authentication parameters (as necessary) upon initial binding with ESCI, or upon change of utility authentication parameters (e.g. usage measurement interval). EUMD shall be able to send message to Utility via ESCI acknowledging successful authentication and completion of initial setup of EUMD according to utility PEV program. Re-establishment of PEV – Utility communications session (following initial enrollment and setup) can be achieved without full authentication and discovery steps as required for initial session. | The unique ID shall be communicated from the EVBS [PEV] to PFE or BMS. The Utility shall be able to determine EV Driver [customers]/EVBS [PEV] not enrolled in EVBS [PEV] program. PEV shall be plugged into Energy Portal (i.e. PEV in ‘On Plug’ state) prior to participating in communications session with ESCI. PEV shall be able to charge upon plugging into Electric Vehicle Supply Equipment (EVSE) enabled 120V or 240V AC Energy Portal (with or without communications established with utility). The Energy Services Communication Interface (ESCI) shall exist at the customer premise and be capable of communicating to the Utility and can communicate to the PEV and End Use Measurement Device (EUMD) to facilitate exchange of authentication and charging session information. PEV, EUMD, and Energy Services Communication Interface shall be able to establish a secure communications link. If ESCI communications cannot be established between PEV and Utility within a configurable period of time after ‘on plug’ state, charging will proceed (according to customer preferences) with all charges accruing to premise customer account according to that customer’s regular utility rate. PEV shall be capable of communicating with ESCI. PEV is capable of communicating with the Utility through an ESCI. PEV shall be capable of providing to the ESCI its unique PEV ID upon initiation of a communications session between PEV and ESCI. ESCI shall be able to provide the Premise ID to the Utility (along with PEV ID provided by PEV) for validation/verification. The Utility shall be able to verify that usage attributable to PEV charging is sourced from the same customer/premise that has provided the ESCI for PEV-to-Utility communications (e.g., Load correlation to ESCI communications). The Utility shall be able to send a confirmation message via ESCI to PEV to indicate authentication of PEV ID and Premise ID information, establishing a successful PEV/ESCI binding. PEV is capable of receiving a confirmation message from Utility via ESCI establishing valid charging session. This indication can in turn be made available to customer to indicate that communications session has been successfully established. PEV shall be able to receive utility authentication parameters (as necessary) upon initial binding with ESCI, or upon change of utility authentication parameters. PEV shall be able to send message to Utility via ESCI acknowledging successful authentication and completion of initial setup of PEV according to utility PEV program. EUMD is required to discretely measure usage provided for PEV charging. EUMD function can be inclusively located anywhere in a zone from the PEV and the branch circuit panel connection. EUMD shall be capable of communicating with the Utility through an ESCI The Utility shall be able to send a discovery message via ESCI to EUMD to indicate authentication of PEV ID and Premise ID information, establishing a successful PEV/ESCI binding. EUMD is capable of receiving a discovery message from Utility via ESCI establishing valid charging session. This indication can in turn be made available to customer to indicate that communications session has been successfully established. EUMD shall allow for remote reconfiguration of energy measurement interval length. EUMD shall be able to receive utility authentication parameters (as necessary) upon initial binding with ESCI, or upon change of utility authentication parameters (e.g. usage measurement interval). EUMD shall be able to send message to Utility via ESCI acknowledging successful authentication and completion of initial setup of EUMD according to utility PEV program. Re-establishment of PEV – Utility communications session (following initial enrollment and setup) can be achieved without full authentication and discovery steps as required for initial session. |  |  |  | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary | Alternative
PEV2 - Customer connects PEV to premise energy portal | X | [6 empty] | AES – See ESCO Charger Clearinghouse Control Device Customer Customer Account Customer Energy Management System Electric Vehicle Supply Equipment (EVSE) Energy Portal (EP)/Smart Energy Portal (SEP) Energy Services Communication Interface (ESCI) See ESI for similarities ESI End Use Measurement Device (EUMD) ESCO – See AES Guest PEV, EV, PHEV Roaming Utility Utility | PEV shall be capable of plugging into EVSE enabled 120V or 240V AC energy portal to receive a charge of electric energy. Premise supports charging multiple PEVs simultaneously, both “home” and guest”. PEV shall be able to charge upon plugging into EVSE enabled 120V or 240V AC energy portal (with or without communications established with utility) The PEV shall be capable of sensing ‘on plug’ state, participating in communications with ESCI, and proceeding with charging according to customer selected preference. The Energy Services Communication Interface shall exist at the customer premise and be capable of communicating to the Utility and can communicate to the PEV to facilitate exchange of charging session information. Vehicle is communicating to the utility through an Energy Services Communication Interface (ESCI) PEV has a unique ID, which can be stored within and communicated from PEV. The PEV shall be capable of providing to the Energy Services Communication Interface (ESCI) its unique PEV ID upon initiation of a communications session between PEV and ESCI. The Utility shall maintain information on all Customers and PEVs enrolled in the PEV programs, associated PEV IDs, Customer IDs, and premise IDs. Utility shall be able to determine customers/premises not enrolled in PEV program. Utility has established message and data interface exchange mechanism with Clearinghouse for verification of roaming PEV. Utility shall be able to verify that usage attributable to PEV charging is sourced from the same customer/premise that has provided the ESCI for PEV-to-Utility communications (e.g., Load correlation to ESCI communications). PEV capable of receiving a confirmation message from Utility via ESCI establishing valid charging session. This indication can in turn be made available to customer to indicate that communications session has been successfully established. An End Use Measurement Device is required to discretely measure usage provided for PEV charging. End Use Measurement Device (EUMD) function can be inclusively located anywhere in a zone from the PEV and the branch circuit panel connection The End Use Measurement Device shall be a meter capable of metering energy supplied to the PEV for each metering interval according to the tariff The End Use Measurement Device shall be capable of recording charging session information (e.g., PEV ID, Premise ID). PEV End Use Measurement Device is utility-, auto manufacturer-, and state weights and measures body-compatible (Specific standard to be determined). The End Use Measurement Device shall allow for remote configuration of energy measurement interval length. The End Use Measurement Device shall be capable of reporting all PEV charging session information and energy usage for PEV charging to the Energy Services Communication Interface. The End Use Measurement Device shall be capable of communicating with the Utility via the Energy Services Communication Interface. PEV, End Use Measurement Device, and Energy Services Communication Interface have established a secure communications link. The Energy Services Communication Interface shall be capable of reporting all PEV charging sessions information and energy usage for PEV charging to the Utility. The Utility shall accurately bill the correct customer account for the total kWhrs supplied during a predetermined billing period to a PEV, according to the selected rate tariff, when the PEV customer and the local premise customer are the same. The Utility shall accurately bill the correct local premise customer account for the total kWhrs supplied during a predetermined billing period to a PEV, according to the selected rate tariff, when the PEV customer and the charging premise customer are NOT the same and the charging premise customer has been designated for PEV usage charges. The Utility shall accurately credit the correct local premise customer account for the total kWhrs supplied during a predetermined billing period to a PEV, according to the selected rate tariff, when the PEV customer and the local premise customer are NOT the same and the PEV customer has been designated for PEV usage charges. Utility will handle billing PEV usage to utility account associated to PEV ID. The Utility shall accurately credit the correct local premise customer account for the total kWhrs supplied during a predetermined billing period to a PEV, according to the selected rate tariff, when the PEV customer and the local premise customer are NOT the same and the PEV customer has been designated for PEV usage charges. In the foreign/roaming utility charging case, Clearinghouse will handle billing transaction to home utility account associated to PEV ID and settling charges across utilities. The Clearinghouse shall store the relationship between PEV ID, Home Utility ID, and Home Utility Account ID. If ESCI communications cannot be established between PEV and Utility within a configurable period of time after ‘on plug’ state, charging will proceed (according to customer preferences) with all charges accruing to premise customer account according to that customer’s regular utility rate. ESCI shall be able to provide the Premise ID to the Utility (along with PEV ID provided by PEV) for validation/verification. Utility shall have a means to determine whether PEV operator/customer or premise customer accrues energy charges when Premise Customer and PEV operator/customer are not the same. (Must be considered in enrollment scenario). | Time will be maintained by each device in the system to UTC with 1 second resolution EUMD shall record interval data configurable for interval lengths between 1 minute and 60 minutes inclusive. PEV attempts to initiate communication session before initiating charging. PEV waits a minimum time (e.g., 1 minute) to allow for verification/validation before charging activation |  |  |  | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary | None
PEV3 - Customer enrolls in a PEV3 Demand Side Management Program | X | [6 empty] | AES – See ESCO Charger Clearinghouse Control Device Customer Customer Account Customer Energy Management System Electric Vehicle Supply Equipment (EVSE) Energy Portal (EP)/Smart Energy Portal (SEP) Energy Services Communication Interface (ESCI) See ESI for similarities ESI End Use Measurement Device (EUMD) ESCO – See AES Guest PEV, EV, PHEV Roaming Utility Utility | Utility shall track Customer preference for remote notification of PEV Demand Response (DR) events. Utility shall transmit PEV Demand Response event alerts to Customer via Customer-designated communication channel(s). The Energy Services Communication Interface (ESCI) shall exist at the customer premise and be capable of securely communicating between the Utility and PEV to facilitate exchange of demand side management information. PEV shall be capable of communicating to the Utility through an Energy Services Communication Interface (ESCI). PEV shall have a unique ID. PEV shall be capable of providing to the Energy Services Communication Interface (ESCI) its unique PEV ID upon initiation of a communication session between PEV and ESCI. Utility shall maintain information on all Customers and PEVs enrolled in the PEV programs, including demand side management programs, associated PEV IDs, customer IDs, and premise IDs. Utility shall be able to transmit discrete demand response event messages to an ESCI and onward to PEV. Utility shall be able to transmit periodic/hourly pricing tables to an ESCI and onward to PEV. PEV shall charge based on Customer-configurable preferences and shall take appropriate action based upon discrete demand response events and/or a periodic/hourly price table. Customer shall have the ability to override and/or opt-out of discrete demand response events. PEV shall send Customer opt-out notification message to Utility End Use Measurement Device shall discretely measure usage provided for PEV charging. End Use Measurement Device (EUMD) function shall be inclusively located anywhere in a zone from the PEV and the branch circuit panel connection. End Use Measurement Device shall be a meter capable of metering energy supplied to the PEV for each metering interval according to the tariff. End Use Measurement Device shall record charging session information (e.g., PEV ID, Premise ID). End Use Measurement Device shall allow for remote configuration of energy measurement interval length. End Use Measurement Device shall report all PEV charging session information and energy usage for PEV charging to the Energy Services Communication Interface. PEV, End Use Measurement Device, and Energy Services Communication Interface shall employ appropriate security policies when communicating demand side management program-related messages.. Energy Services Communication Interface shall report all PEV charging session information and energy usage to Utility. Utility shall apply correct rate structure for accurate customer billing considering any enrolled PEV demand side management programs and the benefits for compliance or charges for overrides and opt outs which are included in those programs. | Time will be maintained by each device in the system to UTC with 1 second resolution EUMD shall record interval data configurable for interval lengths between 1 minute and 60 minutes inclusive. Pre–event notification shall be sent to customers in advance in a range from one minute in an emergency up to 24 hours for normal/planned discrete demand response events. |  |  |  | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
E - General Registration and Enrollment Process | X | [6 empty] | AES see ESCO Charger Clearinghouse Control Device Customer Customer Account Customer Energy Management System Electric Vehicle Supply Equipment (EVSE) Energy Portal (EP)/Smart Energy Portal (SEP) Energy Services Communication Interface (ESCI) ESI End Use Measurement Device (EUMD) ESCO see AES Guest PEV, EV, PHEV Roaming Utility Utility | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
U1 - TOU Program | X | [6 empty] | [EVBS, PFE, Energy Meter, BMS] Customer Clearing House PEV, EV, PHEV ESCO Utility | PEV [EVBS] and Utility [PFE] establish communications. PEV [EVBS] sends ID [to whom?--PFE or BMS], EUMD [Energy Meter] sends ID [to whom? PFE or BMS] and EMS [BMS] authenticates. Rate Time Period info is exchanged [sent from PFE to EVBS] and PEV [EVBS] identifies charge start and end times. EUMD [Energy Meter] sends energy delivered message [to EVBS and Driver]. 1. EVBS, BMS, (and Customer Of Record) and PFE establish communications. 2. EVBS sends ID to BMS. Energy Meter sends ID to BMS. 3. BMS authenticates the identities of the EVBS and Energy Meter. 4. PFE sends rate Time Period info to EVBS and EVBS identifies charge start and end times. 5. Energy Meter sends energy delivered message to EVBS and Driver. |  | 1. EV Driver identifies kWh needed, charge start and end times to EVBS. |  |  | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
U1 - TOU Program | X | [6 empty] | [EVBS, PFE, Energy Meter, BMS] Customer Clearing House PEV, EV, PHEV ESCO Utility | PEV [EVBS] and Utility [PFE] establish communications. PEV [EVBS] sends ID [to whom?--PFE or BMS], EUMD [Energy Meter] sends ID [to whom? PFE or BMS] and EMS [BMS] authenticates. Rate Time Period info is exchanged [sent from PFE to EVBS] and PEV [EVBS] identifies charge start and end times. EUMD [Energy Meter] sends energy delivered message [to EVBS and Driver]. 1. EVBS, BMS, (and Customer Of Record) and PFE establish communications. 2. EVBS sends ID to BMS. Energy Meter sends ID to BMS. 3. BMS authenticates the identities of the EVBS and Energy Meter. 4. PFE sends rate Time Period info to EVBS and EVBS identifies charge start and end times. 5. Energy Meter sends energy delivered message to EVBS and Driver. |  | 1. EV Driver identifies kWh needed, charge start and end times to EVBS. |  |  | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
U2 - Discrete Event Program | X | [6 empty] | Customer PEV, EV, PHEV Utility | PEV and Utility establish communications. PEV sends ID, DR sends ID and EMS authenticates. Scheduled DR load info is exchanged and PEV identifies charge start and end times. DR sends energy status message. |  |  |  |  | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
U3 - Real Time Pricing (RTP) Program | X | [6 empty] | Customer Clearing House PEV, EV, PHEV ESCO Utility | PEV and Utility establish communications. PEV sends ID, EUMD sends ID and EMS authenticates. Rate Time Period info is exchanged and PEV identifies charge start and end times. EUMD sends energy delivered message. |  |  |  |  | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
U4 - Critical Peak Pricing (CPP) Program | X | [6 empty] | Customer Clearing House PEV, EV, PHEV ESCO Utility | PEV and Utility establish communications. PEV sends ID, EUMD sends ID and EMS authenticates. Rate Time Period info is exchanged and PEV identifies charge start and end times. EUMD sends energy delivered message. |  |  |  |  | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
U5 - Optimized Energy Transfer Program | X | [6 empty] | Customer PEV, EV, PHEV Utility | PEV and Utility establish communications. PEV sends ID, EUMD sends ID and EMS authenticates. TCIN, Power and Energy info is exchanged and PEV identifies charge start and end times. EUMD sends energy delivered message. |  |  |  |  | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
S1 Cordset | X | [6 empty] | Customer PEV EVSE PEV/ESCI EUMD ESCI Utility | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
S2 Premise EVSE | X | [6 empty] | EVSE Customer PEV PEV/ESCI EUMD ESCI Utility | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
S3 Premise EVSE that includes the charger | X | [6 empty] | EVSE Customer PEV PEV/ESCI EUMD ESCI Utility | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | Secondary | None | Secondary
L1 - Customer connects PEV at Home - premise | X | [6 empty] | Customer EVSE PEV/Energy Services Communications Interface (ESCI) PEV End Use Measurement Device Energy Services Communication Interface Utility | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
L2 - Customer connects PEV at Another Home | X | [6 empty] | PEV Customer EVSE PEV/Energy Services Communications Interface (ESCI) End Use Measurement Device Energy Services Communication Interface Utility | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
L3 - Customer connects PEV Outside Home Territory | X | [6 empty] | PEV Customer EVSE PEV/ Energy Services Communications Interface (ESCI) ESCI Roaming Utility Clearinghouse Utility End Use Measurement Device Energy Services Communication Interface | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
L4 - Customer connects PEV at Public Location | X | [6 empty] | PEV Customer EVSE PEV/ Energy Services Communications Interface (ESCI) | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
PR1 - Customer charges the PEV | X | [6 empty] | PEV Customer EVSE PEV/ Energy Services Communications Interface (ESCI) Utility Utility/Clearinghouse | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
PR2 - Customer discharges the PEV | X | [6 empty] | Utility Customer PEV | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
Demand Charge Mitigation | X | [6 empty] | Charger Clearinghouse Control Device Customer Customer Account Customer Energy Management System Electric Vehicle Supply Equipment (EVSE) Energy Portal (EP)/Smart Energy Portal (SEP) Energy Services Communication Interface (ESCI) ESI End Use Measurement Device (EUMD) Guest PEV, EV, PHEV Roaming Utility Utility | [5 empty] | PEV | None | None | Primary | Secondary | None | Secondary | None | None | None | Secondary
SAE V2G-AC |  | X | X | X | X | X |  | EVSE, PEV, BMS (and optional NSP), Utility, EVSE Owner, EV Owner | (1) For each session at connection of EV to EVSE, EVSE shall provide site settings to EV, confirm proper EV settings, and authorize EV to discharge during session (if acceptable to EVSE based on CPUC Rule 21 requirements). (2) NSP or BMS shall provide DER commands to EV onboard inverter and receive DER status information from EV inverter during session to perform some V2G application (such as facility demand charge management, AGC frequency regulation, or autonomous volt-VAR support). | (1) CPUC shall establish a Rule 21 interconnection approval process where the EVSE (site) owner shall apply to the Utility to approve a V2G-AC DER interconnection based on the model number of the EVSE. The EVSE shall be required to authorize the roaming EV inverter to discharge during a specific session as determined by Rule 21 requirements for roaming EVs with onboard inverters. (2) EV Owner enters agreement with V2G Application owner (NSP, BMS) for specific services. (3) EV operator authorizes participation by EV in a V2G Application for a session(s). (4) EV owner has agreement with EVSE owner for use of EVSE for the session. | (1) Customer expects that the communication protocol used between the EV onboard inverter and the BMS (or NSP) shall support the use of any smart inverter function implemented by the EV in accordance with international standards. (2) Customer authorizes participation in a V2G Application during session. (3) Customer defines the "Target SOC" and "Time Charge Needed" to support cooperative engagement with BMS/NSP. | (1) CPUC shall update Rule 21 to define EV and EVSE requirements and an interconnection approval process which will allow a roaming EV with an onboard inverter to connected to a special AC Level 2 EVSE (V2G-AC) and engage in V2G applications. | It is not permitted for an EV to discharge energy when connected to the utility grid without prior approval of the interconnection by the utility (Rule 21). Because the EV roams, communication is required between EVSE and EV to confirm that the EV is authorized to discharge at a specific site. | Optional | Optional | Optional | Optional | Secondary | Primary | Optional | Secondary | Optional | Optional | None
SAE V2G-DC |  | X | X | X | X | X |  | PCEV, ECS [EVSE], EVBS [PEV], FMS [BMS] (and optional PFE [NSP]), Utility, EVSE Owner, EVD [EV Owner] | (1) At connection of EVBS [EV] to PCEV [EVSE], PCEV [EVSE] shall engages EVBS [EV] in a DC DER mode (see DC Flow Management Use Case). (2) PFE [NSP] or FMS [BMS] shall sends DER commands to PCEV via the ECS [EVSE inverter] and receives status information from PCEV via the ECS [EVSE inverter] during session to perform some V2G application (such as facility demand charge management, AGC frequency regulation, or autonomous volt-VAR support). (Term normalization note: The EVSE used in this approach is a single product containing both the PCEV and the ECS. Communications between these elements is integral to the product but the PCEV and ECS components are separated here for normalization consistency.) | (1) UCR [EVSE Owner] applies to PFE [Utility] for interconnection of ECS [EVSE inverter] based on model number of ECS [EVSE] in accorance with Rule 21 requirements. (Term normalization note: the Rule 21 reference identifies the ECS as a DC EVSE which combines a ECS and PCEV.) PFE [Utility] approves interconnection. (Term normalization note: Utility may be separate from the PFE, but in that case the approval of device connection is separate from the functional activity during VGI activity.) (2) UCR [EVSE Owner] enters a services agreement with PFE [DER operator] (which could be a V2G operator) for energy storage system type DER. (3) EVD [EV owner] authorizes participation by EVBS [EV] with site ECS [EVSE] in a DER (V2G) service for session. | (1) UCR [EVSE (site) owner] shall authorizes engagement in a specific DER/V2G application with FMS [BMS] (or PFE [NSP]) for defined interval. (2) EVD [EV owner] shall authorizes participation with site ECS [EVSE] in a DER/V2G Application during session. (3) EVD [EV owner] shall/should/could? defines the "Target SOC" and "Time Charge Needed" to support cooperative engagement with FMS/PFE [BMS/NSP]. | (1) CPUC shall update Rule 21 to define any unique requirements and an interconnection approval process which should apply to an ECS [EVSE] with an PCEV [inverter] engaging as a energy storage type of DER (V2G-DC). (2) Direct communication between EVBS [EV] and PCEV [EVSE] is required as described by Use Case DC Flow Management. The PCEV [EVSE] engages the DC DER Mode. | Communication between ECS [EVSE] and FMS/PFE [BMS/NSP] are optional if ECS [EVSE] can be manually engaged to discharge or operated in islanded home as backup generator (V2H-DC). | Optional | Alternative | None | None | Primary | None | None | Primary | Optional | Optional | None
SAE V2G-DC |  | X | X | X | X | X |  | EVSE, PEV, BMS (and optional NSP), Utility, EVSE Owner, EV Owner | (1) At connection of EV to EVSE, EVSE engages EV in a DC DER mode (see DC Flow Management Use Case). (2) NSP or BMS sends DER commands to EVSE inverter and receives status information from EVSE inverter during session to perform some V2G application (such as facility demand charge management, AGC frequency regulation, or autonomous volt-VAR support). | (1) EVSE Owner applies to Utility for interconnection of EVSE inverter based on model number of EVSE in accorance with Rule 21 requirements. Utility approves interconnection. (2) EVSE Owner enters a services agreement with DER operator (which could be a V2G operator) for energy storage system type DER. (3) EV owner authorizes participation by EV with site EVSE in a DER (V2G) service for session. | (1) EVSE (site) owner authorizes engagement in a specific DER/V2G application with BMS (or NSP) for defined interval. (2) EV owner authorizes participation with site EVSE in a DER/V2G Application during session. (3) EV owner defines the "Target SOC" and "Time Charge Needed" to support cooperative engagement with BMS/NSP. | (1) CPUC shall update Rule 21 to define any unique requirements and an interconnection approval process which should apply to an EVSE with an inverter engaging as a energy storage type of DER (V2G-DC). (2) Direct communication between EV and EVSE is required as described by Use Case DC Flow Management. The EVSE engages the DC DER Mode. | Communication between EVSE and BMS/NSP are optional if EVSE can be manually engaged to discharge or operated in islanded home as backup generator (V2H-DC). | Optional | Alternative | None | None | Primary | None | None | Primary | Optional | Optional | None
DC Flow Management | X | X |  | X | X |  |  | PCEV [EVSE], EVBS [PEV] | PCEV [EVSE] and EVBS [EV] shall exchange information to jointly manage the DC power flow between the PCEV [EVSE] and EVBS [EV] during a session. Channel could can relay other useful information between EVBS & EVD [EV] and ECS [EVSE] as needed to support EVD [EV customer]. | EVBS [EV] receptacle and ECS [EVSE] cable plug shall must be physically compatible for DC conductive transfer and provide interoperable communications. | (1) EVD [Customer] shall authorizes participation in either DC Fast Charging or DC DER Mode. Could be by default for type of ECS [EVSE]. | For discharging, UCR [site] shall have has DER interconnection agreement with PFE [utility] for V2G-DC operation based on EVC [EVSE] model number. | Communication between the EVBS [EV] and ECS [EVSE] shall be is required for DC transfer. Communication of either ECS [EVSE] or EVBS [EV] with FMS [BMS] or PFE [NSP] are optional, but desired, and part of Use Case SAE V2G-DC. | None | None | None | None | None | None | None | Primary | None | None | None
DC Flow Management | X | X |  | X | X |  |  | EVSE,PEV | EVSE and EV exchange information to jointly manage the DC power flow between the EVSE and EV during a session. Channel can relay other useful information between EV and EVSE as needed to support EV customer. | EV receptacle and EVSE cable plug must be physically compatible for DC conductive transfer and provide interoperable communications. | (1) Customer authorizes participation in either DC Fast Charging or DC DER Mode. Could be by default for type of EVSE. | For discharging, site has DER interconnection agreement with utility for V2G-DC operation based on EVSE model number. | Communication between the EV and EVSE is required for DC transfer. Communication of either EVSE or EV with BMS or NSP are optional, but desired, and part of Use Case SAE V2G-DC. | None | None | None | None | None | None | None | Primary | None | None | None
"USE RENEWABLE ENERGY TO MAKE THE BEST USE FOR CHARGING AN EV FLEET TRANSPORTATION AT BEST COST" (Load Improvement thru Curtailing with Over-generation in fleet operations deployed with Software Algorithms and Battery Storage to achieve value opportunity for all PEV customers and IOU) | X | X | X |  |  | X |  | Host Site, PEV, EVSE, Sub-Meter, Site Controller/ EMS, Site Meter, Battery Energy Storage System (BESS), Utility/ISO (NSP) | 1) The Site Controller Shall be able to obtain the current Energy capacity for each PEV and EVSE and the BMS 2) The Site Controller Shall be able to obtain the total site energy available. 3) The Site Controller Shall obtain the customer specifications for the PEV fleet: daily miles, number of chargers, volts available for charging, number of PEV's, hours in drive mode, hours available to charge, hours in dwell time, night time charging miles and low speed/braking benefits. 4) The Site Controller Shall be able to send a command signal to the PEV and EVSE to manage the energy load of the Fleet operations using load control algorithms based on customers specifications. 5) All communication equipment Shall be required to have a High Speed Connection that is guaranteed to respond to a signal in 5 second increments. 6) Mapping information Should be required to intelligently determine fleet behavior, traffic condition affects and circuit load availability. (more braking, more generator) 7) Storage Shall be mandated for Fleets in order to support own use and other grid sharing benefits at peak time and night time. 8) Battery Efficiency monitoring and degradation % Shall be guaranteed to perform at standard efficiency level over X period of time (different chemistries react differently and last longer etc.) 9) BMS Shall have a one to one relation to each EVSE. Sub meters Shall be co-located at each EVSE to understand the charge session data. | 1) The communications between the Site Controller and the EV Should be cyber secure. 2) It Shall require Interoperability with multiple vendors and dedicated ports. 3) The On Board Diagnostic Shall be required to support Mal Function Alerts of EVSE or PEV and Should have service response in "minimum" time and repaired in "maximum" time. 4) System Shall be conforming to Life Cycle period automatic testing for both reliability and security, perhaps monthly. 5) Communication between Site controller and EVSE Shall monitor performance of cell temperature, cell balancing and protection. Temperature Alerts Shall be required, as cycling on and off creates heat due to fluctuating voltage and frequency creating more wear and tear. 6) All equipment Shall be UL certified and meet all conformance standards. 7) All data links Shall be open with standards for connecting universally. 8) Peak Time grid Charging Should be eliminated and the algorithm Shall enable the Renewable Charging. 9) This Use Case Could be a Communication Enabler. | 1) Should be able to opt in or out of event at the EV or Site Controller 2) Shall be able to enter miles needed over "X" amount of hours at the EV and Site Controller. Understanding how much charging is required in day time and maximum allotted from over night charging determines remaining required day time charging. 3) Driver Shall be able to understand how many times he is required to plug in during his shift in order to stay on the road and in order to avoid peak time use. 4) kWh use and kW use from Transportation Fleet use VS building use Shall be available and segregated with Sub-metering. 5) Customer Should have an EV Rate choice with a benefit for "Managed" peak time use and Over generation sinking. 6) Could require a Wireless sense control from PEV to EVSE for more convenience. 7) Telematics Could communicate the needs of the fleet reporting and enhance the benefits of a PEV fleet for example how many kWh per mile do I need or did I achieve? Communication Should be required at all times with the PEV not just when charging. What is the EV doing at all times (driving or charging?) 8) Site Controller information Should support File Transfer and Auto-Configurable and Configuration support. 9) The kWh advertised fees Shall include "ALL" fees as TAXES are part of the utility invoice but are NOT the advertised rate. | 1) Site controller Should connect to Network Service Provider to communicate with all vehicles in fleet and all IOU's in region. 2) Driver Should be able to have more than one option for determining required voltage that he must be charging at in order to remain on the road and to react to available dwell time when at base or on road. 3) Sub-Metering Shall be required for deployment of fleet operations in order to manage fleet operational cost and for reporting consideration for a 'Motor Fuel Tax' in the future and the LCFS credit reporting. 4) GEO fencing for all HVIP vehicles Should be required in order to establish travel in inner city and / or disadvantaged communities, plus ELD (electronic logging data) is a regulatory requirement for commercial carriers effective 12-2017. 5) PEV customer Should be required to be on LCFS program to produce credits or to get a LCFS tariff rate incentive. 6) PEV Could communicate Max kW and Peak kW for fleet management goals. 7) Should provide alerts on SOC changes when weather affects capacity (wind & cold climates) or hills in route. 8) EVSE and PEV Should support Bi-directional discharging. 9) Make Ready Should be supported for PEV Fleets. | 1) For non-communication PEV, Site Controller Could manage the PEV load by using the EVSE Control 2) For non-communication the PEV, site controller Could manage the PEV load by EVSE speed when at less than 15 minutes of use or with multi meters 3) Could provide Service item alerts and system upgrades in order to remain reliable. 4) Driver education Could improve use of technology: How many times did you plug in? What was your ending capacity 5) Should provide ability to interpret codes and repair or reprogram simple issues via the EVSE dash board or Site Controller. 6) Telematics, Could always provide information on what the EV is doing at all times, is it charging or driving or dwelling? | EVSE or PEV (ultimately the power flow will be adjusted to the weakest link: property, EVSE or PEV; and then it can also be stepped down by managing it) | Optional | None | None | None | Secondary | Primary | Secondary | None | None | Secondary
DC Charge -Discharge system use case - Vehicle to Home |  | X | X | X | X | X |  | EVD, UCR [Driver/Home owner], EVBS [PEV], ECS, PCEV [EVSE], PFE [utility tariff] (Term normalization note: utility tariff is an information item from the PFE. Requirements were edited to better identify the actor and information exchange.) | 1) PCEV [EVSE] shall have input for Min & Max SOC of vehicle battery or a driving range based equivalent 2) PCEV [EVSE] shall have input for operational mode 3) ECS [EVSE] should have input for TOU Tariff rates / schedule 4) ECS [EVSE] should have input for customer scheduling 5) ECS [EVSE] could have utility communication for updating TOU pricing & schedule | 1) ECS [EVSE] could have status and feedback information to user | 1) EVD [Customer] shall be able to set battery SOC limits or driving range at the PCEV 2) UCR [Customer] shall be able to set the operation mode and schedule of ECS [device] 3) EVD [Customer] shall be able to override ECS [system] settings or turn on/off device |  | 1) UCR [Customer] interface could be through a FMS [home BMS] | None | Alternative | None | Primary | Alternative | None | None | Primary | Primary | Optional | None
DC Charge -Discharge system use case - Vehicle to Home |  | X | X | X | X | X |  | Driver/Home owner, PEV, EVSE, utility tarriff | 1) EVSE shall have input for Min & Max SOC of vehicle battery or a driving range based equivalent 2) EVSE shall have input for operational mode 3) EVSE should have input for TOU Tarriff rates / schedule 4) EVSE should have input for customer scheduling 5) EVSE could have utility communication for updating TOU pricing & schedule | 1) EVSE could have status and feedback information to user | 1) Customer shall be able to set battery SOC limits or driving range 2) Customer shall be able to set the operation mode and schedule of device 3) Customer shall be able to override system settings or turn on/off device |  | 1) Customer interface could be through a home BMS | None | Alternative | None | Primary | Alternative | None | None | Primary | Primary | Optional | None
DC Charge -Discharge system use case - Aggregated Vehicle to Home |  | X | X | X | X | X |  | EVD, UCR [Driver/Home owner], PFE [Aggregator], EVBS [PEV], ECS, PCEV [EVSE], PFE [utility tariff information] | 1) PCEV [EVSE] shall have input for Min & Max SOC of vehicle battery or a driving range based equivalent 2) PCEV [EVSE] shall have input for customer operational mode preferences 3) ECS [EVSE] should have input for TOU Tarriff rates / schedule 4) ECS [EVSE] could have input for customer scheduling 5) ECS [EVSE] should have PFE [NSP] communication for updating TOU pricing & schedule 6) ECS [EVSE] Shall have PFE [NSP] control communication to perform aggregation | 1) ECS [EVSE] should have status and feedback information to user | 1) EVD [Customer] shall be able to set battery SOC limits or driving range 2) UCR [Customer] shall be able to set operation mode and schedule preferences 3) EVD [Customer] shall be able to override system settings or turn on/off device |  | 1) Communication of ESC with PFE [NSP] could be through a FMS [BMS] | Alternative | Primary | None | Primary | Alternative | None | Alternative | Primary | Primary | Optional | None
DC Charge -Discharge system use case - Aggregated Vehicle to Home |  | X | X | X | X | X |  | Driver/Home owner, Aggregator, PEV, EVSE, utility tariff information | 1) EVSE shall have input for Min & Max SOC of vehicle battery or a driving range based equivalent 2) EVSE shall have input for customer operational mode preferences 3) EVSE should have input for TOU Tarriff rates / schedule 4) EVSE could have input for customer scheduling 5) EVSE should have NSP communication for updating TOU pricing & schedule 6) EVSE Shall have NSP control communication to perform aggregation | 1) EVSE should have status and feedback information to user | 1) Customer shall be able to set battery SOC limits or driving range 2) Customer shall be able to set operation mode and schedule preferences 3) Customer shall be able to override system settings or turn on/off device |  | 1) Communication with NSP could be through a BMS | Alternative | Primary | None | Primary | Alternative | None | Alternative | Primary | Primary | Optional | None
Maximize GHG reductions at workplaces at low cost by load managing a circuit to prevent critical peaks | x |  | x | x | x | x |  | Site Controller, Trip Relay or EVSE | The Site Controller shall calculate the peak energy period or detect the voltage sag and communicate to a Trip Relay (primary) or EVSE (secondary) to curtail chahrging | 1) Site Controller could be software based and reside within a gateway device for the EV parking lot or provided as a cloud service . Note: Site Controller could control the entire EV parking lot (one size-fits all) requiring no communication pathway to the EV or EVSE. Because the EVs in the lot are self selecting (e.g., long-range BEVs or PHEVs), they don't care if on a few extremely hot days they don't get a charge (service stops due to circuit is tripped) Customer could have other workplace lots at the same address for other use cases to serve other types of customers (e.g. short range BEVs) | Note - customer experience in this use case is almost identical to gasoline cars today 1) Shall not expect a full charge every day (e.g., best to have a long-range BEV or PHEV or have a short commute in a short-range BEV) 2) Note - No EV driver control of charging, but rather central control by the NSP. In exchange EV driver shall A) get assigned parking B) have to move the car when fully charged C) receive a very low charging price C) not have to think about charging price (e.g. payroll deduction, or at most yearly check), and should sign a sustainability pledge that they typically at night either park on the street or in a common area of an MUD (unassigned parking at night) | 1) Separately metered service 2) Site controller could be the Network Service Provider (could be utility) that is communicating with the ISO today or DSO in the future 3) Site host could avoid networking fees for each EVSE as the EVSEs are dumb - with all the intelligence in the site controller 4 - note - major reason for this to provide primary charging location for those who park on streets and MUD common areas at night, and provide large GHG & air pollution reductions compared to other workplace charging | EVSE control using SAE J1772 | PEV | none | Secondary | None | None | Secondary | None | None | None | None | None
Autonomous default inverter management by the EV to manage voltage decreases | X | [6 empty] | EV | EV shall implement default Autonomous Inverter Functions that support the Grid as per SIWG Phase 1 | EVs must be equiped with this capability |  |  |  | PEV | None | None | None | None | None | None | None | None | None | None
Autonomous default inverter management by the EV to manage voltage increases |  | x | [5 empty] | EV | EV shall implement default Autonomous Inverter Functions that support the Grid as per SIWG Phase 1 | EVs must be equiped with this capability |  |  |  | PEV | None | None | None | None | None | None | None | None | None | None
Maximize GHG reductions at workplaces at low cost by load managing an EV charging line to prevent critical peaks, provide demand response, and some wholesale market services | x |  | x | x | x | x |  | Utility, Utility Customer (site host) | The utility sends AMI signal to open and close meter service relay, which turns off power to the entire charge line under that meter | Some EV charging systems are under one utility meter with no other loads. The utility meter shall control the entire EV parking lot (one size-fits all) requiring no communication pathway to the EV or EVSE. Because the EVs in the lot are self selecting (e.g., long-range BEVs or PHEVs), they don't care if a on few days a year they don't get a full charge (service stops due to circuit is turned off by signal from meter) Customer could have other workplace lots at the same address for other use cases to serve other types of customers (e.g. short range BEVs) | Note - customer experience in this use case is almost identical to gasoline cars today 1) Shall not expect a full charge every day (e.g., best to have a long-range BEV or PHEV or have a short commute in a short-range BEV) 2) Utility customer (site host) and EV driver shall sign up for this program 3) Note - No EV driver control of charging, but rather central control by the NSP. In exchange EV driver shall A) get assigned parking B) have to move the car when fully charged C) receive a very low charging price C) not have to think about charging price (e.g. payroll deduction, or at most yearly check), and should sign a sustainability pledge that they typically at night either park on the street or in a common area of an MUD (unassigned parking at night) | Inexpensive and easy way to directly control charging load – utility sends disconnect signal to the meter. Some latency in response, but ~200A can be interrupted this way, and restored. Can't ramp down or ramp-up partially. Can do more than the use case above 2) Separately metered service 3) Site host could avoid networking fees for each EVSE 4) note - major reason for this to provide primary charging location for those who park on streets and MUD common areas at night, and provide large GHG & air pollution reductions compared to other workplace charging |  | PEV | None | None | None | None | None | None | None | None | None | None
Maximize GHG reductions at workplaces at low cost by load managing an EV charging line to prevent critical peaks, provide demand response, and some wholesale market services | x |  | x | x | x | x |  | Utility, Utility customer (site host), BMS | The utility sends AMI signal through meter to communicate with BMS directly and respond to price or control signals (i.e. Zigbee). Some utility AMI meters have dual radios to communicate with onsite networks. Some EVSEs are capable of talking the same language directly. | BMS or site controller must be equipped to communicate with the utility meter. 1) Site Controller could be software based and reside within a gateway device for the EV parking lot or provided as a cloud service . Site Controller could control the entire EV parking lot (one size-fits all) requiring no communication pathway to the EV or EVSE. Because the EVs in the lot are self selecting (e.g., long-range BEVs or PHEVs), they don't care if a on few days a year they don't get a full charge (service stops due to circuit is turned off by signal from meter) Customer could have other workplace lots at the same address for other use cases to serve other types of customers (e.g. short range BEVs) | Note - customer experience in this use case is almost identical to gasoline cars today 1) Shall not expect a full charge every day (e.g., best to have a long-range BEV or PHEV or have a short commute in a short-range BEV) 2) Utility customer (stie host) and EV driver shall sign up for this program 2) Note - No EV driver control of charging, but rather central control by the NSP. In exchange EV driver shall A) get assigned parking B) have to move the car when fully charged C) receive a very low charging price C) not have to think about charging price (e.g. payroll deduction, or at most yearly check), and should sign a sustainability pledge that they typically at night either park on the street or in a common area of an MUD (unassigned parking at night) | 1) Separately metered service for EVs or metered service covers EVs AND other loads 2) Site controller (BMS) should from the utility and BMS is communicating with the ISO today or DSO in the future (could be owned by non-utility NSP) 3) Site host could avoid networking fees for each EVSE as the EVSEs are dumb - with all the intelligence in the site controller 4 - note - major reason for this to provide primary charging location for those who park on streets and MUD common areas at night, and provide large GHG & air pollution reductions compared to other workplace charging | Control via HAN or EVSE instead of the BMS | PEV | primary | Secondary | None | None | None | None | None | None | None | None
Load managing an EV charging line at fleets and homes to prevent critical peaks, provide demand response, and some wholesale market services | x |  | x | x | x | x |  | Utility, Utility customer (site host) | The utility sends AMI signal to open and close meter service relay, which turns off power to the entire charge line under that meter | Some EV charging systems are under one utility meter with no other loads. The utility meter shall control the entire EV parking lot (one size-fits all) requiring no communication pathway to the EV or EVSE. Homes in the future can have 2, 3 or 4 EVs, and fleets many more. Because the EVs in these cases are self selecting (e.g., long-range BEVs or PHEVs), they don't care if a on few days a year they don't get a full charge (service stops due to circuit is turned off by signal from meter) | Note - customer experience in this use case is almost identical to gasoline cars today 1) Shall not expect a full charge every day (e.g., best to have a long-range BEV or PHEV) 2) Utility customer shall sign up for this program 3) Note - No EV driver control of charging, but rather central control by the NSP. In exchange EV fleet or home shall receive a very low charging price monthly and not have to think about charging price changing daily. | Inexpensive and easy way to directly control charging load – utility sends disconnect signal to the meter. Some latency in response, but ~200A can be interrupted this way, and restored. Can't ramp down or ramp-up partially. Can do more than the use case above 2) Separately metered service 3) Site host could avoid networking fees for each EVSE |  | PEV | None | None | None | None | None | None | None | None | None | None
Load managing an EV charging line at fleets and homes to prevent critical peaks, provide demand responds or some whole sale market services | x |  | x | x | x | x |  | Utility, Utility customer (site host), BMS | The utility sends AMI signal through meter to communicate with BMS directly and respond to price or control signals (i.e. Zigbee). Some utility AMI meters have dual radios to communicate with onsite networks. Some EVSEs are capable of talking the same language directly. | BMS or site controller must be equipped to communicate with the utility meter. 1) Site Controller could be software based and reside within a gateway device for the EV parking lot or provided as a cloud service . Site Controller could control the entire EV parking lot (one size-fits all) requiring no communication pathway to the EV or EVSE. Because the EVs in the lot are self selecting (e.g., long-range BEVs or PHEVs), they don't care if a on few days a year they don't get a full charge (service stops due to circuit is turned off by signal from meter) | Note - customer experience in this use case is almost identical to gasoline cars today 1) Shall not expect a full charge every day (e.g., best to have a long-range BEV or PHEV) 2) Utility customer shall sign up for this program 3) Note - No EV driver control of charging, but rather central control by the NSP. In exchange EV fleet or home shall receive a very low charging price monthly and not have to think about charging price changing daily. | 1) Separately metered service for EVs or metered service covers EVs AND other loads 2) Site controller (BMS) should from the utility and BMS is communicating with the ISO today or DSO in the future (could be owned by non-utility NSP) 3) Site host (fleet or home) could avoid networking fees for each EVSE as the EVSEs are dumb - with all the intelligence in the site controller | Control via HAN or EVSE instead of the BMS | PEV | primary | Secondary | None | None | None | None | None | None | None | None
Automated Utility Electricity Rate Tariff Processing | X |  |  | X |  | X |  | PFE / Utility Customer of Record / EVBS | 1. Upon EV Driver plug in PFE shall request Utility Customer of Record (UCOR) account rate tariff/schedule from Utility 2. Utility shall verify UCOR account ID and authorization - shall transmits rate tariff/schedule to PFE per request 3. PFE receives UCOR rate tariff/schedule and shall transmit to EVBS (EV Battery System). | 1. Shall have security for customer data privacy and protection from external attacks | 1. Utility Customer Of Record shall have provided authorization for PFE access to customer utility account information | Utility Customer of Record must provide authorizations to share data between utility and PFE |  | EV Battery System | Primary | None | Secondary | None | None | Primary | None | None | None | Secondary
Automated Utility Electricity Rate Tariff Processing | X |  |  | X |  | X |  | NSP/ OVGIP / PEV / Customer | 1. Upon customer plug in OVGIP shall request customer residential account rate tariff/schedule from Utility 2. Utility shall verify customer account ID and authorization - transmits rate tariff/schedule to OVGIP 3. OVGIP receives rate tariff/schedule and shall transmit to customer PEV. | 1. Shall have security for customer data privacy and protection from external attacks | 1. Customer shall have provided authorization for OVGIP access to customer utility account information | Customer must provide authorizations to share data between utility and OEM. |  | PEV | None | None | Primary | None | None | None | None | None | None | Secondary
Aggregated PEV Demand Response (DR) and Dynamic Pricing Signals (which includes Critical Peak Pricing (CPP), Variable Peak Pricing (VPP), and Real Time Prcing (RTP)) | X |  | X |  | X |  |  | ISO / Utility or ESP or Aggregator / OVGIP / PEV / Customer | 1. OVGIP shall formulate PEV load capacity projections for bid purposes, either increase load or decrease load based on program requirements, and transmit to Utility / ESP / Aggregator / ISO 2. Utility / ESP / ISO shall determine DR/Dynamic Price schedule either day ahead or day of (one hour notification) and provide signals to OVGIP 3. OVGIP shall calculate aggregated response and allocate DR/CPP signals to PEV. 4. PEVs shall determine opt in/out based on customer charge settings and TCIN 5. OVGIP shall accumulate charge data from PEVs for event and transmit for use in settlement processes with Utility / ESP / Aggregator in accordance to establlished V&M baseline 6. OVGIP shall receive and process decrease/increase DR load management commands from Utility / ESP / Aggregator to PEV to provide ramping support for renewables over/under generation. | 1. Shall have security for customer data privacy and protection from external attacks 2. OVGIP may have automated access to customer whole house meter data for measurement and verification of customer performance I.e. 10/10 baseline measurement and verification process. Access based on IOU requirements. | 1. Customer receives notifications/alerts about DR events or Dynamic Price schedules 2. Customer shall have capability to opt in/out of DR / Dynamic Price Event 3. Alternative is the PEV can make the opt in/out determination based on TCIN, power requriements, and other customer charge settings | 1. Utility regional designation for events are based on GPS coordinates. 2. M&V requirements and utilization of PEV data is subject to IOU / ISO discretion on a program by program basis. |  | PEV | None | None | Primary | Secondary | None | None | None | None | None | Secondary
Interface with HEMS | X |  |  | X | X |  |  | NSP / Residential HEMS or ESI / OVGIP / PEV/ Customers | 1. OVGIP shall commuicate with the residential HEMS/ESI 1. IOU / ESP/ Aggregator shall send DR signals or Real Time / Dynamic Pricing signals to residential HEMS/ ESI 2. HEMS/ESI shall communicate signals to the OVGIP. HEMS will provide PEV ID, and residential meter ID for association purposes. 3. OVGIP shall receive and transmit HEMS / ESI signals or commands to the PEV 4. Customer should have capability to set or change PEV charge preferences remotely through the HEMS/ESI - OVGIP communications pathwary while PEV plugged in at residence. Can address TOU charge schedule settings or other time variables for start of charging or TCIN according to customer needs. | 1. Shall have security for customer data privacy and protection from external attacks | 1. Customer receives notifications/alerts about DR and RTP / Dynamic Pricing events scheduled 2. Customer shall have capability to opt in/out of Event 3. Alternative is the PEV should be able to automatically opt in/out based on TCIN, power requriements, and other customer PEV charge settings | 1. OVGIP shall establish priorities based on primacy of residential HEMS/ESI to determine PEV response to broadcasted IOU DR or RTP or other pricing signals. |  | PEV | Primary | None | None | None | None | Primary | Secondary | None | None | Secondary
Interface with HEMS | X |  |  | X | X |  |  | PFE, BMS, EVBS, EV Driver | PFE shall commuicate with the residential BMS 1. PFE shall send DR signals or Real Time / Dynamic Pricing signals to BMS or to EVBS 2. BMS shall communicate signals to the PFE including EVBS ID, and Utility Customer of Record ID [Customer ID] for association purposes. 3. EV Driver should have capability to set or change EVBS charge preferences remotely through the BMS - PFE communications pathway while EVBS plugged in at residence including TOU charge schedule settings or other time variables for start of charging or Charge at Departure or Miles Required according to customer needs. | 1. Shall have security for customer data privacy and protection from external attacks | EV Driver should have capability to set or change EVBS charge preferences remotely through the BMS - PFE communications pathway while EVBS plugged in at residence including TOU charge schedule settings or other time variables for start of charging or Charge at Departure or Miles Required according to customer needs. |  |  |  | Primary | None | Secondary | None | None | Primary | Secondary | None | None | Secondary
Interface with BMS | X |  | X |  | X |  |  | NSP / BMS / OVGIP / PEV | 1. BMS shall communicate with the IOU / ESP / Aggregator for DR and Pricing signals in accordance with program enrollment requirements and communicate appropriate BMS DR event and other load management response signals to the OVGP to the PEV. 2. OVGIP shall communicate with the BMS and shall provide PEV customer charge preferences such as TCIN, power requirements, and duration 3. BMS shall communicate to OVGIP either individual PEV charge parameters or aggregated PEV charge parameters depending on the BMS load control strategy, requirements, and functional implementation | 1. Shall have security for customer data privacy and protection from external attacks 2. BMS shall have monitoring and control over PEV charging infrastructure at the facility and capability to override PEV customer preferences based on conditions of the facility load management needs i.e. Demand Charge Mitigation and DER energy management limitations/thresholds/constraints | 1. Customer should receive notifications/alerts about charging status based on BMS scheduled parameters from the PEV 2. Customer should have capability to opt in/out of load management directive from the BMS based on TCIN 3. PEV should be ableto make the opt in/out determination based on TCIN, power requriements, and other customer PEV charge settings 3. BMS shall have capability to override customer opt out based on facility energy management priorities for optimized cost performance | 1. OVGIP shall establish priorities based on primacy of facility BMS to determine PEV response to broadcasted IOU DR or RTP or other pricing signals. 2. OVGIP identification of PEVs plugged in at facility will be based on geo fencing coordinates of the facility - altrenatively the BMS may be able to provide PEV ID to OVGIP at time of plug in. |  | PEV | Primary | None | None | None | None | Primary | Optional | None | None | Secondary
Interface with EVSE Network Provider | X |  | X |  | X |  |  | PFE, EV Battery System, EV Driver | 1. Premise is the PFE is the responsible 3rd party EMS provider for the facility PEV charging jnfrastructure. In this regard the EVSE Network Provider is synomymous with the BMS interface use case for functional requirements. In this use case the EVSE Network Provider (EVSP) could be responding to the facility BMS control commands.For purposes of this use case the assumption is the EVSP is acting autonomously on behalf of the facility, MUD, or workplace environment. 1. PFE will obtain from the relevant authorities for [IOU / ESP / Aggregator] for DR and Pricing information in accordance with program enrollment requirements and shall communicate appropriate DR event and other load management response signals from the PFE to the EV Battery System. 2. OVGIP shall communicate with the EVSP and PFE will provide EV driver charge preferences such as energy or miles required at departure time, power requirements, and duration 3. PFE shall communicate to either individual or aggregated EV Battery System charge parameters depending on the load control strategy, requirements, and functional implementation 4. PFE should be able to provide EV Battery System ID to PFE at time of plug in. | 1. Shall have security for customer data privacy and protection from external attacks 2. PFE shall have monitoring and control over ECS at the facility and capability to override EV driver preferences based on conditions of the facility load management needs i.e. Demand Charge Mitigation and DER energy management limitations / thresholds / constraints | 1. EV driver should receive notifications/alerts about charging status based on PFE scheduled parameters from the EV Battery System 2. Customer should have capability to opt in/out of load management directive from the PFE based on energy or mileage reuq 3. EV Battery System should be able to make the opt in/out determination based on energy or miles required at departure time, power requriements, and other EV driver charge settings 3. PFE shall have capability to override customer opt out based on facility energy management priorities for optimized cost performance | 1. PFE shall establish priorities based on primacy of FMS EVSP to determine EVBS [PEV] response to broadcasted pricing signals. 2. PFE identification of ECS plugged in at facility will be based on geo fencing coordinates of the facility |  | PEV | Primary | None | None | None | None | Primary | Optional | None | None | Secondary
Interface with EVSE Network Provider | X |  | X |  | X |  |  | EVSE Network Provider / OVGIP / PEV | 1. Premise is the EVSE Network Provider is the responsible 3rd party EMS provider for the facility PEV charging jnfrastructure. In this regard the EVSE Network Provider is synomymous with the BMS interface use case for functional requirements. In this use case the EVSE Network Provider (EVSP) could be responding to the facility BMS control commands.For purposes of this use case the assumption is the EVSP is acting autonomously on behalf of the facility, MUD, or workplace environment. 2. EVSP shall communicate with the IOU / ESP / Aggregator for DR and Pricing signals in accordance with program enrollment requirements and communicate appropriate DR event and other load management response signals to the OVGP to the PEV. 2. OVGIP shall communicate with the EVSP and shall provide PEV customer charge preferences such as TCIN, power requirements, and duration 3. EVSP shall communicate to OVGIP either individual PEV charge parameters or aggregated PEV charge parameters depending on the load control strategy, requirements, and functional implementation | 1. Shall have security for customer data privacy and protection from external attacks 2. EVSP shall have monitoring and control over PEV charging infrastructure at the facility and capability to override PEV customer preferences based on conditions of the facility load management needs i.e. Demand Charge Mitigation and DER energy management limitations / thresholds / constraints | 1. Customer should receive notifications/alerts about charging status based on EVSP scheduled parameters from the PEV 2. Customer should have capability to opt in/out of load management directive from the EVSP based on TCIN 3. PEV should be ableto make the opt in/out determination based on TCIN, power requriements, and other customer PEV charge settings 3. EVSP shall have capability to override customer opt out based on facility energy management priorities for optimized cost performance | 1. OVGIP shall establish priorities based on primacy of facility EVSP to determine PEV response to broadcasted IOU DR or RTP or other pricing signals. 2. OVGIP identification of PEVs plugged in at facility will be based on geo fencing coordinates of the facility - altrenatively the EVSP may be able to provide PEV ID to OVGIP at time of plug in. |  | PEV | Primary | None | None | None | None | Primary | Optional | None | None | Secondary
Optimized Load Management utilizing ISO/ IEC 15118 Protocol | X |  | X |  | X |  |  | NSP / OVGIP / EVSE / PEV / Customer | 1. This use case addresses the implementation of the OVGIP communications to the PEV through the EVSE utilizing the 15118 protocol. Communications between the NSP and OVGIP follow the requirements of the PEV Aggregation Use Case. The differentiation is the communications pathway from the OVGIP to the PEV utilizes internet protocols between the OVGIP and the EVSE with translation to !5118 from the EVSE to the PEV. 2. OVGIP shall communicate with the NSP for DR and Pricing event signals and allocate signals to the appropriate EVSEs 3. EVSE shall have the SECC functionality to translate the OVGIP messages and commands to the 15118 protocol and EV shall have the EVCC to communicate 15118 message protocol with the EVSE. | 1. Shall have security for customer data privacy and protection from external attacks. Requires security from point to point in this case from OVGIP to the PEV. 2. OVGIP shall communicate with eMobility Operators who maintain subscription contracts with PEV customers for purposes of authenticating and authorizing customers to charge at specific EVSEs 3. OVGIP shall communicate charge session data to the eMobility Operators for customer billing purposes as a clearing house functionality. In this regard the OVGIP can be the eMobility Operator who maintains customer accounts and controls communications to the EVSE. | 1. Customer should receive notifications/alerts about charging status based on scheduled parameters from the PEV 2. Customer should have capability to opt in/out of load management directive based on TCIN 3. PEV should be ableto make the opt in/out determination based on TCIN, power requriements, and other customer PEV charge settings | 1. Assumes all EVSE shall have sub metering functionality for M&V settlements 2. OVGIP will be responsible to provide aggregated PEV load capacity projections for appropriate energy market bidding programs based on PEV customer charging behavior data, and based on primacy considerations for on site energy managment control implementations |  | PEV | None | Primary | Secondary | Optional | None | None | None | Primary | None | Secondary
Vehicle Roaming | X |  | X |  | X |  |  | OVGIP / eMobility Operators / Utilities | None | There are no VGI functional communications for this use case. Is predominantly a business transaction use case for providing clearing house functionality between mutiple eMobility Operators who have subscription agreements with customers for access and utilization of the eMobility Operator owned EVSEs. Could apply to inter utility clearing house customer account management wherein a customer has a primary utility account for his residence and all EV charging by the customer in other utility territories are processed between utilities through a clearing house in order to consolidate the customer EV charging costs on his primary residence utility bill. . Shall have security for customer data privacy and protection from external attacks. | N/A | N/A |  | N/A | None | None | None | None | None | None | None | None | None | None
EVSE Networking Functionality | X |  | X |  | X |  |  | OVGIP / EVSE | None | There are no VGI functional requirements. Use Case is predicated on the OVGIP being the EVSP for direct networking of EVSEs. OVGIP shall provide the functionality for EVSE manufacfturers to monitor EVSE locations, availability, reservation, and diagnostics for EVSE status monitoring and customer information | N/A | N/A |  | N/A | None | None | None | None | None | None | None | None | None | None
Metering and Data Exchange Monitoring and Measuring | X |  | X | X |  | X |  | OVGIP / Utilities / PEV | 1. Use Case is predicated on the requirements for measurement and verification utilizing utility grade metering data 2. OVGIP shall have access to customer residential account metering data and EV sub metering account data through communications with the customer residential designated utility. 3. Metering data will be correlated with PEV charge data to report customer performance for residential DR and Pricing event programs. This is provided as basis for determining customer responsiveness to the program and entitlement to compensation per the utility program requirements. | 1. Shall have security for customer data privacy and protection from external attacks. 2. OVGIP should have access to utility customer account data if required for M&V purposes. 3. Utilities / ISO could have option to utilize the data from the PEV telemetry for M&V purposes per their determination. | 1. Customer should have visibility about information being provided especially that which affects performance compensation | N/A | 1. Utility / ESP / Aggregator (NSPs) have authority to establish M&V requirements for specific energy management and energy market programs. For specific aggregation programs NSP could accept PEV telemetry data for electricity consumption for managed charging. | PEV | None | None | Primary | Primary | None | None | None | None | None | None
Customer Enrollment | X |  | X |  | X |  |  | OVGIP (Aggregator) / Utility / Customer | None | 1. There are no VGI functional communications requirements for this use case. 2. Basis for this use case is to define a consolidated and consistent enrollment process for all utility programs that is applicable to all OEMs participating and utilizing the OVGIP as th e aggregator interface to the NSPs. 3. Primary emphasis is to establish a one form customer authorization agreement that provides customer permission for utilities and OEMs to share their PEV charging related utility account and behavior data to enable the VGI programs. 4. Customer enrollment responsibility is determined based on the utility or ESP program requirements. The common issue is the customer permissions to access and share their data between primary and secondary actors to enable engagement and execution of the VGI program. 5. Shall have security for customer data privacy and protection for external attacks | 1. Customer authorizations for access to utility account data must be obtained to share data between Utility and OVGIP. 2. Agreements for data privacy terms and conditions shall be instituted between stakeholders |  |  | N/A | None | None | None | Primary | None | None | None | None | None | None
Overgeneration Support | X |  | X |  | X |  |  | ISO / Utility / Aggregator / Fleet Management System / BMS / PEV / Customer | 1. NSP (ISO/DSO) projects day ahead periods for renewables over generation and shall transmit either Dynamic Price (Assumption is that the price during over generation will be a discounted kWH rate to incentivize daytime charging) or DR event signals to increase PEV charging load (Assumpition is there will be incentives for customer participation). In the workplace scenario customers shall be notified to ensure SOC capacity is available for charging at work during the day.Workplace may offer flow down incentives to employees for this purpose. 2. Signals shall be received by Aggregator / Fleet Management System / BMS. Fleet Management System and BMS can be synonymous. 3. Aggregator / Fleet Management System / BMS shall process and transmit Dynamic Price or DR event information to the PEV. Fleet Management Systems / BMS may operate as site controllers for managing charging in accordance with the Site Controller Use Case. 4. PEV shall start / stop charging according to the Price or DR event signals or site controller commands. 5. Aggregators could interact with multiple Fleet Management Systems / BMS as part of ISO or Uility wholesale energy market or capacity bidding programs. Refer to Aggregated PEV Demand Response (DR) and Critical Peak Pricing (CPP) Use Case. | 1. Customers or Employees shall have opt in/out priveleges based on SOC or TCIN 2. Customer shall be provided notificatons / alerts through smart phone APP. Assumes customer can monitor PEV charge status via APP for PEV communications which will provide alerts for changes to charging status. 2. Fleet Management Systems / BMS shall have override capability to ensure PEV load management meets facility and fleet energy management objectives. 3. M&V could be based on PEV energy measurement telemetry, site meters, or sub meters per the requirements of the cognizant NSP. |  |  | 1. TOU rates may be established to acccount for renewable overgeneration. In this case the TOU rate tariffs will be transmitted from the utility to the PEV which will charge based on customer PEV charge settings / preferences - to charge at the lowest price periods per the TOU schedule. See Automated Utility Tariff Processing. Use Case | PEV | Primary | None | Optional | Secondary | None | Primary | None | None | None | Secondary
Residential Peak Demand Management (Evening Ramp) | X |  | X |  | X |  |  | ISO / Utility / Aggregator / PEV | 1. NSP (ISO / Utility) shall project PEV load reduction parameters for mitigating evening peak demand. Parameters provide time duration (start stop times), location (feeder/transformer/Sub lap/etc.), percent or kW reducton. 2. NSP shall transmit DR or Dynamic Price signals to the Aggregator 3. Aggregator shall transmit DR or Dynamic Price signals to the PEV 4. PEV shall respond to the signal according to the customer TCIN preferences and charge settings. | 1. M&V could be based on PEV energy measurement telemetry, site meters, or sub meters per the requirements of the cognizant NSP. 2. Customer shall be provided notificatons / alerts through smart phone APP. Assumes customer can monitor PEV charge status via APP for PEV communications which will provide alerts for changes to charging status. |  |  | 1. TOU rates may be established to acccount for peak demand periods. In this case the TOU rate tariffs will be transmitted from the utility to the PEV which will charge based on customer PEV charge settings / preferences - to charge at the lowest price periods per the TOU schedule. See Automated Utility Tariff Processing. Use Case | PEV | Optional | None | Primary | None | None | Optional | None | None | None | Secondary
Monitoring and Measurement REQUIREMENTS NORMALIZED | X |  | X | X | X | X |  | Utility / DSO / Aggregator / PEV / Customer | Scenario A 1. Utilities want to be able to monitor PEV customer charge behavior and be able to provide incentives or discounted EV price/rates that influence when customers charge. Utility needs data on customer charge times , location, charge rate, SOC and measurement of electricity consumption. 2. Aggregator shall have access ( i.e. through OEM servers) to monitor PEV for data on SOC , charge times, duration, charge rate, electicity consumption, and location. 3. Aggregator shall provide specific customer PEV charging data to utility as measurement and verification for customer incentive according to utility program requirements. Data can be reported on weekly, monthly, or other frequency basis. Scenario B 1. Utllities want PEV charge data for situational awareness and basis of strategies and program determinations for asset upgrade deferral. 2. Aggregator shall have access (i.e. through OEM servers) to monitor PEV charge behavior information (aggregated PEV load profile data across periods of the day) segregated by specific utility distribution locations and segments (Sub Laps, Feeders, Sub Feeders, Transformers, etc) 3. Aggregator shall provide aggregated PEV load profile data to utilities for use in determining load managment stratigies and programs to support asset upgrade deferral. Scenario C 1. Utilities want situational awareness monitoring information on PEV aggregated locational load data. Requires near real time monitoring of PEV SOC and location to identify near term load impact for PEV charging. Is appropriate for advent of autonomous PEV car sharing fleets which require PEVs to be immediately charged on a continuous basis to provide intended customer transportation services. 2. Aggregators shall have access to monitor PEV SOC and location information on real time basis. Aggregator shall be able to formulate projected locational charging loads based on PEVs SOC which provide indications of required near time charging. 3. Expanded functionality of Aggregator is ability to provide EVSE networking capabilities to identify nearest available charging location for autnomous vehicles. | 1. System shall have end to end security to protect customer data privacy and to protect from external attacks. 2. Assumes that customer permissions and enrollaments as required are in place for accessing and sharing their PEV charge information between Aggregator and utilities. | 1. Customers could want access to their PEV charge data provided to the utilities by the Aggregator. 2 Customer wants the lowest cost of kWh; however, still needs to leave at a set time with the maximum SOC possible | Customer interface via SMART phone to select the best possible option available at the time of this charging event. | 1. TOU rates may be established to acccount for peak demand periods. In this case the TOU rate tariffs will be transmitted from the utility to the PEV which will charge based on customer PEV charge settings / preferences - to charge at the lowest price periods per the TOU schedule. See Automated Utility Tariff Processing. Use Case | PEV | None | None | Primary | Secondary | None | None | None | None | None | Primary
Monitoring and Measurement ORIGINAL USE CASE | X |  | X | X | X | X |  | Utility / DSO / Aggregator / PEV | Scenario A 1. Utilities want to be able to monitor PEV customer charge behavior and be able to provide incentives or discounted EV price/rates that influence when customers charge. Utility needs data on customer charge times , location, charge power rate, and measurement of electricity consumption. 2. Aggregator shall have access ( i.e. through OEM servers) to monitor PEV for data on SOC , charge times, duration, charge power rate, electicity consumption, and location. 3. Aggregator shall provide specific customer PEV charge data to utility as measurement and verification for customer incentive according to utility program requirements. Data can be reported on weekly, monthly, or other frequency basis. Scenario B 1. Utllities want PEV charge data for situational awareness and basis of strategies and program determinations for asset upgrade deferral. 2. Aggregator shall have access (i.e. through OEM servers) to monitor PEV charge behavior information (aggregated PEV load profile data across periods of the day) segregated by specific utility distribution locations and segments (Sub Laps, Feeders, Sub Feeders, Transformers, etc) 3. Aggregator shall provide aggregated PEV load profile data to utilities for use in determining load managment stratigies and programs to support asset upgrade deferral. Scenario C 1. Utilities want situational awareness monitoring information on PEV aggregated locational load data. Requires near real time monitoring of PEV SOC and location to identify near term load impact for PEV charging. Is appropriate for advent of autonomous PEV car sharing fleets which require PEVs to be immediately charged on a continuous basis to provide intended customer transportation services. 2. Aggregators shall have access to monitor PEV SOC and location information on real time basis. Aggregator shall be able to formulate projected locational charging loads based on PEVs SOC which provide indications of required near time charging. 3. Expanded functionality of Aggregator is ability to provide EVSE networking capabilities to identify nearest available charging location for autnomous vehicles. | 1. System shall have end to end security to protect customer data privacy and to protect from external attacks. 2. Assumes that customer permissions and enrollaments as required are in place for accessing and sharing their PEV charge information between Aggregator and utilities. | 1. Customers could want access to their PEV charge data provided to the utilities by the Aggregator. |  |  |  | None | None | Primary | None | None | None | None | None | None | None
Spin/Non-Spin Reserves - Emergeny Despatch | X | X | X |  |  |  |  | NSP,Aggregator, EV | The PFE could send the send the following Commands and the EVBS who shall respond accordingly: 1) The EVBS shall respond to dispatch in emergency within 10 minutes through PFE or BMS. for regional regulation | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity (PFE), the EVBS shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | The Utility Customer of Record or EVBS perferences could opt-out, depending upon mutually agreeed contract |  | Load Control only (V1G) to EVSE using SAE J1772 | None | Alternative | Primary | None | None | None | None | None | None | None | None
Freequency Regulation - Provide frequency stability (i.e. regulate up or down) via aggregation during demand/supply imbalance by quickly ramping to accurately follow an automatic generation control signal | X | X | X |  |  |  |  | NSP, Aggregator, EV | The PFE could send the send the following Commands and the EVBS who shall respond accordingly: 1) The EVBS shall respond to up/down regulation signals - Alternative being proposed at DERP proceedings and Rule 21. 2) The Energy Meter shall provide real-time telemetery 4s - 5 Minutes with +/-2% accuracy. 3) PFE Communication shall be less than 4s latency. | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity (PFE), the EVBS shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | The Utility Customer of Record or EVBS perferences could opt-out, depending upon mutually agreeed contract |  |  | None | None | Primary | None | None | None | None | None | None | None | None
Dampen variability of randomly fluctuating load by accommodating expected ramp up and down rates (MW/minute) for a given duration | X | X | X |  |  |  |  | NSP, Aggregator, EV | The PFE could send the send the following Commands and the EVBS who shall respond accordingly: 1) The EVBS shall respond to up/down regulation signals - Alternative being proposed at DERP proceedings and Rule 21. 2) The Energy Meter shall provide real-time telemetery 4s - 5 Minutes with +/-2% accuracy. 3) PFE Communication shall be less than 4s latency. | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity (PFE), the EVBS shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | The Utility Customer of Record or EVBS perferences could opt-out, depending upon mutually agreeed contract |  |  | None | None | Primary | None | None | None | None | None | None | None | None
Resource Adequacy - RA is a planning and procurement process to ensure that capacity exists and is under contract so responsible LSEs can serve all of their load and ensure that the ISO can meet its operational needs and maintain reliability. | X | X | X |  |  |  |  | IOU, Aggregator, EV | The NSP shall send the send the following Commands and the EV or Aggregator who shall respond accordingly: 1) Aggregators offering resources participating in ISO markets under an RA contract have an RA shall-offer-obligation to the ISO. 2) System and local RA have explicit 24 hour shall-offer requirements. 3) RA capacity that is contracted for as RA capacity for even one hour in a day is considered RA for an entire day. 4) In addition to having a shall-offer obligation, RA capacity is (1) ineligible to receive payments under the ISO’s backstop capacity procurement mechanism (“CPM”), and (2) ineligible to receive residual unit commitment (“RUC”) payments and must bid in to RUC at $0. Note: ISO uses MUST for Shall (as shown here) | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity, the EV shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | The Customer or EV perferences could opt-out, depending upon mutually agreeed contract |  |  | None | None | Primary | None | None | None | None | None | None | None | None
Distribution Voltage Maintenance & Support - Discharge real power to regulate system voltage within standard tolerance band | X | X | X | X |  |  |  | IOU, EV | The IOU shall send the send the following Commands and the EV or Aggregator who shall respond accordingly: 1) The EV Shall provide VAR as defined under Rule 21 Phase 1 for V2G. 2) The EV should provide VAR support as defined under Rule 21 Phase 1 for load | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity, the EV shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | The Customer or EV perferences could opt-out, depending upon mutually agreeed contract |  |  | None | None | Primary | None | None | None | None | None | None | None | None
Distribution Capacity Deferral - Delay or avoid distribution infrastructure investments by using aggregated DERs to manage system peak and/or provide energy at times when there is a distribution capacity constraint | X | X | X |  |  |  |  | IOU, Aggegator, EV | The IOU shall send the send the following Commands and the EV or Aggregator who shall respond accordingly: 1) The EV Shall support Rule 21 requirements for V2G. 2) The EV Shall support Rule 21 requirements for load control | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity, the EV shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | The Customer or EV perferences could opt-out, depending upon mutually agreeed contract |  |  | None | None | Primary | None | None | None | None | None | None | None | None
Distribution Reliability Back Tie -A specific type of distribution capacity deferral where the distribution capacity constraint will arise if/when a circuit is switched to feed load of another feeder | X | X | X |  |  |  |  | IOU, Aggegator, EV | The IOU shall send the send the following Commands and the EV or Aggregator who shall respond accordingly: 1) EV Shall support Utility DR load curtailment requests | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity, the EV shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | The Customer or EV perferences could opt-out, depending upon mutually agreeed contract |  |  | None | None | Primary | None | None | None | None | None | None | None | None
Distribution Resiliency/Microgrid - A specific type of distribution capacity deferral where resource can create a microgrid to alleviate a specific distribution capacity constraint | X | X | X |  |  |  |  | IOU Aggregator, BMS, EV | The IOU shall send the send the following Commands and the EV or Aggregator who shall respond accordingly: 1) The EV could support Islanding for Microgrid 2) The EV could support local control (switch from Utility) | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity, the EV shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | The Customer or EV perferences could opt-out, depending upon mutually agreeed contract |  |  | None | None | Primary | None | None | Primary | None | None | None | None
On-Site Power Quality - EV ramps up/down charging or discharges in response to dampen power quality issues such as voltage or harmonics fluctuations. | X | X | X |  |  |  |  | IOU, Aggregator, BMS, EV | The BMS shall send the send the following Commands and the EV or Aggregator who shall respond accordingly:1) The EV shall respond to Power quality Commands from the BMS | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity, the EV shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | The Customer or EV perferences could opt-out, depending upon mutually agreeed contract |  |  | Secondary | None | Primary | None | None | Secondary | None | None | None | None
On Site Power Reliability (Back Up Power) - EV provides power to a site during a grid outage event. (likely requires energy management system) | X | X | [5 empty] | BMS, EV | The BMS shall send the send the following Commands and the EV or Aggregator who shall respond accordingly: 1) The EV shall island itself under command of the BMS or Automatically | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity, the EV shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | The Customer or EV perferences could opt-out, depending upon mutually agreeed contract |  |  | None | None | None | None | None | Primary | None | None | None | None
Create GHG Credits - Provide GHG benefits by shifting electricity use from a time when a fossil fueled resource is on the margin to a time when a renewable resource is on the margin. Potentially monetizable if such shifting can create credits that can be sold or can help the customer meet GHG obligations (may only apply to large customers in certain industries). | X | X | X |  |  |  |  | IOU, Aggregator, BMS, EV | The IOU shall send the send the following Indicator and the EV or Aggregator who shall respond accordingly: 1) The EV shall be capable of receiving a Utility signal that indicates renewable Energy or Fossile fuel mix are generating the energy to receive carbon credit and act accordingly | 1) The Communications shall be cybersecure and encrypted end to end. 2) In the event of communication failure of any kind with the controlling entity, the EV shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | 1) The Customer should be able to select when to charge depending on whether renewables are being generated. 2) The Customer or EV perferences could opt-out, depending upon mutually agreeed contract |  |  | None | None | Primary | None | None | None | None | None | None | None
Rule 21 |  | X | X | X | X | X |  | Utility, Aggregator, BMS or EMS, EV | 1) The Utility shall be able to send a command or an event to the Aggregator or to the EV for the following local control of the EV Inverter (onboard or offboard) 2) The EV shall send confirmations and status information to the Aggregator or to the EMS 3) CA Rule 21 defines the following Functions: I. Anti-Islanding Protection II. Low and High Voltage Ride-Through III. Low and High Frequency Ride-Through IV. Dynamic Volt-Var Operation V. Ramp Rates VI. Fixed Power Factor VII. Frequency/Watt VIII. Volt/Watt IX. Monitoring X. Connect/Disconnect XI. Set Max Active Output XII. Set Active Power Setpoint XIII. Scheduling XIV. Dynamic Reactive Current (optional) 4) CA Rule 21 requires the following responses: I. Operational State II. Percentage of rated Capacity III. Operational Mode IV. Real Power Output (Meter Readings) | 1) The communications between the Utility-Aggregator , the Aggregator-EV, and the Utility-EV shallbe secure | 1) The Customer should be able to ascertain which mode the Inverter is participating and the effect on his battery capacity and opt-out of an event | 1) EV's with onbaord inverters shall be required to obtain site configuration and approval to discharge based upon Utility approval |  | None | None | Primary | Optional | None | Secondary | None | None | None | Secondary
Note on K28: Atkins, Lance: The ECS connection activity may belong in the Other requirements section.
Note on H37: Dean Taylor: see Use case on "what do drivers want" - originally classified as other, but this example was pulled out as new use case
Note on P37: primary path is NSP 's site controller to a trip relay which is not on this sheet
Note on H40: Dean Taylor: see Use case on "what do drivers want" - originally classified as other, but this example was pulled out as new use case
Note on H41: Dean Taylor: see Use case on "what do drivers want" - originally classified as other, but this example was pulled out as new use case

## 1 Functional requirement matrix
Category/ Requirement ID | Functional Requirements | Direction | Should Shall Could | PFE and BMS | BMS and EVBS | BMS and DCPC | BMS and EVSE | PFE and EVBS | PFE and DCPC | PFE and EVSE | EVBS and DCPC | PFE and EV Driver | BMS and EV Driver | EVBS and EV Driver | EVSE and EVBS | Acknowledge [receive] | Opt-out [receive] | Notes: | LEGEND
1- Rule 21 | For Generation control, send DER Curves and Controls (Rule 21) as Events or controls with start time and duration | [17 empty] | ✔
F.1.01 | Low and High Voltage Ride-Through | > | Shall | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | N/A | ✔ | ✖ | * is alternative to ISO up/down regulation The Shall may not apply in all circumstances (e.g. utilities) | ✖
F.1.02 | Low and High Frequency Ride-Through |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | N/A | ✔ | ✖ |  | N/A
F.1.03 | Dynamic Volt-Var Operation |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | N/A | ✔ | ✖ |  | >
F.1.04 | Ramp Rates |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | N/A | ✔ | ✖ |  | <
F.1.05 | Fixed Power Factor |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.06 | Frequency/Watt* |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.07 | Volt/Watt |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.08 | Connect/Disconnect |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | N/A | ✔ | ✖
F.1.09 | Set Max Active Output* |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.1 | Set Active Power Setpoint |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.11 | Scheduling |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.12 | Dynamic Reactive Current (optional) |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.13 | Site Information (e.g. Line Voltage) |  |  | ✔ | ✔ | N/A | ✖ | ✔ | N/A | ✖ | N/A | ✖ | ✖ | ✖ | ✔ | ✔ | ✖
F.1.14 | Permission to Dischage |  |  | ✔ | ✔ | N/A | ✖ | ✔ | N/A | ✖ | N/A | ✖ | ✖ | ✖ | ✔ | ✔ | ✖
F.1.15 | Contain Dispatch Location Information |  | Should | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✔ | ✔ | ✔ | ✔ | ✖ | ✔ | ✖
F.1.16 | Provide Inverter Make, Model and Approval status | < | Shall | ✔ | ✔ | N/A | ✖ | ✔ | N/A | ✖ | N/A | ✖ | ✖ | ✖ | ✔ | N/A | N/A
F.1.17 | DER Status information |  | Should | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
2- Pricing | Send Pricing or Tariff
F.2.01 | Tiered | > | Could | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✖ | N/A | Up to 30 days may be requested
F.2.02 | ToU |  | Shall | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✖ | N/A
F.2.03 | Critical Peak Pricing |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✖ | N/A
F.2.04 | Real Time Pricing (Hourly) |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✖ | N/A
F.2.05 | Special Tariffs (e.g. Price Interrupted) |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✖ | N/A
3- Load Control | Send Load Control Information (Increase charge or reduce Charge) with start time and duration
F.3.01 | Upto Day ahead using DR events | > | Shall | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✔ | ✔ | ✔ | ✔ | ✖ | ✔ | ✔
F.3.02 | Upto Day ahead using DER (Load) events | bar: ✔ to ✔
F.3.03 | Immediate emergency DR control (10 Minute response) | bar: ✔ to ✔
F.3.04 | Immediate emergency DER control (10 Minute response) | bar: ✔ to ✔
F.3.05 | Should have Primacy and Define Priority (e.g. BMS over PFE) |  | Should | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✔ | ✔ | ✔ | ✔ | ✖ | ✔ | ✖
F.3.06 | Contain Dispatch Location Information | bar: ✔ to ✔
4- Smart Charging | Negotiate Optimum Charging or Generatio based upon driver or site preferences
F.4.01 | Departure Time | > | Shall | ✖ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✔ | ✔
F.4.02 | Charge Rate | bar: ✖ to ✔
F.4.03 | Energy Required | bar: ✖ to ✔
F.4.04 | When the EVBS connects to the DCPC, the EVBS shall engage in DC DER Mode (should) | bar: ✖ to ✔
F.4.05 | Exchange information to manage DC power Flow | bar: ✖ to ✔
F.4.06 | Max Charge Rate |  |  | ✔ | ✔ | N/A | ✖ | ✔ | N/A | ✖ | N/A | ✖ | ✖ | ✖ | ✖ | ✔ | ✖
F.4.07 | Request Current Charge Power and SoC |  | Should | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖
F.4.08 | Departure Time | < | Shall | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | N/A | N/A
F.4.09 | Charge Rate |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | N/A | N/A
F.4.1 | Energy Required |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | N/A | N/A
F.4.11 | Departure Time |  |  | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✔ | ✖ | N/A | N/A
F.4.12 | Desired SoC |  |  | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✔ | ✖ | N/A | N/A
F.4.13 | Price to Charge |  | Should | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✔ | ✖ | N/A | N/A
F.4.14 | Provide SoC on a regular basis |  |  | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
5- Monitoring | Charge Event Data For M&V, Billing, and Monitoring
F.5.01 | Start Time | < | Shall | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
F.5.02 | End Time |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
F.5.03 | KWh |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
F.05.04 | KW |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
6- Restart | Set Power Restoration Parameters
F.6.01 | Soft Start | > | Should | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✔ | ✖
F.6.02 | Random delay Start | bar: ✔ to N/A
F.6.03 | Ramp times | bar: ✔ to N/A
7- Miscellaneous | Other Requirements
F.M1 | GPS Location | < | Should | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
F.M2 | Send Renewable or Fossil Mix | > | Should | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✖ | ✖ | ✖ | ✖

## 2. non-functional requirements
Category
NF 2.01 | Cyber securuity best practices be used to protect customer data and prevent external attacks NISTR 7628. | Security and privacy
NF 2.02 | EV Driver and Customer of Record shall have provided required permissions and enrollments as for accessing and sharing their EVBS charge information and any required Energy Meter charge measurement and verification data with PFE and / or BMS.
NF 2.03 | Authentication and Authorization of the EVBS by the PFE or BMS shall be automatic
NF 2.04 | PFE/BMS and EVBS communications containing control data or publicly identifiable information (PII), or data that can be used to calculate PII, shall be encrypted
NF 2.05 | Communications between the EVBS and PFE/BMS that contains PII or control data should be encrypted end to end
NF 2.06 | the EVBS and PFE/BMS Communications shall utilize authentication and authorization
NF 2.07 | BMS and EVBS or EVC could negotiate power levels based upon pricing curve (such as paying more for a higher power or earlier departure time).
NF 2.08 | The EVBS and DCPC shall exchange information to jointly manage the DC power flow during a session. | DC
NF 2.09 | EVBS receptacle and DCPC cable plug shall be physically compatible for DC transfer and provide interoperable communications.
NF 2.10 | EVSE should have status and feedback information to UCR or EVD
NF 2.11 | In the event of communication failure of any kind with the PFE or BMS, the EV shall default to a known default state and not the last state. The state shall be defined, for maximum safe operation for any grid condition. | Messaging
NF 2.12 | The PFE could send the send the following Commands and the EVBS or PFE who shall respond accordingly: 1) The Site Meter shall provide real-time telemetery 4s - 5 Minutes with +/-2% accuracy. 2) ISO Communication shall be less than 4s latency.
NF 2.13 | The Communications could use message compression technique to increase the communications efficiency
NF 2.14 | PFE shall have access to EVBS charge history data to be able to formalize DR capacity projections required for energy market and bidding capacity programs. | EVBS
NF 2.15 | EVBS Data (ex measurement and verification for incentives) such as ( charge times, duration, charge power rate, electicity consumption, and location) shall be reported by regional locations and/or distribution circuit levels such as transformer, sub-feeder, feeder, sublap, etc. Data should be available in PFE prescribed intervals. according to PFE prescribed requoirements.

## 3. customer requirements
C 3.01 | The Customer should have the capability of opting out of an event/directive
C 3.02 | The Customer shall be able to set or otherwise convey energy parameters and/or operational mode preferences
C 3.03 | The EV driver shall receive notifications or alerts about charging status and DR event schedules
C 3.04 | The customer should have the ability to review pricing
C 3.05 | Customers could want access to their charge data provided to the PFE and/or BMS by their EVBS.

## 4. other requirements
Oth 4.01 | BMS could exchange data such as pricing or desired power level with the PFE regardless of how implemented onsite
Oth 4.02 | The site EVPC shall be programmed with the site specific settings and be approved by permit
Oth 4.03 | The EVPC shall return to the Inverter default state, EVBS shall default as defined in Rule 21 Phase 1 in event of no commands or fault condtions.
Oth 4.04 | Direct communication between EVBS and DCPC is required as described by Use Case DC Flow Management. The DCPC engages the DC DER Mode.
Oth 4.05 | DCPC, EVBS and BMS could be automatically or manually engaged to discharge or operate in an islanded home as backup generator (V2H-DC) which could eliminate need for communication between DCPC and BMS/PFE
Oth 4.06 | PFE should be able to target events to locations based on GPS coordinates, physical locaiton or other criteria.
Oth 4.07 | M&V and billing requirements and utilization of data should be subject to PFE or regulatory requirements.
Oth 4.08 | If the BMS is managing the Demand charge for the Site, the BMS shall be able to obtain the total site power level

## 5. alternative requirements
Alt 5.01 | For non-communication EVBS, BMS or PFE could manage the EVBS load by using the EVSE J1772 Control
Alt 5.02 | EVSE could be user programmed with parameters such as TOU tarifs or other scheduling
Alt 5.03 | EVSE could have PFE communication for updating TOU pricing & schedule
Alt 5.04 | PFE energy meter could disconnect EVSE in some instances to reduce power, typically in an emergency setting