## Functional Requirements
SME | Gordon Lum |  | Protocol | IEEE 2030.5 |  |  | Version | 2017
Category/ Requirement ID | Functional Requirements | Direction | Should Shall Could | PFE and BMS | BMS and EVBS | BMS and DCPC | BMS and EVSE | PFE and EVBS | PFE and DCPC | PFE and EVSE | EVBS and DCPC | PFE and EV Driver | BMS and EV Driver | EVBS and EV Driver | EVSE and EVBS | Acknowledge [receive] | Opt-out [receive] | Notes:
1- Rule 21 |  | For Generation control, send DER Curves and Controls (Rule 21) as Events or controls with start time and duration
F.1.01 | Low and High Voltage Ride-Through | > | Shall | Y | Y | Y |  | Y | Y |  | N |  |  |  | NA | Y |  | Directly maps to IEEE 1547
F.1.02 | Low and High Frequency Ride-Through |  |  | Y | Y | Y |  | Y | Y |  | N |  |  |  | NA | Y |  | Directly maps to IEEE 1547
F.1.03 | Dynamic Volt-Var Operation |  |  | Y | Y | Y |  | Y | Y |  | N |  |  |  | NA | Y
F.1.04 | Ramp Rates |  |  | Y | Y | Y |  | Y | Y |  | N |  |  |  | NA | Y* |  | DefaultDERControls does not have explicit Ack, but can be inferred from the end of an active DERControl
F.1.05 | Fixed Power Factor |  |  | Y | Y | Y |  | Y | Y |  | N | Y* | Y* | Y* | - | Y | Y | Need to clarify Driver role
F.1.06 | Frequency/Watt* |  |  | Y | Y | Y |  | Y | Y |  | N | Y* | Y* | Y* | - | Y | Y | Need to clarify Driver role
F.1.07 | Volt/Watt |  |  | Y | Y | Y |  | Y | Y |  | N | Y* | Y* | Y* | - | Y | Y | Need to clarify Driver role
F.1.08 | Connect/Disconnect |  |  | Y | Y | Y |  | Y | Y |  | N |  |  |  | NA | Y
F.1.09 | Set Max Active Output* |  |  | Y | Y | Y |  | Y | Y |  | N | Y* | Y* | Y* | - | Y | Y | Need to clarify Driver role
F.1.1 | Set Active Power Setpoint |  |  | Y | Y | Y |  | Y | Y |  | N | Y* | Y* | Y* | - | Y | Y | Need to clarify Driver role
F.1.11 | Scheduling |  |  | Y | Y | Y |  | Y | Y |  | N | Y* | Y* | Y* | - | Y | Y | Need to clarify Driver role
F.1.12 | Dynamic Reactive Current (optional) |  |  | N | N | N |  | N | N |  | N | N | N | N | - | N | N
F.1.13 | Site Information (e.g. Line Voltage) |  |  | Y | Y | N/A |  | Y | N/A |  | N/A |  |  |  | ✔️ | Y |  | Hank McGlynn clarified this comes from J3072, so IEEE 2030.5 supports this.
F.1.14 | Permission to Dischage |  |  | Y | Y | N/A |  | Y | N/A |  | N/A |  |  |  | ✔️ | Y |  | Hank McGlynn clarified this comes from J3072, so IEEE 2030.5 supports this.
F.1.15 | Contain Dispatch Location Information |  | Should | Y | Y |  |  | Y |  |  | N | Y* | Y* | Y* | - | Y |  | Josh McDonald clarified this refers to sending dispatch to location-based groups. IEEE 2030.5 supports this.
F.1.16 | Provide Inverter Make, Model and Approval status | < | Shall | Y | Y | N/A |  | Y | N/A |  | N/A |  |  |  | ✔️ | N/A | N/A | Hank McGlynn clarified this comes from J3072, so IEEE 2030.5 supports this.
F.1.17 | DER Status information |  | Should | Y | Y |  |  | Y | Y |  | N |  |  |  | ✖️ | N/A | N/A
2- Pricing |  | Send Pricing or Tariff (Up to 30 days may be requested)
F.2.01 | Tiered | > | Could | Y | Y |  |  | Y |  |  |  | Y* | Y* | Y* | ✖️ |  | N/A | Need to clarify Driver role
F.2.02 | ToU |  | Shall | Y | Y |  |  | Y |  |  |  | Y* | Y* | Y* | ✖️ |  | N/A | Need to clarify Driver role
F.2.03 | Critical Peak Pricing |  |  | Y | Y |  |  | Y |  |  |  | Y* | Y* | Y* | ✖️ |  | N/A | Need to clarify Driver role
F.2.04 | Real Time Pricing (Hourly) |  |  | Y | Y |  |  | Y |  |  |  | Y* | Y* | Y* | ✖️ |  | N/A | Need to clarify Driver role
F.2.05 | Special Tariffs (e.g. Price Interrupted) |  |  | Y | Y |  |  | Y |  |  |  | Y* | Y* | Y* | ✖️ |  | N/A | Need to clarify Driver role
3- Load Control |  | Send Load Control Information (Increase charge or reduce Charge) with start time and duration
F.3.01 | Upto Day ahead using DR events | > | Shall | Y | Y |  |  | Y |  |  | N | Y* | Y* | Y* | - | Y | Y | Need to clarify Driver role
F.3.02 | Upto Day ahead using DER (Load) events |  |  | Y | Y |  |  | Y |  |  | N | Y* | Y* | Y* | - | Y | Y | Need to clarify Driver role
F.3.03 | Immediate emergency DR control (10 Minute response) |  |  | Y | Y |  |  | Y |  |  | N | Y* | Y* | Y* | - | Y |  | Need to clarify Driver role. PFE/BMS can control polling rate of client DR device
F.3.04 | Immediate emergency DER control (10 Minute response) |  |  | Y | Y |  |  | Y |  |  | N | Y* | Y* | Y* | - | Y |  | Need to clarify Driver role. PFE/BMS can control polling rate of client DER device
F.3.05 | Should have Primacy and Define Priority (e.g. BMS over PFE) |  | Should | Y | Y |  |  | Y |  |  | N | Y* | Y* | Y* | - | N |  | Need to clarify Driver role. Primacy is part of the Program data. There is no explicit Ack for Program data.
F.3.06 | Contain Dispatch Location Information |  |  | Y | Y |  |  | Y |  |  | N | Y* | Y* | Y* | - | Y |  | Josh McDonald clarified this refers to sending dispatch to location-based groups. IEEE 2030.5 supports this.
4- Smart Charging |  | Negotiate Optimum Charging or Generation based upon driver or site preferences
F.4.01 | Departure Time | > | Shall |  | Y |  |  | Y |  |  |  | Y* | Y* | Y* | - | Y | Y | FlowReservationResponse:interval
F.4.02 | Charge Rate |  |  |  | Y |  |  | Y |  |  |  | Y* | Y* | Y* | - | Y | Y | FlowReservationResponse:powerAvailable
F.4.03 | Energy Required |  |  |  | Y |  |  | Y |  |  |  | Y* | Y* | Y* | - | Y | Y | FlowReservationResponse:energyAvailable
F.4.04 | When the EVBS connects to the DCPC, the EVBS shall engage in DC DER Mode (should) | [9 empty] | N | [6 empty] | Not sure what this is.
F.4.05 | Exchange information to manage DC power Flow | [9 empty] | N
F.4.06 | Max Charge Rate |  |  | Y | Y | N/A |  | Y | N/A |  | N/A |  |  |  |  | Y | N/A | DERControl:opModMaxLimW
F.4.07 | Request Current Charge Power and SoC |  | Should | Y | Y |  |  | Y | [9 empty] | PFE/BMS does not need to request this info. DER periodically posts it.
F.4.08 | Departure Time | < | Shall | Y | Y |  |  | Y |  |  |  | Y* | Y* | Y* | ✖️ | N/A | N/A | Need to clarify Driver role. FlowReservationRequest:intervalRequested
F.4.09 | Charge Rate |  |  | Y | Y |  |  | Y |  |  |  | Y* | Y* | Y* | ✖️ | N/A | N/A | Need to clarify Driver role. FlowReservationRequest:powerRequested
F.4.1 | Energy Required |  |  | Y | Y |  |  | Y |  |  |  | Y* | Y* | Y* | ✖️ | N/A | N/A | Need to clarify Driver role. FlowReservationRequest:energyRequested
F.4.11 | Departure Time | [12 empty] | Y | ✖️ | N/A | N/A | Can be calculated from other values
F.4.12 | Desired SoC | [12 empty] | Y | ✖️ | N/A | N/A | PowerStatus:PEVInfo:targetStateOfCharge
F.4.13 | Price to Charge |  | Should | [10 empty] | Y | ✖️ | N/A | N/A | Can be calculated from other values
F.4.14 | Provide SoC on a regular basis |  |  |  | Y | [9 empty] | ✖️ | N/A | N/A | PowerStatus:estimatedChargeRemaining
5- Monitoring |  | Charge Event Data For M&V, Billing, and Monitoring
F.5.01 | Start Time | < | Shall | Y | Y |  |  | Y | [6 empty] | ✖️ | N/A | N/A
F.5.02 | End Time |  |  | Y | Y |  |  | Y | [7 empty] | N/A | N/A | Calculated from Start Time and Duration
F.5.03 | KWh |  |  | Y | Y |  |  | Y | [7 empty] | N/A | N/A
F.05.04 | KW |  |  | Y | Y |  |  | Y | [7 empty] | N/A | N/A
6- Restart |  | Set Power Restoration Parameters
F.6.01 | Soft Start | > | Should | Y | Y | Y |  | Y | Y |  |  | Y* | Y* | Y* | - | Y* |  | Need to clarify Driver role. Soft Start is a Default DER Control which does not have an explicit Ack, but can be inferred from the end of an active DER Control
F.6.02 | Random delay Start |  |  | Y | Y | Y |  | Y | Y |  |  | Y* | Y* | Y* | - | Y* |  | Need to clarify Driver role. Soft Start is a Default DER Control which does not have an explicit Ack, but can be inferred from the end of an active DER Control
F.6.03 | Ramp times |  |  | Y* | Y* | Y* |  | Y* | Y* |  |  | Y* | Y* | Y* | - | Y* |  | Need to clarify Driver role. Soft Start is a Default DER Control which does not have an explicit Ack, but can be inferred from the end of an active DER Control. Supports Ramp Rate instead of Ramp Time.
7- Miscellaneous |  | Other Requirements
F.M1 | GPS Location | < | Should | N | N |  |  | N | [6 empty] | ✖️ | N/A | N/A
F.M2 | Send Renewable or Fossil Mix | > | Should | Y | Y |  |  | Y |  |  |  | Y* | Y* |  |  |  |  | Need to clarify Driver role. Supported in the costKind object of the Pricing function set
-
Y
Y*
N