## Use Case Summary Matrix
| Use Case | Submitter | Description | Status | Folder Location |  |  | Primary Actor | Use Case Category | Primary Functional Requirements Category
| Demand Fee Mitigation | Jeremy Whaling | Reduce peak demand to provide more cost effective workplace/public charging | Approved | June 8 Review |  | #REF! | Building Management System | Demand Mitigation | 3- Load Control
| Demand Charge Mitigation Use Case | Rich Scholer | Reduce EV charging or export from EV to reduce a customer's peak demand at their utility meter, thereby reducing overall energy cost | Approved | June 29 Review | 1 | #REF! | EV Battery System | Demand Mitigation | 3- Load Control
| E- General Registration and Enrollment Process/ PEV0 - Customer Enrollment | Rich Scholer | General customer enrollment process to notify utility of presence of EV on site and participate in utility programs | Approved | June 29 Review | 1 | #REF! | EV Driver | Customer Programs | 5- Monitoring
PEV2 – VGI Premise/location variations - Customer plugs in EV to charge | L1 - Customer connects PEV at Home = pev2 | Rich Scholer | Customer is able to charge its EV at home with no additional equipment | Approved | June 29 Review | 1 | #REF! | Utility Customer of Record | Customer Programs | 5- Monitoring
| L2 - Customer connects PEV at another Home | Rich Scholer | Charging in another home with no additional equipment: 1) customer pays utility for power used at another home through utility bill 2) homeowner pays for customer's EV charging session | Approved | June 29 Review | 1 | #REF! | EV Driver | Customer Programs | 5- Monitoring
| L3 - Customer connects PEV outside Home Territory | Rich Scholer | Charging outside of utility territory 1) customer pays for charging session through utility bill 2) customer pays separately for charging session to a different entity | Approved | June 29 Review | 1 | #REF! | EV Driver | Customer Programs | 5- Monitoring
| L4 - Customer connects PEV at Public Location | Rich Scholer | Public charging 1) customer pays for charging session through utility bill 2) customer pays separately for charging session to a different entity | Approved | June 29 Review | 1 | #REF! | EV Driver | Customer Programs | 5- Monitoring
PEV1 – Establish/re-establishing VGI communications - utility sends signals to EV to start communications | PR1 - Customer charges the PEV | Rich Scholer | Process for charging the EV (varies depending on equipment and software used) | Approved | June 29 Review | 1 | #REF! | EV Driver | Monitoring and Measuring | 3- Load Control
| PR2 - Customer discharges the PEV | Rich Scholer | Process for discharging the EV (varies depending on equipment and software used) | Approved | June 29 Review | 1 | #REF! | EV Driver | Monitoring and Measuring | 3- Load Control
| S1 - Cordset (Level 1 Charging) | Rich Scholer | 120V AC to vehicle charging | Approved | June 29 Review | 1 | #REF! | EV Battery System | Monitoring and Measuring | 3- Load Control
| S2 - Premise EVSE (AC) | Rich Scholer | 240V/208V AC to vehicle charging | Approved | June 29 Review | 1 | #REF! | EV Battery System | Monitoring and Measuring | 3- Load Control
| S3 - Premise EVSE (DC) | Rich Scholer | DC to vehicle charging | Approved | June 29 Review | 1 | #REF! | DC Power Converter Systen | Direct Current Flow | 3- Load Control
PEV3 – VGI Program combinations and interactions of utility demand response programs. Refer to U1 or 3 or 4 (price programs) combined with U2 (DRLC) that could also include U5 for optimized charging. | U1 - TOU Program = PEV 3 | Rich Scholer | TOU rates (existing program) | Approved | June 29 Review | 1 | #REF! | Power Flow Entity | Pricing Programs | 2- Pricing
| U2 - Discrete Event Demand Response Program | Rich Scholer | Direct load/price control (enrollment in existing utiliy program) | Approved | June 29 Review | 1 | #REF! | Power Flow Entity | Load Control | 2- Pricing
| U3 - Real Time Pricing (RTP) Program | Rich Scholer | Active management through real-time pricing programs (enrollment in existing utility program) | Approved | June 29 Review | 1 | #REF! | Power Flow Entity | Pricing Programs | 2- Pricing
| U4 - Critical Peak Pricing (CPP) Program | Rich Scholer | Critical peak pricing program (existing program) | Approved | June 29 Review | 1 | #REF! | Power Flow Entity | Demand Mitigation | 2- Pricing
| U5 - Optimized Energy Transfer | Rich Scholer | Programs addressing the utilization and application of managed charging for regulation and ancillary services, mitigating demand charges, and local load balancing (new programs) | Approved | June 29 Review | 1 | #REF! | Power Flow Entity | Demand Mitigation | 4- Smart Charging
| DC EVSE + Telematics use case diagram | Lance Atkins | Vehicle with DC port serves as energy storage to provide renewable energy storage or TOU benefits. If paired with bi-directional EVSE, could serve as back-up power. | Not a Use Case; Used to Support Other Use Cases | June 27 Review |  | #REF!
VGI-Smart Charging use case - Integration of the EV with a facility EMS that includes management of other load devices | 1. Dynamic prioritization/coordination | Barry Sole | Avoids/reduces demand charges by scheduling charging of several EVs and/or other loads | Approved | June 27 Review |  |  | Building Management System | Demand Mitigation | 3- Load Control
| 2. Dynamic charge power | Barry Sole | Energy Management System (EMS) instructs the EV to reduce its charging power (via the EVSE) in response to unforeseen grid conditions to avoid local brownouts | Approved | June 27 Review |  |  | Building Management System | Load Control | 3- Load Control
| 3. Reduce the cost of charging | Barry Sole | Supports facility-wide peak-shaving, off-peak charging time, maximizing the use of renewables through pricing programs | Approved | June 27 Review |  |  | Building Management System | Demand Mitigation | 3- Load Control
| 4 . Open and Manageable | Barry Sole | Any PEV can connect to the facility's EMS through a networked EVSE | See Minutes | June 27 Review |  |  | Energy Connection System | Customer Programs | 5- Monitoring
| DC Energy Flow | Hank McGlynn | Point-to-point communications between the DC charger and the EVSE; can be paired with other types of DER as a more general case of DER grid integration | Approved | June 27 Review |  |  | DC Power Converter Systen | Direct Current Flow | 1- Rule 21
| Automated Utility Electricity Rate Tariff Processing | George Bellino | EV owner can schedule charging through the EV to occur during lowest cost periods based on its rate schedule | Approved | June 22 Review |  |  | EV Driver | Customer Programs | 2- Pricing
| Aggregated PEV Demand Response (DR) and Critical Peak Pricing (CPP) | George Bellino | Aggregated EV demand responds to DR event signals from utility or other ESP/aggregator | Approved | June 22 Review |  |  | Utility Customer of Record | Demand Response | 4- Smart Charging
| Interface with Home Energy Management System (HEMS) or Energy Services Interface (ESI) | George Bellino | Load management information and signals are sent to the EV by the residential HEMS or ESI | Approved | June 22 Review |  |  | Building Management System | Load Control | 4- Smart Charging
| Interface with Building Energy Management System | George Bellino | Load management information and signals are sent to the EV by the BEMS to integrate, monitor and mangage the EV charging load | Approved | June 22 Review |  |  | Building Management System | Load Control | 1- Rule 21
| Interface with EVSE Network Provider | George Bellino | Load management information and signals are sent to the EV through the EVSE network provider | See Minutes | June 22 Review |  |  | Energy Connection System | Load Control | 4- Smart Charging
| Real Time Price (RTP) Signal Event Processing | George Bellino | Automated processing of pricing signals from the utility or other energy service provider/aggregator. Allows EV driver to set price thresholds to stop, curtail, or continue charging depending on needs | Approved | June 22 Review |  |  | Power Flow Entity | Pricing Programs | 4- Smart Charging
| Optimized Load Management (ISO/IEC 15118) | George Bellino | EV charging is managed through a web application that communicates energy market and pricing signals from the ISO, utility, or other ESP with the EVSE network operator | Approved | June 22 Review |  |  | Power Flow Entity | Pricing Programs | 4- Smart Charging
| Vehicle Roaming | George Bellino | Customer's EV charging costs are consolidated across multiple utility service territories into the customer's primary residence utility account | Approved | June 22 Review |  |  | Utility Customer of Record | Customer Programs | 7- Miscellaneous
| EVSE Networking Functionality | George Bellino | EVSE networking functionality that interfaces and interacts with EVSEs from multiple manufacturers and distributors | Approved | June 22 Review |  |  | Energy Connection System | Monitoring and Measuring | 4- Smart Charging
| Metering and Data Exchange | George Bellino | Submeter tracks EV-only energy use and is accessible using a standardized data format that can be integrated with the utility's back-end management systems | Approved | June 22 Review |  |  | Energy Meter | Monitoring and Measuring | 5- Monitoring
| Overgen VGI Use Case IOU-OEM | Joshua McDonald | Shifting PEV charging to coincide with peak PV generation to help absorb overgeneration using demand response or pricing signals | Approved | June 20 Review |  | #REF! | Power Flow Entity | Demand Response | 4- Smart Charging
| Peak Demand Management | George Bellino | Curtail or shift charging, or discharge energy from PVs during times when demand exceeds supply to avoid having to fire peaker plants | Approved | June 20 Review |  |  | Power Flow Entity | Demand Response | 4- Smart Charging
| Voltage Support | George Bellino | EV charging network monitors and responds to voltage issues caused by variable PV generation; regulates charging to help keep voltage within a tolerance band via autonomous Volt-Watt functionality | See Rule 21 Use case | June 20 Review |  |  | Power Flow Entity | Load Control | 3- Load Control
| Residential Peak Demand Management (Evening Ramp) | George Bellino | Mitigate peak evening demand in the residential sector using load management strategies to shift EV charging using dynamic pricing, demand response, and/or discharing from EV batteries onto the grid | Approved | June 20 Review |  | #REF! | EV Driver | Load Control | 3- Load Control
| DC Charge -Discharge system use case | Lance Atkins | Use the EV as emergency backup power or to provide residential power during high cost periods via a power inverter, a dedicated outlet, or an electric switching unit (no power flow back to grid) | Approved | June 15 Review |  | #REF! | Building Management System | Demand Response | 3- Load Control
| PEV as CA Rule 21 DER | Niki DeLeon | EVs interconnect to the grid through Rule 21 using IEEE 2030.5 for stationary, grid-connected inverters and/or SAE J3072 for on-board vehicle inverters. Can serve DER applications including shifting load, absorbing renewable overgeneration, and discharging to the grid during high demand periods. | Approved - See Minutes for additional information | June 15 Review | 1 | #REF! | Energy Connection System | Inverter Control | 1- Rule 21
| DER V2G - AC Use case | Hank McGlynn | A DER is created by connecting a PEV with an onboard inverter to an AC Level 2 EVSE, both certified to SAE J3072. This EVSE-PEV pair can engage in many types of V2G applications based on using IEC 61850 smart inverter functions. | Approved | June 15 Review | 1 | #REF! | Energy Connection System | Inverter Control | 1- Rule 21
| DER V2G - DC Use case | Hank McGlynn | A DER is created by connecting a PEV to an EVSE that includes a four-quadrant power converter (inverter). This EVSE-PEV pair can engage in many types of V2G applications based on using IEC 61850 smart inverter functions. | Approved | June 15 Review | 1 | #REF! | Energy Connection System | Inverter Control | 1- Rule 21
| Fleet Management | Lisa McGee | Use a software platform to manage charging at multiple DCFC and provide load management and grid services using an on-site energy storage system. If fleet operations allow, vehicles could absorb mid-day overgeneration and/or discharge power onto the grid for demand response | Approved | July 6 Review |  | #REF! | Power Flow Entity | Demand Response | 4- Smart Charging
| Improved TOU Rates | Dean Taylor/Bill Boyce/Max Baumhefner/Adam Langton | Use EV-specific rates to encourage charging at super-off-peak hours and reduce overall cost of driving an EV | Approved | July 6 Review | 1 | #REF! | Power Flow Entity | Pricing Programs | 2- Pricing
| Circuit-level load management | Dean Taylor/Mike Bourton/Jordan Smith | Maximize GHG reductions at workplaces by load managing on the circuit level to prevent critical peaks. Load management would be done on a facility level, using software. EV driver would have no control over charging sessions and may not be fully charged. | Post Use-Case Subgroup Submission |  |  |  | Building Management System | Demand Mitigation | 3- Load Control
| EV on-board inverter reacts to voltage fluctuations | Dean Taylor/Mike Bourton/Jordan Smith | An EV with an on-board inverter implements default Autonomous Inverter Functions that support the Grid as per SIWG Phase 1 in response to increases or decreases in voltage | Post Use-Case Subgroup Submission |  |  |  | EV Battery System | Inverter Control | 3- Load Control
| Utility sends demand response signal to EV-only meter | Dean Taylor/Mike Bourton/Jordan Smith | A utility sends an AMI signal to an EV-only meter to manage charging by preventing critical peaks, and providing demand response and some wholesale market services. Can occur at workplaces, fleets, and customer homes | Post Use-Case Subgroup Submission |  |  |  | Power Flow Entity | Vehicle to Grid | 3- Load Control
| Utility sends demand response signal through EV-only meter to building EMS | Dean Taylor/Mike Bourton/Jordan Smith | A utility sends an AMI signal to an EV-only meter, which relays the signal to the facility's EMS to manage the full building's load, including EV charging, to prevent critical peaks and provide demand response and some wholesale market services. Can occur at workplaces, fleets, and customer homes | Post Use-Case Subgroup Submission |  |  |  | Power Flow Entity | Vehicle to Grid | 3- Load Control

## Functional Requirements Matrix
Category/ Requirement ID | Functional Requirements | Direction | Should Shall Could | PFE and BMS | BMS and EVBS | BMS and DCPC | BMS and EVSE | PFE and EVBS | PFE and DCPC | PFE and EVSE | EVBS and DCPC | PFE and EV Driver | BMS and EV Driver | EVBS and EV Driver | EVSE and EVBS | Acknowledge [receive] | Opt-out [receive] | Notes: | LEGEND
1- Rule 21 | For Generation control, send DER Curves and Controls (Rule 21) as Events or controls with start time and duration | [17 empty] | ✔ | Requirement can be met by communication between these two actors
F.1.01 | Low and High Voltage Ride-Through | > | Shall | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | N/A | ✔ | ✖ | * is alternative to ISO up/down regulation The Shall may not apply in all circumstances (e.g. utilities) | ✖ | Requirement cannot be met by communication between these two actors
F.1.02 | Low and High Frequency Ride-Through |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | N/A | ✔ | ✖ |  | N/A | These two actors are not involved in meeting this requirement
F.1.03 | Dynamic Volt-Var Operation |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | N/A | ✔ | ✖ |  | > | The direction of communication between the actors listed (ie PFE > BMS= PFE communicating to BMS)
F.1.04 | Ramp Rates |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | N/A | ✔ | ✖ |  | < | The direction of communication between the actors listed (ie PFE < BMS = BMS communicating to PFE)
F.1.05 | Fixed Power Factor |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.06 | Frequency/Watt* |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.07 | Volt/Watt |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.08 | Connect/Disconnect |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | N/A | ✔ | ✖
F.1.09 | Set Max Active Output* |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.1 | Set Active Power Setpoint |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.11 | Scheduling |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.12 | Dynamic Reactive Current (optional) |  |  | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✔ | ✔ | ✔ | N/A | ✔ | ✔
F.1.13 | Site Information (e.g. Line Voltage) |  |  | ✔ | ✔ | N/A | ✖ | ✔ | N/A | ✖ | N/A | ✖ | ✖ | ✖ | ✔ | ✔ | ✖
F.1.14 | Permission to Dischage |  |  | ✔ | ✔ | N/A | ✖ | ✔ | N/A | ✖ | N/A | ✖ | ✖ | ✖ | ✔ | ✔ | ✖
F.1.15 | Contain Dispatch Location Information |  | Should | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✔ | ✔ | ✔ | ✔ | ✖ | ✔ | ✖
F.1.16 | Provide Inverter Make, Model and Approval status | < | Shall | ✔ | ✔ | N/A | ✖ | ✔ | N/A | ✖ | N/A | ✖ | ✖ | ✖ | ✔ | N/A | N/A
F.1.17 | DER Status information |  | Should | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
2- Pricing | Send Pricing or Tariff
F.2.01 | Tiered | > | Could | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✖ | N/A | Up to 30 days may be requested
F.2.02 | ToU |  | Shall | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✖ | N/A
F.2.03 | Critical Peak Pricing |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✖ | N/A
F.2.04 | Real Time Pricing (Hourly) |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✖ | N/A
F.2.05 | Special Tariffs (e.g. Price Interrupted) |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✖ | N/A
3- Load Control | Send Load Control Information (Increase charge or reduce Charge) with start time and duration
F.3.01 | Upto Day ahead using DR events | > | Shall | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✔ | ✔ | ✔ | ✔ | ✖ | ✔ | ✔
F.3.02 | Upto Day ahead using DER (Load) events | bar: ✔ to ✔
F.3.03 | Immediate emergency DR control (10 Minute response) | bar: ✔ to ✔
F.3.04 | Immediate emergency DER control (10 Minute response) | bar: ✔ to ✔
F.3.05 | Should have Primacy and Define Priority (e.g. BMS over PFE) |  | Should | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✔ | ✔ | ✔ | ✔ | ✖ | ✔ | ✖
F.3.06 | Contain Dispatch Location Information | bar: ✔ to ✔
4- Smart Charging | Negotiate Optimum Charging or Generatio based upon driver or site preferences
F.4.01 | Departure Time | > | Shall | ✖ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✔ | ✔
F.4.02 | Charge Rate | bar: ✖ to ✔
F.4.03 | Energy Required | bar: ✖ to ✔
F.4.04 | When the EVBS connects to the DCPC, the EVBS shall engage in DC DER Mode (should) | [17 empty] | if required=shall? | bar: ✖ to ✔
F.4.05 | Exchange information to manage DC power Flow | bar: ✖ to ✔
F.4.06 | Max Charge Rate |  |  | ✔ | ✔ | N/A | ✖ | ✔ | N/A | ✖ | N/A | ✖ | ✖ | ✖ | ✖ | ✔ | ✖
F.4.07 | Request Current Charge Power and SoC |  | Should | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖
F.4.08 | Departure Time | < | Shall | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | N/A | N/A
F.4.09 | Charge Rate |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | N/A | N/A
F.4.1 | Energy Required |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | N/A | N/A
F.4.11 | Departure Time |  |  | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✔ | ✖ | N/A | N/A
F.4.12 | Desired SoC |  |  | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✔ | ✖ | N/A | N/A
F.4.13 | Price to Charge |  | Should | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✔ | ✖ | N/A | N/A
F.4.14 | Provide SoC on a regular basis |  |  | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
5- Monitoring | Charge Event Data For M&V, Billing, and Monitoring | [17 empty] | Description?
F.5.01 | Start Time | < | Shall | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
F.5.02 | End Time |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
F.5.03 | KWh |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
F.05.04 | KW |  |  | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
6- Restart | Set Power Restoration Parameters | [17 empty] | Title/Description?
F.6.01 | Soft Start | > | Should | ✔ | ✔ | ✔ | ✖ | ✔ | ✔ | ✖ | ✖ | ✔ | ✔ | ✔ | ✖ | ✔ | ✖
F.6.02 | Random delay Start | bar: ✔ to N/A
F.6.03 | Ramp times | bar: ✔ to N/A
7- Miscellaneous | Other Requirements
F.M1 | GPS Location | < | Should | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | ✖ | N/A | N/A
F.M2 | Send Renewable or Fossil Mix | > | Should | ✔ | ✔ | ✖ | ✖ | ✔ | ✖ | ✖ | ✖ | ✔ | ✔ | ✖ | ✖ | ✖ | ✖

## Mapping Summary Table
Functional Requirements Category | Open ADR | IEEE 2030.5 | OCPP | Telematics | SAE Suite | IEEE 2030.1.1 | ISO 15118
1- Rule 21 | Not Supported | Supported | Not Supported | Supported in Combination | Supported in Combination | Supported in Combination | Not Supported
2- Pricing | Supported | Supported | Supported in Combination | Supported in Combination | Supported in Combination | Supported in Combination | Supported in Combination
3- Load Control | Supported | Supported | Supported in Combination | Supported in Combination | Supported in Combination | Supported in Combination | Supported in Combination
4- Smart Charging | Supported in Combination/Not Supported | Supported | Supported in Combination/Not Supported | Supported in Combination | Supported in Combination | Supported in Combination | Supported in Combination
5- Monitoring | Supported in Combination | Supported | Supported in Combination | Supported in Combination | Supported in Combination | Supported in Combination | Supported in Combination
6- Restart | Supported | Supported | Not Supported | Supported in Combination | Supported in Combination | Supported in Combination | Supported in Combination
7- Miscellaneous | Not Supported | Not Supported | Not Supported | Supported in Combination | Not Supported | Supported in Combination | Not Supported
Details of how this table was constructed are available at www.cpuc.ca.gov/vgi as VGI Mapping Sub-Working Group Final Report under the Deliverables Heading.

## Drop_Down_Menus
Primary Actor | Use Case Category | Functional Requirements Category
EV Driver | Pricing Programs | 1- Rule 21
Power Flow Entity | Demand Mitigation | 2- Pricing
Utility Customer of Record | Demand Response | 3- Load Control
EV Battery System | Load Control | 4- Smart Charging
DC Power Converter Systen | Monitoring and Measuring | 5- Monitoring
Energy Connection System | Direct Current Flow | 6- Restart
Energy Meter | Vehicle to Grid | 7- Miscellaneous
Building Management System | Inverter Control
Customer Programs