This document is an excerpt of

basic use-case information for vehicle to building or grid from:

the Electric Vehicle Power Supply System Association guidelines for the CHAdeMO Association

Guidelines of Charge/Discharge System

for Electric Vehicle V2H DC version

Electric Vehicle Power Supply System Association

EVPS-002：2014

Version 2.0

－Table of Contents －

Page

1. Scope of application.............................................................................................................................. 4

2. Normative reference ............................................................................................................................ 4

3. Terms and definitions ......................................................................................................................... 5

3.1 Vehicle.................................................................................................................................. 5

3.1.1 Vehicle contactor............................................................................................................... 5

3.1.2 Vehicle inlet...................................................................................................................... 5

3.2 EVPS (Electric Vehicle Power System) ............................................................................. 5

3.2.1 PCS................................................................................................................................... 5

3.2.2 Charge/discharge cable assembly.................................................................................... 5

3.2.3 Charge/discharge connector............................................................................................. 6

3.3 Charging.............................................................................................................................. 6

3.4 Discharging ........................................................................................................................ 6

3.5 CAN communication.......................................................................................................... 6

3.5.1 ID .................................................................................................................................... 6

3.6 Independent power outlet................................................................................................. 6

3.7 Other ................................................................................................................................. 6

3.7.1 Enclosure ....................................................................................................................... 6

3.7.2 Earth fault detection ..................................................................................................... 6

3.7.3 Commercial power source ............................................................................................. 6

3.7.4 Grid ................................................................................................................................ 6

3.7.5 Blackout ......................................................................................................................... 7

4. Configuration..................................................................................................................................... 7

5. System overview................................................................................................................................ 7

5.1 Scope ................................................................................................................................. 7

5.2 Functions........................................................................................................................... 8

5.2.1 Start-up ......................................................................................................................... 8

5.2.2 Charge/discharge mode................................................................................................. 8

5.3 Stopping ........................................................................................................................... 9

5.4 Connection to an undischargeable vehicle...................................................................... 9

6. Function and safety requirements  (redacted)............................................................................... 9

7. Circuit configuration  (redacted)................................................................................................... 15

8. Communication control  (redacted)............................................................................................... 26

9. Charge/discharge control  (redacted)............................................................................................ 28

Appendix A Materials for CHAdeMO charge sequence 0.9.1  (redacted)........................................ 34

Appendix B Materials for CHAdeMO charge sequence 1.0.1  (redacted)........................................ 65

Appendix C Supplimentary material for discharge current conversion  (redacted)....................... 99

Preface

In recent years, as one of the ways to reduce carbon dioxide emissions, vehicles equipped with a battery and/or a generator for their operation (hereinafter “Electric Vehicle”), including electric vehicles, plug-in hybrid vehicles and fuel cell vehicles, have become prevalent.

Meanwhile, due to a shortage of grid power supply after the Great East Japan Earthquake and popularization of renewable energy including photovoltaic generation, the demand for peak shift/cut of power using an electrical storage device is growing. In addition, there is a growing demand for power source in case of an emergency.

In this situation, the Electric Vehicle can be very useful.

This guideline has been prepared to ensure electric safety and compatibility between Electric Vehicle and connected devices/control systems with regard to the ‘Vehicle to Home’ (hereinafter “V2H”) where vehicles such as Electric Vehicles equipped with a battery and/or a generator for supplying electric power to household wiring using its power storage and power generation capabilities, and the ‘Vehicle to Load’ (hereinafter “V2L”) where the Electric Vehicle supplies electric power directly to electrical equipment.

This guideline sets out the details of provisions regarding the power connection between the vehicle and the household wiring as well as power control.

As forms of power supply to houses, there are various use cases of V2H according to the form of output from a vehicle, household wiring type, and the presence/absence of grid connection, but this guideline defines the following 6 categories.

Category 0 (V2L)

Aside from the power grid, the Electric Vehicle supplies electric power directly to electric equipment with a vehicle power inverter.

Category 1 (V2H: Independent dedicated outlet)

The Electric Vehicle supplies electric power to a dedicated outlet connected to the interior wiring of a house without connection to a power grid (grid connection).

Category 2 (V2H: Switching)

The Electric Vehicle and power grid are not directly connected (no grid connection), but electric power supplied to a house can be selected from either the power grid or the Electric Vehicle, using a switching unit.

Category 3 (V2H: Grid connection (no reverse power flow))

The Electric Vehicle and power grid are connected (grid connection) through a power inverter installed around houses and supply power to the interior wiring. There is no reverse power flow to the commercial power source side.

Category 4 (V2H: Grid connection (reverse power flow))

The Electric Vehicle and power grid are connected (grid connection) through a power inverter installed around houses and supply power to the interior wiring. There is reverse power flow to the commercial power source side.

Category 5 (V2G)

The Electric Vehicle is directly connected to a power grid.

Each category has its own characteristics as follows.

Category 0 can supply power easily, but it limits the power supply to electrical equipment that can be connected to an outlet.

Categories 1 to 5 need to meet regulations including indoor wiring regulations for the connection to the wirings of houses, and require more functions than Category 0. However, these categories enable the use of a power supply at places away from vehicles including indoors.

Categories 3 to 5 require functions including grid connection protective equipment, but these categories allow a combination use of power from the grid and Electric Vehicles and can realize various kinds of energy managements including power peak shift by covering part of the power consumption at home with Electric Vehicles.

In addition, in the categories not using the grid connection, Electric Vehicles supply power to electrical household appliances through an inverter converting DC to AC. However, the inverter does not have a high tolerance to overcurrent including inrush current, and under some conditions, power cannot be supplied. On the other hand, in the categories where the grid connection is achieved, the appliances can be used normally since the inrush current is taken care of by the grid.

1. Scope of application

This guideline sets out system specifications for vehicles with a traction battery and/or a generator, including electric, plug-in hybrid and fuel-cell vehicles, and EVPS (Electric Vehicle Power System), which conduct charging and/or discharging between the vehicles and household distribution system using direct current (hereinafter “DC”) power, and in addition, this guideline specifies requirements for the EVPS. (Category 1, 2 and 3)

The official version of this guideline does not deal with the interoperation with Home Energy Management System (hereinafter “HEMS”).

To make sure that your charger confirms to this guideline, a compatibility check shall be performed based on voluntary test standards (regarding safety and compatibility) to be published on October 2014.

2. Normative reference

This guideline refers to the following standards.

ECE R100 	Technical standard regarding road tracking vehicles agreement regulation No. 100

IEC 61851-1:2010 	Electric vehicle conductive charging system – Part 1: General requirements

IEC 61851-21:2001 	Electric vehicle conductive charging system – Part 21: Electric vehicle requirements for conductive connection to an a.c./d.c. supply

IEC 61851-23:2014 	Electric vehicle conductive charging system – Part 23: D.C. electric vehicle charging station

IEC 62196-1: 2011 	Plugs, socket-outlets, vehicle connectors and vehicle inlets – Conductive charging of electric vehicles – Part1: General requirements

IEC 62196-3: 2014 	Plugs, socket-outlets, vehicle connectors and vehicle inlets – Conductive charging of electric vehicles – Part3: Dimensional compatibility and interchangeability requirements for d.c. pin and a.c/d.c/ pin and contact-tube vehicle couplers

ISC 11898-2:2003 	Road vehicle – Controller area network (CAN) – Part 2: High-speed medium access unit

JIS/TSD0007 	Basic functions of a quick charger for electric vehicles

JIS C 60664-1:2009 	Insulation coordination for equipment within low-voltage systems − Part 1: Principles, requirements and tests

JIS C 8303:2007 	Plugs and receptacles for domestic and similar general use

JEAC 9701-2012 	Grid-interconnection Code

Ministerial ordinances on technical standards for electric facilities

Interpretations of technical standards for electric facilities

Indoor wiring regulation

Quick charger technical specifications for the electric vehicles (CHAdeMO Association)

JCS 4522:2013 	Flexible cable for electric vehicles

JCS-0168-1:2004 	Calculation of permissible current for 33 kV or less power cable - Part 1: Calculation formula and constants (The Japanese Electric Wire & Cable Makers’ Association standard)

JASO D-612-3: 2001 	Automobile parts, fuse – Part 3: blade type fuse

JASO D-612-6:2009 	Automobile parts, fuse – Part 3: low profile mini fuse

3. Terms and definitions

Main terms and definitions used in this guideline are as follows.

3.1 Vehicle

In this guideline, a vehicle means an electric vehicle having a discharging function including hybrid and plug-in hybrid electric vehicles and fuel-cell vehicles.

3.1.1 Vehicle contactor

A switch in charge/discharge circuit on a vehicle that is provided to electrically connect or disconnect the vehicle traction battery and an EVPS’s charge/discharge circuit, operated with the DC 12V supplied from the EVPS through a specific control signal line.

3.1.2 Vehicle inlet

The equipment mounted on the vehicle with a coupling system for charging/discharging.

3.2 EVPS (Electric Vehicle Power System)

The equipment that controls charging and discharging current to and from a vehicle. It comprises of an indicator, charge/discharge cable assemblies etc.

3.2.1 PCS

A device that mutually converts the DC and alternative current (hereinafter “AC”), and makes grid connection possible or supplies power to the electrical household appliances and/or vehicles.

3.2.2 Charge/discharge cable assembly

The cable that makes a connection between a vehicle and an EVPS. Charging and discharging are conducted with the same cable. A charge/discharge connector part to be connected to the vehicle is included.

3.2.3 Charge/discharge connector

A part connected to a vehicle inlet with a coupling system for charging/discharging. (JIS/TSD0007)

3.3 Charging

To supply electric power from an EVPS to a vehicle and to charge a vehicle traction battery.

3.4 Discharging

To supply power to a load from a vehicle generator and/or a vehicle traction battery through an EVPS.

3.5 CAN communication

A type of onboard network protocol.

(In this guideline, it is used between an EVPS and a vehicle)

3.5.1 ID

A name that is given to classify data information.

3.6 Independent power outlet

A dedicated outlet placed in a house and disconnected from the grid. It enables the power supply from a vehicle during blackout etc.

3.7 Other

3.7.1 Enclosure

The exterior of an instrument, including knob, handle, grip etc.

3.7.2 Earth fault detection

To detect the state where the insulated condition between the power circuit and the ground has deteriorated or an earth fault has occurred.

3.7.3 Commercial power source

Power to be supplied to an electric power user from an electric power provider as a business transaction and equipment to supply the power

3.7.4 Grid

An abbreviation of the commercial power system and its distribution grid (system) to supply power to an electric power user from an electric power provider as a business transaction

3.7.5 Blackout

Decrease of power-supply voltage that falls below the output voltage range

4. Configuration

An example of V2H system configuration is shown in Fig. 4

Fig. 4 An example of configuration for discharging in case of DC connection

5. System overview

5.1 Scope

(1) 	Due to the increased needs to use an EV as a storage battery, the system is intended to be used as a device to supply electric power from the EV to a house or an independent power outlet. A charging method according to the Quick Charger Technical Specifications for Electric Vehicles (hereinafter “CHAdeMO”) is a way to charge electric vehicles by using DC voltage.

(2) 	The system has the “charge/discharge mode” in which charging and discharging can be conducted without stopping in order to respond to the load changes of photovoltaic power generation and the electric loads with charging/discharging selection. However, this mode can be used only for either charging or discharging according to an application.

(3) 	This guideline focuses on the bidirectional power transmission method to perform mutually between an EVPS and a vehicle. The algorithm of controlling electric energy transmitted to/from vehicle and the HEMS functions that deal with the controlling policy are not standardized in this guideline.

Fig. 5.1 System overview

5.2 Functions

5.2.1 Start-up

(1) 	The EVPS shall be first started when a charge/discharge cable is connected to the vehicle.

(2) 	The start-up shall be carried out by maintaining the mutual synchronization using control signals.

(3) 	Charging/discharging shall be implemented only when both the vehicle and the EVPS are dischargeable. (As for the case where an undischargeable vehicle is connected, see 5.4 Connection to an undischargeable vehicle).

5.2.2 Charge/discharge mode

(1) 	In a charge/discharge mode, the EVPS shall control charge/discharge current within the range of maximum charge current (in charge mode using CHAdeMO, charge current command value) and maximum discharge current. The accuracy of current control shall be determined by system requirements etc. In addition, the charge/discharge mode may be used only for either charging or discharging by setting the maximum charge current or maximum discharge current to 0.

(2) 	Provided that the stopping conditions of an EVPS are met in charge/discharge mode, such as the case where it is determined that the EVPS has reached the minimum discharge voltage, the minimum remaining battery capacity for discharging/the minimum charging rate for discharging, the maximum charge voltage or the maximum remaining capacity for charging/maximum charging rate for charging, the EVPS shall proceed to stop-sequence. If it is determined that the stopping conditions of a vehicle are met, the vehicle may proceed stop-sequence.

Fig. 5.2 Schematic view of current control in charge/discharge mode

5.3 Stopping

(1) 	Both the vehicle and the EVPS shall be able to request stopping to the other.

(2) 	Stop processing shall be implemented while mutual synchronization is maintained using control signal lines. However, it shall be made possible to stop the vehicle and the EVPS as a system by providing both of them with the function to stop each other without fail even when a trouble occurs, like the case when synchronization cannot be maintained.

5.4 Connection to an undischargeable vehicle

(1) 	It is desirable that an undischargeable vehicle that is connected to an EVPS can be charged according to the EVPS’s charging capability using the charging protocol (CHAdeMO) to which the vehicle is applicable.

(2) 	The EVPS which does not have the function explained in item (1) shall clearly display such to that effect.

6. Function and safety requirements  (redacted)

7. Circuit configuration  (redacted)

8. Communication control  (redacted)

9. Charge/discharge control  (redacted)

Appendix A

This appendix shows the data allocation, charge/discharge sequence, timing etc. for the

CHAdeMO specification 0.9.1.  (redacted)

Appendix B

This appendix shows the data allocation, charge/discharge sequence, timing etc. for the

CHAdeMO specification 1.0.1 and the amendment 1 of CHAdeMO specification 1.0.1.  (redacted)

Appendix C

This Appendix shows supplimental material regarding data allocation.  (redacted)