## Sac Div 2016 Audit Response
Finding Type [Internal, NOV, AOC] | Finding # | Finding | Response | Associated Attachment (File Name)
NOV - PG&E's Internal Review Findings | IRSF | Prior to the start of the audit, PG&E provided SED its findings from the internal review it conducted of the Division. Some of PG&E’s internal review findings are violations of PG&E’s operations and maintenance standards, and are therefore violations of Title 49 Code of Federal Regulations (CFR), §192.13(c). Table 1 lists all valve and regulator station violations that PG&E noted. SED is aware that PG&E corrected some of its findings prior to SED’s audit. Please provide SED an update on the items that were still pending corrective actions. Updated IRSF response needed: Missed Maintenance - While performing a field inspection a Gas Mechanic discovered two separate HPR sets that appeared to feed facilities identified as gas main. As such these facilities appear to meet the definition of a District regulator station. Facility that is currently classified as a distribution main is in the process of being reclassified as a service. | Per the attached summary of PG&E's Sacramento Division Internal Review, there was 1 finding, which has been highlighted in yellow, that was awaiting resolution. The requested update to this finding has been provided on the Internal Review. Attached, please find attachment 1 "Att 1_Sacramento Internal Review.docx". | Att 1_Sacramento Internal Review.docx
NOV | 1 | Title 49 CFR §192.605 states in part: (a) General. Each operator shall prepare and follow for each pipeline, a manual of written procedures for conducting operations and maintenance activities and for emergency response…” PG&E’s Utility Procedure: TD-4430P-04, Gas Valve Maintenance, Publication Date: 01/01/2014 Rev: 01 states in part: “11 Operating Plug Valves During Maintenance 11.1 Valve being maintained must be operated (or stroked. through its complete range when operating conditions permit. 1. Execute a full operation of valve. 2. IF operating conditions do not permit a full operation of valve—to do so would cause downstream piping to be over-pressured or valve flow to be adversely affected, THEN partially operate valve per instructions in Section 11.2, AND document the reason for not fully operating the valve in the action taken section of the Gas Utility Form TD-4430P-04-F02, “Gas Valve Maintenance Record Form—Service History.” SED reviewed Gas Valve Maintenance Record Forms and found that PG&E did not document the reason for not fully operating plug valves on Gas Utility Form TD-4430P-04-F02 in the following instances: Table 2: Plug Valves without Documentation for Partial Operation Valve No. Description Year Valve Type W-33 North Area Zone Valve 2016 Plug W-26 North Area Zone Valve 2016 Plug W-25 North Area Zone Valve 2016 Plug W-24 North Area Zone Valve 2014, 2016 Plug W-23 North Area Zone Valve 2016 Plug W-21 North Area Zone Valve 2015, 2016 Plug BV-29 Greenback & Almond 2016 Plug BV-27 Greenback & Trajan 2016 Plug BV-24 North Area Zone Valve 2015, 2016 Plug BV-22 North Area Zone Valve 2016 Plug BV-19 North Area Zone Valve 2015, 2016 Plug BV-16 North Area Zone Valve 2015,2016 Plug PG&E is in violation of Title 49 CFR §192.605(a) because it failed to document the reason for not fully operating its plug valves. | PG&E recognizes this finding and has taken the following corrective and preventative actions: a) PG&E Sacramento Division has corrected the gas valve maintenance forms for these valves to reflect documentation for partial operation. See attachment 8 "Att 8_Valve partial operation_CONF.pdf". b) To prevent recurrence, PG&E's Quality Control Group assists with record reviews of completed maintenance to ensure compliance, which includes documenting reasons for partial operation. The goal is to identify any errors and have them corrected in real time in order to drive quality and provide timely feedback/instruction. In Sacramento, these reviews of the prior month's work were first started in December 2014. Please note that the Quality Control Group did not go back to review maintenance performed greater than 30 days prior to this start date or the previous year’s maintenance. In addition, a tailboard covering Valve Maintenance Work Procedure TD-4430P-04 was performed on 5/26/2016 to address this issue. See attachment 4 "Att 4_TD-4430P-04 Tailboard_Redacted.pdf". Note, employee personnel numbers have been redacted from this document. | Att 4_TD-4430P-04 Tailboard_Redacted.pdf Att 8_Valve partial operation_CONF.pdf
NOV | 2 | 2. Title 49 CFR §192.605(a) states in part: “General. Each operator shall prepare and follow for each pipeline, a manual of written procedures for conducting operations and maintenance activities and for emergency response.” SED inspected Regulator Station R-22 Inlet Fire Valve V-D03. At the time of the field inspection the valve maintenance card indicated Valve V-D03 was a 6-inch Cameron ball valve. PG&E Gas Valve Maintenance Work Procedure TD-4430P-04 specifies the maximum wrench length and torque limit for operating a valve based on manufacturer, type and size. Work Procedure TD-4430P-04 however, did not specify a maximum wrench length or torque limit for a 6-inch Cameron ball valve. SED observed PG&E exercise Valve V-D03 by attaching a cheater bar on a T-Bar wrench. The assembly measured 5 ½ feet end to end. PG&E later excavated the valve to validate specification and found the valve to be a 4” Grove B4d ball valve. The valve was tagged as inoperable, and an Alternate Means of Control was established while a project was initiated to replace the valve. PG&E is in violation of Title 49 CFR §192.605(a) because it used a wrench exceeding the maximum wrench length allowed of 24” as specified in the Gas Valve Maintenance Work Procedure for a 4” Grove ball valve. Please explain what corrective action PG&E has taken to prevent the use of wrenches which exceed the maximum allowed length. | PG&E recognizes that the use of a 66" T-bar assembly on a 4" Grove valve exceeded the 48" maximum as specified in TD-4430P-04 Appendix E. However, PG&E feels that the crew selected an appropriately sized assembly under the assumption that the valve was in fact a 6" Cameron ball valve, per the Operating Diagram. The use of the incorrectly sized wrench was caused by the inaccurate valve information, rather than a failure to follow the procedure. To prevent recurrence, PG&E submitted a Map Correction form to update the Operating Diagram. This was completed on 10/5/16. Additionally, the valve maintenance form was updated with corrected data. This valve has been scheduled for replacement under PM # 74009741 to permanently correct the non operable condition. See attachment 3 "Att3_NOV B-2 Documentation_CONF.pdf" for documentation of AMC, Map Correction Form, Corrected Operating Diagram, and corrected valve maintenance form. | Att3_NOV B-2 Documentation_CONF.pdf Att 4_TD-4430P-04 Tailboard_Redacted.pdf
AOC | 1 | SED reviewed maintenance records for regulator stations. Maintenance records indicated Regulator Stations B-07, B-10, B-20, B-22, B-37, A-08, A-57, R-09, R-01, R-14, R-41, R-46, R-49, R-60, R-61, A-40, A-64, D-30, DA-15, DA-02, DA-07, R-19, TS-01, WO-07 had regulators that failed to lock-up and noted sulfur deposits on components. Please explain what corrective action PG&E is taking to address lock-up issues due to sulfur deposits in the Division. | PG&E recognizes these observations and has taken the following corrective and preventative actions: a) PG&E has completed the installation of sulfur filters at the following 6 stations: (B-07, A-57, R-46, R-19, TS-01, and WO-07) PG&E has completed corrective notifications and ordered materials to install sulfur filters at these remaining 18 locations in the Sacramento Division ( B-10, B-20, B-22, B-37, A-08, R-09, R-01, R-14, R-41, R-49, R-60, R-61, A-40, A-64, D-30, DA-15, DA-02, DA-07) where lockup could not be achieved as required per procedure TD-4540P-01. Attached, please find attachment 2 "Att 2_ TD-4540P-01.pdf". This procedure is applicable system wide. Section 2.8 and Section 3.6.3 describes the requirements if sulfur is present on station internal components. The tasks include documenting sulfur presence on the maintenance record, cleaning or replacement of affected components, notification to the senior gas quality engineer, and creation of a corrective notification to install sulfur filters if the station contains pilot operated equipment. b) Sulfur causing issues with regulator lock‐up is an industry wide problem, and its effect on equipment is difficult to predict as its immediate impact on components will differ based on numerous variables. Sulfur can adversely affect regulators from functioning properly in two ways to prevent lock‐up; 1) sulfur depositing on the main body or boot, and 2) sulfur obstructing the pilots. Because there is no filter that can be installed on the main line to prevent sulfur from depositing on the main body cages and boots, PG&E will continue to monitor sulfur conditions through our periodic maintenance program and rectify issues as they are found. For sulfur creating obstructions in pilot lines, personnel are instructed to install sulfur‐gon filters in the pilot lines, per TD‐4540P‐01. Additionally, PG&E will utilize the quality control reviews to assist in identifying and monitoring repetitive instances of regulator stations encountering lock‐up issues due to sulfur. As the conditions above are encountered, the local I&R supervisor can work with engineering, asset management and integrity management to address these issues on a case by case basis. c) In addition, a tailboard was conducted on Work Procedure TD-4540P-01 on 5/20/2016 to address this issue. See attachment 6 "Att 6_TD-4540P-01 Tailboard_Redacted.pdf". Note, employee personnel numbers have been redacted from this document. | Att 2_ TD-4540P-01.pdf Att 6_TD-4540P-01 Tailboard_Redacted.pdf
AOC | 2 | SED inspected Regulator Station No. B-25 and found three regulators which had tag numbers that differed from the operating diagram. Table 3: Regulators Incorrectly Tagged Regulator Tag No. R2 R4 R3 R2 R4 R3 SED also observed that regulator R4 failed to lock up. The Division found sulfur deposits on the pilot stem and rebuilt the pilot assembly. | PG&E recognizes these observations and has taken the following corrective and preventative actions: a) During the field inspection, PG&E crews identified the correct regulator tag numbers and made appropriate corrections. b) PG&E has completed the installation of a sulfur filter at Station B-25. Attached, please find attachment 2 "Att 2_ TD-4540P-01.pdf". This procedure is applicable system wide. Section 2.8 and Section 3.6.3 describes the requirements if sulfur is present on station internal components. The tasks include documenting sulfur presence on the maintenance record, cleaning or replacement of affected components, notification to the senior gas quality engineer, and creation of a corrective notification to install sulfur filters if the station contains pilot operated equipment. c) Sulfur causing issues with regulator lock‐up is an industry wide problem, and its effect on equipment is difficult to predict as its immediate impact on components will differ based on numerous variables. Sulfur can adversely affect regulators from functioning properly in two ways to prevent lock‐up; 1) sulfur depositing on the main body or boot, and 2) sulfur obstructing the pilots. Because there is no filter that can be installed on the main line to prevent sulfur from depositing on the main body cages and boots, PG&E will continue to monitor sulfur conditions through our periodic maintenance program and rectify issues as they are found. For sulfur creating obstructions in pilot lines, personnel are instructed to install sulfur‐gon filters in the pilot lines, per TD‐4540P‐01. Additionally, PG&E will utilize the quality control reviews to assist in identifying and monitoring repetitive instances of regulator stations encountering lock‐up issues due to sulfur. As the conditions above are encountered, the local I&R supervisor can work with engineering, asset management and integrity management to address these issues on a case by case basis.. d) Please see response in AOC- 1 for actions to address the sulfur deposits. e) In addition, a tailboard was conducted on Work Procedure TD-4540P-01 on 5/20/2016 to address this issue. See attachment 6 "Att 6_TD-4540P-01 Tailboard_Redacted.pdf". Note, employee personnel numbers have been redacted from this document. | Att 2_ TD-4540P-01.pdf Att 6_TD-4540P-01 Tailboard_Redacted.pdf
AOC | 3 | SED inspected Regulator Station No. B-19 and observed that regulator R3 failed to lock up. The Division found sulfur deposits on the pilot stem and rebuilt the pilot assembly. SED observed corrosion at Regulator Station No. B-19 (see Figure 1) and requested PG&E to evaluate the type of corrosion and take corrective action. | PG&E recognizes these observations and has taken the following corrective and preventative actions: a) PG&E has completed corrective notifications and ordered materials to install a sulfur filter at Station B-19 where lockup could not be achieved as required per procedure TD-4540P-01. Attached, please find attachment 2 "Att 2_ TD-4540P-01.pdf." This procedure is applicable system wide. Section 2.8 and Section 3.6.3 describes the requirements if sulfur is present on station internal components. The tasks include documenting sulfur presence on the maintenance record, cleaning or replacement of affected components, notification to the senior gas quality engineer, and creation of a corrective notification to install sulfur filters if the station contains pilot operated equipment. b) Sulfur causing issues with regulator lock‐up is an industry wide problem, and its effect on equipment is difficult to predict as its immediate impact on components will differ based on numerous variables. Sulfur can adversely affect regulators from functioning properly in two ways to prevent lock‐up; 1) sulfur depositing on the main body or boot, and 2) sulfur obstructing the pilots. Because there is no filter that can be installed on the main line to prevent sulfur from depositing on the main body cages and boots, PG&E will continue to monitor sulfur conditions through our periodic maintenance program and rectify issues as they are found. For sulfur creating obstructions in pilot lines, personnel are instructed to install sulfur‐gon filters in the pilot lines, per TD‐4540P‐01. Additionally, PG&E will utilize the quality control reviews to assist in identifying and monitoring repetitive instances of regulator stations encountering lock‐up issues due to sulfur. As the conditions above are encountered, the local I&R supervisor can work with engineering, asset management and integrity management to address these issues on a case by case basis. c) Please see response in AOC- 1 for actions to address the sulfur deposits. d) A corrective work notification (# 111605689) was created to address atmospheric corrosion for painting. See attachment 5 "Att 5_AOC-3_B-19.pdf" for corrective work notification. e) A NDE examination was performed for this Station on 6/20/2016. Please see attachment 9 "Att 9_Reg Station B-19 Sacramento NDE Final Report.pdf" for full report. In addition, PM # 31276567 was created to replace station piping and components. This project is scheduled for completion by October 2017. | Att 2_ TD-4540P-01.pdf Att 5_AOC-3_B-19.pdf Att 9_Reg Station B-19 Sacramento NDE Final Report.pdf
AOC | 4 | SED inspected Regulator Station No. W0-22 in Woodland, CA and observed that regulator R-2 failed to lock up. PG&E crews found sulfur deposits on the pilot stem and rebuilt the pilot assembly. | PG&E's records do not reflect a station with a WO-22 designation. After consulting with the SED inspector, this is a duplicate of AOC-7.
AOC | 5 | SED inspected the Clarksburg Town Regulator Station (DR20) and Regulator Station No. R-22 and observed that both stations were missing electrical insulators between the pipeline and pipe stands. Insulators were installed at Clarksburg Town Regulator Station on July 12, 2016. Insulators were installed at Regulator Station No. 22 on July 15, 2016. | PG&E recognizes these observations and has taken the following corrective actions: a) The Clarksburg Regulator Station and Station R-22 were both inspected for pipe stand electrical insulators and both stations were found to not have any insulators installed. As SED noted, Clarksburg Regulator Station was inspected and insulators were installed on July 12, 2016 and Station R-22 at Porter Road was inspected and insulators were installed on July 15, 2016.
AOC | 6 | SED inspected Regulator Station No. B-07 and observed that regulator R-3 failed to lock up. The Division found sulfur deposits on the pilot stem and rebuilt the pilot assembly. | PG&E recognizes these observations and has taken the following corrective and preventative actions: a) PG&E has completed the installation of a sulfur filter at Station B-07 on 10/6/2016. Attached, please find attachment 2 "Att 2_ TD-4540P-01.pdf". This procedure is applicable system wide. Section 2.8 and Section 3.6.3 describes the requirements if sulfur is present on station internal components. The tasks include documenting sulfur presence on the maintenance record, cleaning or replacement of affected components, notification to the senior gas quality engineer, and creation of a corrective notification to install sulfur filters if the station contains pilot operated equipment. b) Sulfur causing issues with regulator lock‐up is an industry wide problem, and its effect on equipment is difficult to predict as its immediate impact on components will differ based on numerous variables. Sulfur can adversely affect regulators from functioning properly in two ways to prevent lock‐up; 1) sulfur depositing on the main body or boot, and 2) sulfur obstructing the pilots. Because there is no filter that can be installed on the main line to prevent sulfur from depositing on the main body cages and boots, PG&E will continue to monitor sulfur conditions through our periodic maintenance program and rectify issues as they are found. For sulfur creating obstructions in pilot lines, personnel are instructed to install sulfur‐gon filters in the pilot lines, per TD‐4540P‐01. Additionally, PG&E will utilize the quality control reviews to assist in identifying and monitoring repetitive instances of regulator stations encountering lock‐up issues due to sulfur. As the conditions above are encountered, the local I&R supervisor can work with engineering, asset management and integrity management to address these issues on a case by case basis. c) Please see response in AOC- 1 for actions to address the sulfur deposits. d) In addition, a tailboard was conducted on Work Procedure TD-4540P-01 on 5/20/2016 to address this issue. See attachment 6 "Att 6_TD-4540P-01 Tailboard_Redacted.pdf". Note, employee personnel numbers have been redacted from this document. | Att 2_ TD-4540P-01.pdf Att 6_TD-4540P-01 Tailboard_Redacted.pdf
AOC | 7 | SED inspected Regulator Station No. W0-20 in Woodland, CA and observed that regulator R-2 failed to lock up. The Division found sulfur deposits on the pilot stem and rebuilt the pilot assembly. | PG&E recognizes these observations and has taken the following corrective and preventative actions: a) PG&E has completed the installation of a sulfur filter at Station WO-20 in Woodland on 11/29/2016. Attached, please find attachment 2 "Att 2_ TD-4540P-01.pdf". This procedure is applicable system wide. Section 2.8 and Section 3.6.3 describes the requirements if sulfur is present on station internal components. The tasks include documenting sulfur presence on the maintenance record, cleaning or replacement of affected components, notification to the senior gas quality engineer, and creation of a corrective notification to install sulfur filters if the station contains pilot operated equipment. b) Sulfur causing issues with regulator lock‐up is an industry wide problem, and its effect on equipment is difficult to predict as its immediate impact on components will differ based on numerous variables. Sulfur can adversely affect regulators from functioning properly in two ways to prevent lock‐up; 1) sulfur depositing on the main body or boot, and 2) sulfur obstructing the pilots. Because there is no filter that can be installed on the main line to prevent sulfur from depositing on the main body cages and boots, PG&E will continue to monitor sulfur conditions through our periodic maintenance program and rectify issues as they are found. For sulfur creating obstructions in pilot lines, personnel are instructed to install sulfur‐gon filters in the pilot lines, per TD‐4540P‐01. Additionally, PG&E will utilize the quality control reviews to assist in identifying and monitoring repetitive instances of regulator stations encountering lock‐up issues due to sulfur. As the conditions above are encountered, the local I&R supervisor can work with engineering, asset management and integrity management to address these issues on a case by case basis. c) Please see response in AOC- 1 for actions to address the sulfur deposits. d) In addition, a tailboard was conducted on Work Procedure TD-4540P-01 on 5/20/2016 to address this issue. See attachment 6 "Att 6_TD-4540P-01 Tailboard_Redacted.pdf". Note, employee personnel numbers have been redacted from this document. | Att 2_ TD-4540P-01.pdf Att 6_TD-4540P-01 Tailboard_Redacted.pdf
AOC | 8 | SED inspected Regulator Station No. B-34 in Elk Grove and observed corrosion. SED requests PG&E to evaluate the type of corrosion and take corrective action. | PG&E recognizes this observation and has taken the following corrective actions: a) A corrective work notification (# 112429107) was created to address atmospheric corrosion for painting, and PM # 42904837 was created to have station coated and painted. Scheduled to be completed by 12/21/2017.
AOC | 9 | SED inspected Distribution Critical Main Valve B-01 in Davis and observed PG&E attempt to exercise the valve. The valve could not be exercised with the maximum T-Bar wrench length and number of personnel allowed in PG&E Gas Valve Maintenance Work Procedure TD-4430P-04 and therefore was considered inoperable. Please explain what corrective action PG&E has taken to correct this issue. | PG&E recognizes this observation and has taken the following corrective and preventative actions: a) Initiated and documented an AMC for this valve b) Valve maintenance form was updated with corrected data c) Notification 111789788 and Project order 31258334 was created to replace valve. This project is scheduled for completion in July 2017. See attachment 7 "Att 7_AOC-9 Documentation V-B-01_CONF.pdf" for documentation of AMC, corrected valve maintenance form, and SAP notification documentation d) In addition, a tailboard covering Valve Maintenance Work Procedure TD-4430P-04 was performed on 5/26/2016 to address this issue.See attachment 4 "Att 4_TD-4430P-04 Tailboard_Redacted.pdf." Note, employee personnel numbers have been redacted from this document. | Att 4_TD-4430P-04 Tailboard_Redacted.pdf Att 7_AOC-9 Documentation V-B-01_CONF.pdf
AOC | 10 | SED inspected Regulator Station No. D-22 and observed corrosion. SED requests PG&E evaluate the type of corrosion and take corrective action. | PG&E recognizes this observation and has taken the following corrective actions: a) A corrective work notification (# 112428542) was created to address atmospheric corrosion for painting, and PM # 42904836 was created to have station coated and painted. b) A NDE examination was performed for this Station on 6/20/2016. Please see attachment 10 "Att 10_Reg Station D-22 Sacramento NDE Final Report.pdf" for full report. In addition, PM # 31276563 was created to replace station piping and components. This project is scheduled for completion by October 2017. | Att 10_Reg Station D-22 Sacramento NDE Final Report.pdf
AOC | 11 | SED inspected Regulator Station No. R-22 in Dixon and observed that regulator R-2 failed to lock up. PG&E crews replaced the diaphragm and rebuilt the pilot cartridge. | PG&E recognizes this observation and has taken the following corrective and preventative actions: a) PG&E plans to install a sulfur filter at this location in the Sacramento Division (R-22) where lockup could not be achieved as required per procedure TD-4540P-01. Attached, please find attachment 2 "Att 2_ TD-4540P-01.pdf". This procedure is applicable system wide. Section 2.8 and Section 3.6.3 describes the requirements if sulfur is present on station internal components. The tasks include documenting sulfur presence on the maintenance record, cleaning or replacement of affected components, notification to the senior gas quality engineer, and creation of a corrective notification to install sulfur filters if the station contains pilot operated equipment. b) Sulfur causing issues with regulator lock‐up is an industry wide problem, and its effect on equipment is difficult to predict as its immediate impact on components will differ based on numerous variables. Sulfur can adversely affect regulators from functioning properly in two ways to prevent lock‐up; 1) sulfur depositing on the main body or boot, and 2) sulfur obstructing the pilots. Because there is no filter that can be installed on the main line to prevent sulfur from depositing on the main body cages and boots, PG&E will continue to monitor sulfur conditions through our periodic maintenance program and rectify issues as they are found. For sulfur creating obstructions in pilot lines, personnel are instructed to install sulfur‐gon filters in the pilot lines, per TD‐4540P‐01. Additionally, PG&E will utilize the quality control reviews to assist in identifying and monitoring repetitive instances of regulator stations encountering lock‐up issues due to sulfur. As the conditions above are encountered, the local I&R supervisor can work with engineering, asset management and integrity management to address these issues on a case by case basis. c) Please see response in AOC- 1 for actions to address the sulfur deposits. d) In addition, a tailboard was conducted on Work Procedure TD-4540P-01 on 5/20/2016 to address this issue. See attachment 6 "Att 6_TD-4540P-01 Tailboard_Redacted.pdf". Note, employee personnel numbers have been redacted from this document. | Att 2_ TD-4540P-01.pdf Att 6_TD-4540P-01 Tailboard_Redacted.pdf
AOC | 12 | SED inspected Regulator Station No. R-59 in Dixon and observed that Regulator R2 failed to lock up. PG&E crews replaced the diaphragm and rebuilt the pilot cartridge. | PG&E recognizes this observation and has taken the following corrective and preventative actions: a) PG&E plans to install a sulfur filter at this location in the Sacramento Division (R-59) where lockup could not be achieved as required per procedure TD-4540P-01. Attached, please find attachment 2 "Att 2_ TD-4540P-01.pdf". This procedure is applicable system wide. Section 2.8 and Section 3.6.3 describes the requirements if sulfur is present on station internal components. The tasks include documenting sulfur presence on the maintenance record, cleaning or replacement of affected components, notification to the senior gas quality engineer, and creation of a corrective notification to install sulfur filters if the station contains pilot operated equipment. b) Sulfur causing issues with regulator lock‐up is an industry wide problem, and its effect on equipment is difficult to predict as its immediate impact on components will differ based on numerous variables. Sulfur can adversely affect regulators from functioning properly in two ways to prevent lock‐up; 1) sulfur depositing on the main body or boot, and 2) sulfur obstructing the pilots. Because there is no filter that can be installed on the main line to prevent sulfur from depositing on the main body cages and boots, PG&E will continue to monitor sulfur conditions through our periodic maintenance program and rectify issues as they are found. For sulfur creating obstructions in pilot lines, personnel are instructed to install sulfur‐gon filters in the pilot lines, per TD‐4540P‐01. Additionally, PG&E will utilize the quality control reviews to assist in identifying and monitoring repetitive instances of regulator stations encountering lock‐up issues due to sulfur. As the conditions above are encountered, the local I&R supervisor can work with engineering, asset management and integrity management to address these issues on a case by case basis. c) Please see response in AOC- 1 for actions to address the sulfur deposits. d) In addition, a tailboard was conducted on Work Procedure TD-4540P-01 on 5/20/2016 to address this issue. See attachment 6 "Att 6_TD-4540P-01 Tailboard_Redacted.pdf". Note, employee personnel numbers have been redacted from this document. | Att 2_ TD-4540P-01.pdf Att 6_TD-4540P-01 Tailboard_Redacted.pdf