## Change request
Tab and Column or Row Name (where to make the change) | Change Request | Action Taken
“Distribution Costs and Plans,” Average cost of new regulator station or regulator station replacement | Provide the average cost of a new regulator station. | See row 27.
“Distribution Costs and Plans,” Items 10-13, 17 | Revise as needed to include all pipeline replacement, including services. Estimates may be used, such as estimated length of a service. Include a description of the calculations. | Updated rows, where applicable.
“Distribution Costs and Plans,” all repair, replacement and cost rows | For all information provided based on the 2023 General Rate Case, or to be provided herein, provide values separately for each year (2023, 2024, 2025, 2026). | No action required.
“Distribution Costs and Plans,” all repair, replacement and cost rows | For all information provided based on the 2023 General Rate Case, or to be provided herein, provide an alternate version showing actual values for 2019, 2020 and 2021. | See new columns E, F, and G for recorded values. Column H provides assumptions for columns E through G.
“Distribution Costs and Plans,” Items 20-24 (cost per mile by diameter) | Describe how diameter does or does not affect average cost per mile to replace distribution pipeline. Include the factors contributing to pipeline costs and whether purchasing pipeline itself (as opposed to labor and other costs) constitutes more than 10 percent of cost to replace distribution pipeline. | No action taken as provided before, PG&E does not track cost per mile based on main pipeline diameter.
“Program-Specific,” GRC MAT Code (new row) | Provide MAT code used in the General Rate Case filings which covers the column’s costs. | See row 3.
“Program-Specific,” Planning Period (new row) | Provide the typical length of time to determine the project list (list specifying locations to be repaired/replaced) and the length of time between when the project list is finalized and when the work is installed and operative | See row 4.
“Program-Specific,” all rows | If not already, include columns reflecting all distribution pipeline or regulator station repair or replacement, by cost code (MAT) or by program, whichever is more narrow. | No action required.
“Program-Specific,” all rows | If forecasts are not available, provide historical data based on 2019-2021. | Forecasts are provided; no action required.
“Program-Specific,” “Main Program Data Source” | Provide a description of the primary means of collecting data used in the risk models mentioned, e.g., fleet information. For “field observations” and“material failures,” state the usual occasion of the observations, e.g., leak surveys or customerinitiated investigation. Define “SAP” and “Integrated Investment Planning.” | Provided additional detail. See row 40.
“Program-Specific,” “Aspects Contributing to Risk of Failure” and “Aspects Contributing to Consequences of Failure” | Provide text stating the data types and data sources contributing to the aspects already stated, e.g., pipeline material (utility fleet records), population density (census data), soil liquefaction potential (leak surveys, or specify other source), or weather data (NOAA). Constants that do not vary by pipeline segment need not be addressed. | Provided additional detail. See row 42.

## Distribution Cost and Plans
Gas System Planning OIR (R.20-01-007) September 21, 2022 Ruling
Section B. Question 7. Corrected Supplemental Data
Note:
For averages, average across years covered by the most recent GRC proceeding, starting with the test year.
Row | GRC Distribution Pipeline General Costs and Plans Information | Response | Assumptions | 2019 Recorded | 2020 Recorded | 2021 Recorded | Assumptions/Data Source fo 2019-2021 Recorded Data
1 | Most Recent GRC proceeding name | 2023 General Rate Case
2 | Most Recent GRC proceeding number | A.21-06-021
3 | Most Recent GRC proceeding years covered, starting with test year | 2023 - 2026 | For purposes of responding to this request, PG&E interprets “cost” as its expense and capital expenditures forecasts.
4 | Open or Upcoming GRC proceeding name if any | A.21-06-021 - see above
5 | Open or Upcoming GRC proceeding number if any | n/a - see above
6 | Open or Upcoming GRC proceeding years covered, starting with test year | n/a - see above
7 | Total distribution main miles | 43,775 | Data from PG&E's Annual Gas Distribution System PHMSA 7100.1 Report submitted March 1, 2022. | 43294 | 43509 | 43775 | Data from PG&E's Annual Gas Distribution System PHMSA 7100.1 Report submitted March 4, 2020, submitted February 25, 2021, and submitted March 1, 2022, respectively.
8 | Total distribution service miles | 34,353 | Data from PG&E's Annual Gas Distribution System PHMSA 7100.1 Report submitted March 1, 2022. Reflects the total number of services (3,649,545) multiplied by row 9. | 33677.2484 | 33899.878 | 34353 | Data from PG&E's Annual Gas Distribution System PHMSA 7100.1 Report submitted March 4, 2020, submitted February 25, 2021, and submitted March 1, 2022, respectively.
9 | Average length of service pipeline (miles per service) | 0.0094 | The average service length from PG&E's Annual Gas Distribution System PHMSA 7100.1 Report submitted March 1, 2022 (49.7 feet) divided by 5,280 feet to convert to miles. | 0.0094 | 0.0094 | 0.0094 | Data from PG&E's Annual Gas Distribution System PHMSA 7100.1 Report submitted March 4, 2020, submitted February 25, 2021, and submitted March 1, 2022, respectively.
10 | Total distribution main pipeline miles to be replaced per year | 234 | Average 2023-2026 forecast for Pipeline Replacement Programs (GPRP MAT 14A, Plastic Pipeline Replacement MAT 14D, and Reliability Main Replacement MAT 50A). See PG&E's 2023 GRC Application (A. 21-06-021), Exhibit (PG&E-3), WP 4-27 to WP 4-29 (as served February 28, 2022). | 126 | 131 | 191 | Footage of main replaced for MAT 14A, MAT 14D, and MAT 50A for 2019, 2020, and 2021 respectively from the Gas Safety Plan Report for 2022.
11 | Total distribution service pipeline miles to be replaced per year | 8 | Average 2023-2026 forecast for Reliability Service Replacement Program (MAT 50B) multiplied by row 9. See PG&E's 2023 GRC Application (A. 21-06-021), Exhibit (PG&E-3), WP 4-30 (as served February 28, 2022). This excludes services replaced as part of pipeline replacement projects and leaking service replacements. | 4.888 | 4.0514 | 6.298 | GRC 2023 Exhibit-3 WP 4-30, line 8 for 2019 and 2020. Utilized SAP unit data for 2021.
12 | Total distribution main pipeline miles to be added per year | 8.75 miles capacity | Reflects Capacity Mains (MAT 47B) forecast of 46,200 feet of main installed each year divided by 5,280 to convert feet to miles. See PG&E's 2023 GRC Application (A. 21-06-021), Exhibit (PG&E-3), WP 11-38 (as served February 28, 2022). This excludes New Business and Work at the Request of Others (WRO). The New Business forecast is based on the number of connects and not miles. The WRO forecast is based on a historic programmatic average and is also not based in miles. | 8.7545 | 8.6966 | 9.2458 | SAP pull of units for 2019, 2020, and 2021, respectively for MAT 47B.
13 | Total distribution service pipeline miles to be added per year | n/a | Not available as the 2023 GRC forecast (2023-2026) for Distribution Capacity and New Business/WRO are not forecast in terms of services. | PG&E does not track services as a primary unit of installation. The primary unit tracked for recorded unit purposes for MAT 47B is "feet of main installed".
14 | Number of new regulator stations to be built during GRC period | 12 | Reflects the Capacity Regulator Station (MAT 47C) 2023-2026 forecast total for new regulator stations installed. See PG&E's 2023 GRC Application (A. 21-06-021), Exhibit (PG&E-3), WP 11-38 (as served February 28, 2022). | 2 | 3 | 3 | Recorded units are from PG&E's Gas Distribution Pipeline Safety Report No. 2019 through No. 2021
15 | Number of regulator stations to be replaced during GRC period | 100 | Reflects the 2023-2026 forecast total for Regulator Stations Rebuilds (MAT 50C). Does not include High Pressure Regulator (HPR) type stations because the HPR forecast also includes farm taps. See PG&E's 2023 GRC Application (A. 21-06-021), Exhibit (PG&E-3), WP 6-55 (as served February 28, 2022). | 26 | 22 | 28 | Recorded units are from PG&E's Gas Distribution Pipeline Safety Report No. 2019 through No. 2021
16 | Number of regulator stations to be repaired/upgraded during GRC period | 600 | Reflects the 2023-2026 forecast total for Regulator Station Component Replacements (MAT 50L). See PG&E's 2023 GRC Application (A. 21-06-021); Exhibit (PG&E-3); WP 6-54 (as served February 28, 2022). | 164 | 136 | 129 | Recorded units are from PG&E's Gas Distribution Pipeline Safety Report No. 2019 through No. 2021
17 | Average cost per mile to replace distribution pipeline (mains and services) | See row 18 and 19 |  | See row 18 and 19
18 | Average cost per mile to replace distribution main pipeline | $3,381,219 | Reflects the sum of 2023 - 2026 forecast totals for Pipeline Replacement Programs (GPRP MAT 14A, Plastic Pipeline Replacement MAT 14D, and Reliability Main Replacement MAT 50A) divided by the sum of 2023-2026 forecast unit totals in feet, and multiplied by 5,280 to convert feet to miles. See PG&E's 2023 GRC Application (A. 21-06-021), Exhibit (PG&E-3), WP 4-27 to WP 4-29 (as served February 28, 2022). | 2914426.2388 |  |  | Average is based on 2019-2021 Recorded dollars divided by row 10.
19 | Average cost per mile to replace distribution service pipeline | $3,032,255 | Reflects the 2023 - 2026 average forecast unit cost for the Reliability Service Replacement Program (MAT 50B) divided by row 11. See PG&E's 2023 GRC Application (A. 21-06-021), Exhibit (PG&E-3), WP 4-30 (as served February 28, 2022). | 2956347.4084 |  |  | Average is based on 2019-2020 Recorded dollars divided by row 11.
20 | Average cost per mile to replace distribution main pipeline with diameter of 2” or less | n/a | Not available as PG&E does not track cost per mile based on main pipeline diameter. | Not available as PG&E does not track cost per mile based on main pipeline diameter.
21 | Average cost per mile to replace distribution main pipeline with diameter over 2” through 4” | n/a | Not available as PG&E does not track cost per mile based on main pipeline diameter. | Not available as PG&E does not track cost per mile based on main pipeline diameter.
22 | Average cost per mile to replace distribution main pipeline with diameter over 4” through 8” | n/a | Not available as PG&E does not track cost per mile based on main pipeline diameter. | Not available as PG&E does not track cost per mile based on main pipeline diameter.
23 | Average cost per mile to replace distribution main pipeline with diameter over 8” through 12” | n/a | Not available as PG&E does not track cost per mile based on main pipeline diameter. | Not available as PG&E does not track cost per mile based on main pipeline diameter.
24 | Average cost per mile to replace distribution pipeline with diameter over 12” | n/a | Not available as PG&E does not track cost per mile based on main pipeline diameter. | Not available as PG&E does not track cost per mile based on main pipeline diameter.
25 | Average cost per mile to install new distribution main pipeline | See line 18 |  | See line 18
26 | Average cost per mile to install new distribution service pipeline | See line 19 |  | See line 19
27 | Average cost of new regulator station or regulator station replacement | $2,014,649 | Reflects the 2023-2026 unit cost forecast average for Regulator Stations Rebuilds (MAT 50C). See PG&E's 2023 GRC Application (A. 21-06-021), Exhibit (PG&E-3), WP 6-55 (as served February 28, 2022). | 2345174.3505 |  |  | Average is based on 2019-2021 Recorded divided by row 15.
28 | Average cost of regulator station repair/upgrade (excluding whole station replacement) | $72,270 | Reflects the 2023-2026 unit cost forecast average for Regulator Station Component Replacements (MAT 50L). See PG&E's 2023 GRC Application (A. 21-06-021), Exhibit (PG&E-3), WP 6-54 (as served February 28, 2022). | 81621.9936 |  |  | Average is based on 2019-2021 Recorded divided by row 16.
29 | Total gas distribution system costs per year | 2023 Expense: $576,687,502; 2023 Capital: $1,246,637,878; 2024 Capital: $1,284,908,523; 2025 Capital: $1,338,574,740; and 2026 Capital: $1,353,986,697 | Total gas distribution system forecasts include assets outside of distribution mains and services (e.g. distribution facilities and meters) that are not considered in terms of costs per mile, as well as support costs and program costs that are not tied to specific assets. For expense, PG&E is providing the test year forecast only consistent with its 2023 GRC (as of February 9, 2022). | 2019 Expense: $402,989,482 2019 Capital: $782,683,877 | 2020 Expense: $419,947,102 2020 Capital: $731,126,852 | 2021 Expense: $398,882,890 2021 Capital: $743,581,839 | Total gas distribution system include assets outside of distribution mains and services (e.g. distribution facilities and meters) that are not considered in terms of costs per mile, as well as support costs and program costs that are not tied to specific assets.
30 | Total gas distribution system costs per distribution mains and services pipeline miles per year | 2023 Expense: $7,381; 2023 Capital: $15,956; 2024 Capital: $16,446; 2025 Capital: $17,133; and 2026 Capital: $17,330 | This reflects a calculation of row 29 divided by the sum of rows 7-8 and is not representative of a meaningful cost per mile for the reasons stated in row 29. For expense, PG&E is providing the test year forecast only consistent with its 2023 GRC (as of February 9, 2022). | 2019 Expense: $5,236 2019 Capital: $10.169 | 2020 Expense: $5,425 2020 Capital: $9,445 | 2021 Expense: $5,105 2021 Capital: $9,517 | This reflects a calculation of row 29 divided by the sum of rows 7-8 and is not representative of a meaningful cost per mile for the reasons stated in row 29.

## Program Specific
Gas System Planning OIR (R.20-01-007) September 21, 2022 Ruling
| Section B. Question 7. Corrected Supplemental Data |  |  |  | In the first column, provide information aggregated across all distribution pipeline programs, i.e., including all distribution pipelines, for all cells not greyed out. | [6 empty] | Notes from Ruling: Include both main and service distribution pipelines. For regulator station programs, provide counts of stations instead of miles and exclude these programs from the “Pipeline Program Total” column. Define programs as reflected in the most recent GRC proceeding.
Row | GRC Distribution System Plans and Risks Information by Replacement Program
1 | Program Information | Program Name | Pipeline Program Total | Gas Pipeline Replacement Program | Plastic Pipeline Replacement Program | Reliability Main Replacement Program | Reliability Service Replacement Program | GD Regulator Station Component Replacements | GD Regulator Station Rebuilds | GD High Pressure Regulator (HPR) Program | Assumptions | Use one column for each program affecting distribution pipelines or regulator stations, e.g., the Plastic Pipe Replacement Program.
2 |  | Program Goal (brief description of the focus of the program) |  | Prevent Safety incidents by replacing higher risk steel assets | Prevent Safety incidents by replacing higher risk plastic assets | Maintain Safety and Compliance with assets not covered by MATs 14A or 14D. | Replace ageing service with field identified issues. | Component replacement to ensure reliable operation of distribution stations | Rebuild of non-HPR distribution stations to ensure reliable operation | Removal or rebuild of HPR type distribution stations to ensure reliable operation |  | In the “Program Goal” row, provide a brief description of the focus of the program.
3 |  | GRC MAT Code(s) |  | 14A | 14D | 50A | 50B | 50L | 50C | 2K
4 |  | Planning Period (Provide the typical length of time to determine the project list (list specifying locations to be repaired/replaced) and the length of time between when the project list is finalized and when the work is installed and operative. | PG&E's planning period is dependent on the Program. PG&E's programs accommodate the use of formal operational risk models along with field intelligence and observations to inform work identification and priority timelines for when work will be planned and executed. PG&E also has procedures that provide time bounding to identified work, such as the Gas Distribution Work and Compliance Matrix (TD-4854P-01). | Projects are identified annually using DIMP Riskfinder scoring and leak review and proposed to be planned and executed (installed and operative) generally within 5-years. Jobs are assigned one of three priority levels based on various factors that determines proposed timeline for them to be completed within. | Projects are identified annually using DIMP Riskfinder scoring and leak review and proposed to be planned and executed (installed and operative) generally within 5-years. Jobs are assigned one of three priority levels based on various factors that determines proposed timeline for them to be completed within. | Projects are generally identified through emergent processes that do not have a defined identification horizon. Once identified, projects are planned and executed in accordance with PG&E's internal Work and Compliance timeframe specified in Utility Procedure TD-4854P-01. | Projects are generally identified through emergent processes that do not have a defined identification horizon. Once identified, projects are planned and executed in accordance with PG&E's internal Work and Compliance timeframe specified in Utility Procedure TD-4854P-01. | Projects performed under this program address specific maintenance or operational issues with valves and regulators, and include upgrades of station components to meet current PG&E design standards. Component replacement consists of routine work to replace equipment or components when they have exceeded their useful life or are experiencing performance problems. Equipment additions may be required based on the need for filters, bypass valves, fire valves and other 9 components. | The scope of the facility rebuild will depend on a review of the condition of all facility components, as well as operational and safety issues. A full rebuild project scope typically includes the complete rebuild of the station which results in all piping, manual valves, control valves, pipe supports, and control systems being rebuilt in the same location or nearby to the current facility. | PG&E is planning to replace 100 HPR units each year. This pace will effectively complete the HPR replacement program in 2026. After the 2023-2026 GRC period, the HPR program will become an ongoing control program similar to station rebuild and component replacement obsolescence management programs.
5 |  | Main Program Data Source (description of the primary means of collecting data used to prioritize pipelines for replacement in that program) |  | Risk Model - See rows 40 and 42 below for additional information about data sources and Utility Procedure, TD-4850P-01 - Gas Distribution Integrity Management Program (as provided in response ot Q.A.1 - Risk Assessment, Appendix 1). | Risk Model and Material Failures - See rows 40 and 42 below for additional information about data sources and Utility Procedure, TD-4850P-01 - Gas Distribution Integrity Management Program (as provided in response ot Q.A.1 - Risk Assessment, Appendix 1). | Field observations, Risk Model, and Material Failures - See rows 40 and 42 below for additional information about data sources and Utility Procedure, TD-4850P-01 - Gas Distribution Integrity Management Program (as provided in response ot Q.A.1 - Risk Assessment, Appendix 1). | Field observations - See rows 40 and 42 below for additional information about data sources and Utility Procedure, TD-4850P-01 - Gas Distribution Integrity Management Program (as provided in response ot Q.A.1 - Risk Assessment, Appendix 1). | Field observation, Corrective Action Program (CAP), SAP - PG&E's system of record, fleet information | Field observation, CAP, SAP, fleet information, Integrated Investment Planning (IIP). The IIP Process looks closely at alternative options to mitigate 8compliance threats outside of the traditional assessment mitigations. (See Exhibit (PG&E-3), p. 1-10, lines 7-9 (as served February 28, 2022). | Field observation, CAP, SAP, fleet information, IIP |  | In the “Main Program Data Source” row, provide a description of the primary means of collecting data used to prioritize pipelines for replacement in that program, e.g., leak surveys.
6 |  | Materials of Pipeline Covered by Program |  | Steel | Plastic | All pipelines outside of GPRP and Plastic Pipe Replacements scope. | All | All | All | All
7 |  | Ages of Pipelines Covered by Program |  | Pre-1941 | Pre-1985 | All, see row 4 | All | All | All | All
8 |  | Program Includes Mains, Services or Both |  | Both | Both | Both | Services | Neither | Neither | Neither
9 | Program Forecasts | Pipelines Miles with Known Locations to be Replaced by Program During Years Covered by Most Recent GRC, Per Year | 2023: 276; 2024: 137; 2025: 45; and 2026: 19 | 2023: 53; 2024: 68; 2025: 15; and 2026: 3 | 2023: 202; 2024: 45; 2025: 15; and 2026: 4 | 2023: 21; 2024: 24; 2025: 15; and 2026: 12 | 2023: 414; 2024: 224; 2025: 87; and 2026: 1 | n/a | n/a | n/a | Pipeline Replacement and Service Replacement Programs reflect the Distribution Execution Plan (DEP) work plan for 2023-2026 as of March 25, 2022 and are subject to change. Service replacement information reflects service counts, not miles, consistent with PG&E's presentation of the Service Replacement Program in the 2023 GRC. Pipeline program total miles in column D are inclusive of only the following programs listed in Row 1: Gas Pipeline Replacement Program (MAT 14A) in Column E, Plastic Pipeline Replacement Program (MAT 14D) in Column F, and Reliability Main Replacement Program (MAT 50A) in Column G. Regulator Station Programs do not include pipeline assets, see row 6 above.
10 |  | Pipelines Miles with Locations Yet to be Determined to be Replaced by Program During Years Covered by Most Recent GRC, Per Year | 2023: 0; 2024: 131; 2025: 192; and 2026: 227 | 2023: 0; 2024: 0; 2025: 26; and 2026: 41 | 2023: 0; 2024: 131; 2025: 166; and 2026: 183 | 2023: 0; 2024: 0; 2025: 0; and 2026: 3 | 2023: 386; 2024: 576; 2025: 713; and 2026: 799 | n/a | n/a | n/a | Pipeline Replacement and Service Replacement Programs reflect the difference between row 9 and row 7. For Reliability Main Replacement, the current DEP work plan reflects more miles than the average 2023-2026 GRC forecast. Service replacement information reflects service count, not miles, consistent with PG&E's presentation of the Service Replacement Program in the 2023 GRC. Pipeline program total miles in column D are inclusive of only the following programs listed in Row 1: Gas Pipeline Replacement Program (MAT 14A) in Column E, Plastic Pipeline Replacement Program (MAT 14D) in Column F, and Reliability Main Replacement Program (MAT 50A) in Column G. Regulator Station Programs do not include pipeline assets see row 6 above.
11 |  | Total Pipeline Miles or Count of Regulator Stations to be Replaced by Program During Years Covered by Most Recent GRC, Per Year | 2023: 222; 2024: 230; 2025: 237; and 2026: 246 | 2023: 37; 2024: 39; 2025: 41; and 2026: 44 | 2023: 170; 2024: 176; 2025: 181; and 2026: 187 | 15/year | 800/year | 150/year | 25/year | 100/year | For purposes of responding to this request PG&E interprets “replaced per year” as forecast each year from 2023-2026. Service replacement information reflects service count, not miles, consistent with PG&E's presentation of the Service Replacement Program in the 2023 GRC. See PG&E's 2023 GRC Application (A. 21-06-021), Exhibit (PG&E-3), Workpapers (as served February 28, 2022): WP 4-27 to WP 4-29 for the Pipeline Replacement Programs; WP 4-30 for the Service Replacement Program; WP 6-54 for the GD Regulator Station Component Replacements Program; WP 6-55 for the GD Regulator Station Rebuilds Program; and WP 6-56 for the GD HPR Program. Pipeline program total miles in column D are inclusive of only the following programs listed in Row 1: Gas Pipeline Replacement Program (MAT 14A) in Column E, Plastic Pipeline Replacement Program (MAT 14D) in Column F, and Reliability Main Replacement Program (MAT 50A) in Column G.
12 |  | Total Pipeline Miles to be Replaced by Program for Program Completion, If Applicable | 8,121 | 1,745 | 6,376 | n/a | n/a | n/a | n/a | n/a | Pipeline Replacement Programs reflect remaining scope. Reliability Main Replacement MAT 50A and Service Replacement MAT 50B are n/a because they are ongoing replacement programs for the safety and reliability of the natural gas system. Pipeline program total miles in column D are inclusive of only the following programs listed in Row 1: Gas Pipeline Replacement Program (MAT 14A) in Column E, Plastic Pipeline Replacement Program (MAT 14D) in Column F, and Reliability Main Replacement Program (MAT 50A) in Column G. Regulator Station Programs do not include pipeline assets, see row 6 above.
13 |  | Total Pipeline Miles Subject to Program (include all miles potentially eligible for replacement under the program) | 43,775 | 1,745 | 6,376 | 35,654 | 3,649,545 services | n/a | n/a | n/a | Pipeline Replacement and Service Replacement programs reflect the following from PG&E's Annual Gas Distribution System PHMSA 7100.1 Report submitted March 1, 2022: Pre-1941 metallic pipe including unknown vintage (GPRP MAT 14A); Pre-1985 plastic pipe including unknown vintage (Plastic Pipeline Replacement MAT 14D); Post-1984 all pipe plus post 1940 and beyond steel (Reliability Main Replacement MAT 50A); and Total number of services in the Gas Distribution system (Service Replacement MAT 50B). Pipeline program total miles in column D are inclusive of only the following programs listed in Row 1: Gas Pipeline Replacement Program (MAT 14A) in Column E, Plastic Pipeline Replacement Program (MAT 14D) in Column F, and Reliability Main Replacement Program (MAT 50A) in Column G. Regulator Station Programs do not include pipeline assets, see row 6 above. | In “Total Pipeline Miles Subject to Program,” include all miles potentially eligible for replacement under the program (e.g., subject to leak surveys or made of relevant materials).
14 |  | Expected Year of Completion Per Utility’s Goals, If Applicable |  | Undetermined | 2053, pending the outcomes of future rate cases. | On-Going | On-Going | On-Going | On-Going | HPR as a mitigation program will end in 2026 after which it will become an on-going control program.
15 | Calculated Probability of Leak per Year, or Risk of Failure | Minimum Possible | 0.017 | 0.0617 | 0.0186 | 0.017 | 0.0154 | n/a | n/a | n/a | For purposes of responding to this request for the Pipeline Replacement Programs, PG&E interprets “Risk of Failure” as likelihood of failure. The units of LoF are leaks/year. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, PG&E's Facilities Integrity Management Program (FIMP) is in the process of developing a probabilistic risk model for stations, however, it is still in the preliminary stage and will not have the breakdown of information requested. PG&E's enterprise risk model does not have the granular level of detail requested. | For “Calculated probability of leak per year, or risk of failure, ,” “Consequences of Failure or Calculated probability of serious Safety Incident Given Leak” and “Risk Score,” provide the values at the thresholds indicated, i.e., enter the minimum possible risk of failure, maximum possible risk of failure, the minimum risk of failure calculated for any pipeline segment in the utility’s system, the risk of failure that 25 percent of the utility’s pipeline miles are at or below (25thpercentile), the average risk of failure across the utility’s distribution pipelines, etc. To find the “minimum possible” and “maximum possible,” use the theoretical extremes for each data input used in the calculation. Risk scores are the product of probability of leak per year (SoCalGas terminology) or risk of failure (PG&E terminology) and likelihood of serious incident given leak (SoCalGas terminology) or consequences of failure (PG&E terminology). In the “Aspects Contributing to Risk of Failure” and “Aspects Contributing to Consequences of Failure” rows, provide text stating these aspects and their data sources, such as pipeline age (utility data), population density (census data), etc.
16 |  | Maximum Possible | no maximum defined | no maximum defined | no maximum defined | no maximum defined | no maximum defined | n/a | n/a | n/a | For Pipeline Replacement Programs, see row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). The maximum possible limit is listed as "no maximum defined" because the risk model does not assume a maximum number of leaks that may occur in a year. For Regulator Station Programs, see row 13 for explanation.
17 |  | Minimum | 0.02012 | 0.06689 | 0.025 | 0.02012 | 0.021 | n/a | n/a | n/a | For Pipeline Replacement Programs the units of LoF are leaks/year. For Reliability Main Replacement, the minimum LoF value excludes segments with normalized LoF values below the data precision limit of 1E-08. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
18 |  | 25th Percentile | 0.0372 | 0.0907 | 0.0379 | 0.0359 | 0.0569 | n/a | n/a | n/a | For Pipeline Replacement Programs the units of LoF are leaks/year. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
19 |  | Average | 0.0707 | 0.135 | 0.0541 | 0.0689 | 0.084 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of LoF are leaks/year. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
20 |  | 75th Percentile | 0.0864 | 0.157 | 0.0619 | 0.0852 | 0.0983 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of LoF are leaks/year. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
21 |  | 95th Percentile | 0.158 | 0.25 | 0.0918 | 0.153 | 0.144 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of LoF are leaks/year. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
22 |  | Maximum | 1.59 | 1.25 | 0.871 | 1.59 | 14.7 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of LoF are leaks/year. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
23 | Calculated Probability of Serious Safety Incident Given Leak, or Consequence of Failure | Minimum Possible | 0.0073 | 0.0073 | 0.0073 | 0.0073 | 0.0059 | n/a | n/a | n/a | For Pipeline Replacement Programs, the minimum possible CoF is based on all individual subthreats. The units of CoF are SIFs/100,000 leaks. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
24 |  | Maximum Possible | 65.8 | 65.8 | 65.8 | 65.8 | 65.8 | n/a | n/a | n/a | For Pipeline Replacement Programs, the maximum possible CoF is based on all individual subthreats. The units of CoF are SIFs/100,000 leaks. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
25 |  | Minimum | 0.397 | 0.451 | 1.13 | 0.397 | 0.769 | n/a | n/a | n/a | For Pipeline Replacement Programs, the minimum "effective" CoF value excludes segments with normalized RoF and LoF values below the data precision limit of 1E-08. The units of CoF are SIFs/100,000 leaks. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
26 |  | 25th Percentile | 5.06 | 10.7 | 6.37 | 4.89 | 7.95 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of CoF are SIFs/100,000 leaks. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
27 |  | Average | 17.1 | 19.3 | 22.8 | 16 | 24.6 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of CoF are SIFs/100,000 leaks. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
28 |  | 75th Percentile | 25.9 | 28.1 | 35.6 | 24 | 37.5 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of CoF are SIFs/100,000 leaks. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
29 |  | 95th Percentile | 37.6 | 33.9 | 42.9 | 35.2 | 51.5 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of CoF are SIFs/100,000 leaks. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
30 |  | Maximum | 64 | 59.3 | 63.7 | 64 | 65.7 | n/a | n/a | n/a | For Pipeline Replacement Programs the units of CoF are SIFs/100,000 leaks. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
31 | Risk Score | Minimum Possible Risk Score | 0.000124 | 0.00045 | 0.000136 | 0.000124 | 9.084e-05 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of RoF are SIFs/100,000 years. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13.
32 |  | Maximum Possible Risk Score | no maximum defined | no maximum defined | no maximum defined | no maximum defined | no maximum defined | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of RoF are SIFs/100,000 years. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). The maximum possible limit is listed as "no maximum defined" because the risk model does not assume a maximum number of leaks that may occur in a year. For Regulator Station Programs, see row 13 for explanation.
33 |  | Minimum Risk Score | 0.0247 | 0.0651 | 0.0661 | 0.0247 | 0.0386 | n/a | n/a | n/a | For Reliability Main Replacement, the minimum RoF value excludes segments with normalized RoF values below the data precision limit of 1E-08. The units of RoF are SIFs/100,000 years. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
34 |  | 25th Percentile Risk Score | 0.27 | 1.3 | 0.391 | 0.236 | 0.674 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of RoF are SIFs/100,000 years. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
35 |  | Average Risk Score | 1.18 | 2.47 | 1.26 | 1.07 | 2.13 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of RoF are SIFs/100,000 years. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
36 |  | 75th Percentile Risk Score | 1.6 | 3.26 | 1.74 | 1.47 | 3.13 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of RoF are SIFs/100,000 years. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
37 |  | 95th Percentile Risk Score | 3.3 | 5.09 | 3.1 | 3.01 | 5.29 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of RoF are SIFs/100,000 years. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
38 |  | Maximum Risk Score | 55.4 | 24.9 | 55.4 | 55 | 966 | n/a | n/a | n/a | For Pipeline Replacement Programs, the units of RoF are SIFs/100,000 years. See row 39 for additional risk scoring detail. The Pipeline Program Total reflects the value across the main replacement programs (MATs 14A, 14D, and 50A). This information is presented in scientific notation. For Regulator Station Programs, see row 13 for explanation.
39 | Risk Scoring Discussion and Further Information | Aspects Contributing to Risk of Failure | Eight threat categories: 1) Corrosion, 2) Equipment Failure, 3) Excavation Damage, 4) Incorrect Operations, 5) Material,Weld, or Joint Failure, 6) Natural Forces, 7) Other Outside Forces, and 8) Other. | Eight threat categories: 1) Corrosion, 2) Equipment Failure, 3) Excavation Damage, 4) Incorrect Operations, 5) Material,Weld, or Joint Failure, 6) Natural Forces, 7) Other Outside Forces, and 8) Other. | Eight threat categories: 1) Corrosion, 2) Equipment Failure, 3) Excavation Damage, 4) Incorrect Operations, 5) Material,Weld, or Joint Failure, 6) Natural Forces, 7) Other Outside Forces, and 8) Other. | Eight threat categories: 1) Corrosion, 2) Equipment Failure, 3) Excavation Damage, 4) Incorrect Operations, 5) Material,Weld, or Joint Failure, 6) Natural Forces, 7) Other Outside Forces, and 8) Other. | Eight threat categories: 1) Corrosion, 2) Equipment Failure, 3) Excavation Damage, 4) Incorrect Operations, 5) Material,Weld, or Joint Failure, 6) Natural Forces, 7) Other Outside Forces, and 8) Other. | n/a | n/a | n/a | For purposes of responding to this request PG&E interprets “aspects contributing to risk of failure” as aspects contributing to likelihood of failure and is providing the applicable threat categories. For Pipeline Replacement Programs, see row 39 for additional risk scoring detail. For Regulator Station Programs, see row 13 for explanation.
40 |  | Aspects Contributing to Risk of Failure - Data Types and Data Sources | Leak history (maintenance records), age (asset record), material (asset record), earth movement (geosciences), earthquake faults (geosciences), flood zones (FEMA), high fire threat districts (CPUC) | Leak history (maintenance records), age (asset record), material (asset record), earth movement (geosciences), earthquake faults (geosciences), flood zones (FEMA), high fire threat districts (CPUC) | Leak history (maintenance records), age (asset record), material (asset record), earth movement (geosciences), earthquake faults (geosciences), flood zones (FEMA), high fire threat districts (CPUC) | Leak history (maintenance records), age (asset record), material (asset record), earth movement (geosciences), earthquake faults (geosciences), flood zones (FEMA), high fire threat districts (CPUC) | Leak history (maintenance records), age (asset record), material (asset record), earth movement (geosciences), earthquake faults (geosciences), flood zones (FEMA) | n/a | n/a | n/a | For purposes of responding to this request PG&E interprets “aspects contributing to risk of failure” as aspects contributing to likelihood of failure and is providing the applicable threat categories. For Pipeline Replacement Programs, see row 39 for additional risk scoring detail. For Regulator Station Programs, see row 13 for explanation.
41 |  | Aspects Contributing to Consequences of Failure | Loss of containment severity based on failure mode (e.g. threat), population density, migration and accumulation, and operating pressure. | Loss of containment severity based on failure mode (e.g. threat), population density, migration and accumulation, and operating pressure. | Loss of containment severity based on failure mode (e.g. threat), population density, migration and accumulation, and operating pressure. | Loss of containment severity based on failure mode (e.g. threat), population density, migration and accumulation, and operating pressure. | Loss of containment severity based on failure mode (e.g. threat), population density, migration and accumulation, operating pressure, and presence of excess flow valve. | n/a | n/a | n/a | For Regulator Station Programs, see row 13 for explanation.
42 |  | Aspects Contributing to Consequences of Failure - Data Types and Data Sources | Population density (US Census), public assembly or business district (leak survey), residential/commerical/industrial customer type (meter asset record), pressure (asset record), and excess flow valve (asset record). | Population density (US Census), public assembly or business district (leak survey), residential/commerical/industrial customer type (meter asset record), pressure (asset record), and excess flow valve (asset record). | Population density (US Census), public assembly or business district (leak survey), residential/commerical/industrial customer type (meter asset record), pressure (asset record), and excess flow valve (asset record). | Population density (US Census), public assembly or business district (leak survey), residential/commerical/industrial customer type (meter asset record), pressure (asset record), and excess flow valve (asset record). | Population density (US Census), public assembly or business district (leak survey), residential/commerical/industrial customer type (meter asset record), pressure (asset record), and excess flow valve (asset record). | n/a | n/a | n/a | For Regulator Station Programs, see row 13 for explanation.
43 |  | Discussion of Risk Scoring Approach | For each segment the risk of failure (RoF) (units: SIFs/100,000 years) is calculated at a sub-threat level with an individual likelihood of failure (LoF) (units: leaks/year) and consequence of failure (units: serious injuries or fatalities or SIFs/100,000 leaks). The total RoF and LoF on a given segment was obtained by summing the sub-threat RoF and LoF values. The total LoF and RoF values were normalized by each segment's length before calculating statistics because of the effect of segment length on these values which tends to skew LoF and RoF towards larger segments. The LoF and RoF values are presented above in normalized units (LoF: leaks/mile-year; RoF: SIFs/100,000 mile-year). This summation approach, however, cannot be applied to Consequence of Failure (CoF) because each sub-threat CoF is dependent upon the mode of failure. For example a loss of containment due to excavation damage is expected on average to result in more injuries or fatalities than a corrosion leak. Therefore summing the sub-threats' CoF values per segment is not meaningful. For the purposes of providing minimum and maximum possible CoF values individual subthreat CoF values were used. An "effective" CoF was calculated by dividing the normalized total RoF score by the normalized total LoF score for each segment. This "effective" CoF cannot be derived from a segment's underlying CoF factors as described in the row above. Descriptive statistics were calculated for all in-scope segments under each program. | See Pipeline Program Total | See Pipeline Program Total | See Pipeline Program Total | See Pipeline Program Total | n/a | n/a | n/a | For Regulator Station Programs, see row 13 for explanation.
44 |  | Staff Contact Name and Email | Eileen Cotroneo, Regulatory Affairs |  |  |  |  | n/a | n/a | n/a | For Regulator Station Programs, see row 13 for explanation.

## Customer Data
Customer Data | For the Year 2021
Total customers | 4576346
Average Annual daily core consumption (MMcfd) | 719
Average Annual daily noncore consumption (MMcfd) | 1509
Average Annual daily wholesale consumption (MMcfd) | REDACTED
Average Annual daily company use and lost/unaccounted for gas (MMcfd) | 50
Systemwide peak hour (date and hour) | 12/15/2021 at 10:00AM
Average Annual daily core consumption metered hourly (MMcfd) | N/A
Average Annual daily noncore consumption metered hourly (MMcfd) | 1509
Average Annual daily company use and lost/unaccounted for gas metered hourly (MMcfd) | N/A
Average Annual daily wholesale consumption metered hourly (MMcfd) | REDACTED
Core consumption during peak hour, for core metered hourly (MMcfh) | N/A
Noncore consumption during peak hour, for noncore metered hourly (MMcfh) | 66
Wholesale consumption during peak hour, for wholesale metered hourly (MMcfh) | REDACTED
Company use and lost/unaccounted for gas during peak hour, for wholesale metered hourly (MMcfh) | N/A
Estimated core consumption during peak hour, for core not metered hourly (MMcfh) | 96.8
Estimated noncore consumption during peak hour, for noncore not metered hourly (MMcfh) | N/A
Estimated wholesale consumption during peak hour, for other not metered hourly (MMcfh) | REDACTED
Estimated other consumption during peak hour, for other not metered hourly (MMcfh) | N/A